## NO Outage Cause Chart
Outages By Cause
ANIMAL | ANIMAL | 34 | 6.953%
CONDUCTOR | CONDUCTOR | 53 | 10.84%
CONTRIBUTING | CONTRIBUTING | 0 | 0%
EQUIPMENT | EQUIPMENT | 182 | 37.22%
ERROR | ERROR | 0 | 0%
HUMAN FACTORS | HUMAN FACTORS | 22 | 4.499%
IMPROPER RELAYING | IMPROPER RELAYING | 7 | 1.431%
LIGHTNING | LIGHTNING | 40 | 8.18%
OTHER | OTHER | 98 | 20.04%
OVERLOAD | OVERLOAD | 0 | 0%
STORM | STORM | 0 | 0%
SUMMARY MISSING | Summary Missing | 17 | 3.476%
VEGETATION | VEGETATION | 36 | 7.362%
TOTAL OUTAGES |  | 489

## Outage Cause Category Details
SUMMARY_CAUSE | Cause Detail
ANIMAL | Animal - Squirrel | 19
| Animal - Other (Describe in Remarks Field) | 13
| Animal - Bird Reportable Incident (Mortality or Injury) | 2
ANIMAL Total |  | 34
CONDUCTOR | Secondary/Service Conductor | 17
| Equipment - Primary Conductor | 31
| Equipment - Shield Conductor | 3
| Cable in duct | 2
CONDUCTOR Total |  | 53
EQUIPMENT | Equipment - Fuse Link | 32
| Equipment - Transformer | 63
| Equipment - Arrestor | 16
| Equipment - Pole | 8
| Equipment - Fuse Switch | 9
| Equipment - Air Break / Disconnect Switch | 1
| Equipment - Crossarm | 35
| Equipment - Connector Sleeve | 7
| Equipment - Elbow | 6
| Equipment - Other (Describe in Remarks Field) | 5
EQUIPMENT Total |  | 182
HUMAN FACTORS | Human Error - Non-Entergy Workers (Describe in Remarks) | 3
| Vehicle | 10
| Mis-Coordination (Describe in remarks) | 1
| Contractor - Distribution Line (Describe in remarks) | 2
| Company - Distribution Line (Describe in remarks) | 3
| Other Error - Company (Describe in Remarks Field) | 1
| Malicious Damage | 1
| Contractor - Substation (Describe in remarks) | 1
HUMAN FACTORS Total |  | 22
IMPROPER RELAYING | Relay Design Error - Drawing | 7
IMPROPER RELAYING Total |  | 7
LIGHTNING | Lightning | 40
LIGHTNING Total |  | 40
OTHER | Scheduled Interruption | 47
| Inspected Unknown | 17
| Foreign Objects - Other | 13
| Emergency Switching | 2
| Unknown - Under Investigation | 13
| Fire - Other (Describe in Remarks Field) | 2
| Transient Fault | 4
OTHER Total |  | 98
Summary Missing | Equipment - Connector / Sleeve | 14
| Equipment - Neutral / Shield Conductor | 2
| Secondary cable | 1
Summary Missing Total |  | 17
VEGETATION | Overhanging Limb | 18
| Tree/Limb Growing Inside R.O.W. | 4
| Tree On Line Outside R.O.W. | 4
| Vine Growing into Line | 10
VEGETATION Total |  | 36
Grand Total |  | 489

## Outages by District & Weather
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
NAME | Weather Condition | SUMMARY_CAUSE | Cause Detail | Outage Date | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES1 | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 71
Council District B | [9 empty] | 98
Council District C | [9 empty] | 101
Council District D | [9 empty] | 99
Council District E | [9 empty] | 120
Grand Total | [9 empty] | 489

## Outages by District & Zip Code
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
NAME | ZIP | SUMMARY_CAUSE | Cause Detail | Outage Date | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES1 | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 71
Council District B | [9 empty] | 98 | NOTE: Outages that occurred outside the physical boundaries of Algiers into Gretna are grouped into zip code 70056 – Council District C, as they are serviced by feeders from Algiers.
Council District C | [9 empty] | 101
Council District D | [9 empty] | 99
Council District E | [9 empty] | 120
Grand Total | [9 empty] | 489

## Data
CASE_ID | In NOCC Reporting | NETWORK_NAME | WEATHER_CONDITION | FIRST_CALL_DATE_TIME | LAST_CALL_DATE_TIME | TROUBLE_CLEAR_TIME | FEEDER_ID | Feeder Owner | DEVICE_TYPE | DEVICE_ID | DISTRIBUTION_LOCATION_NBR | System_ | LOCAL_OFFICE_NBR | TOTAL_CUSTOMERS_AFFECTED | ACTUAL_CUSTOMER_MINUTES | TOTAL_DURATION_MINUTES1 | SUMMARY_CAUSE | CAUSE | CAUSE_DESC | MAJOR_EVENT | REMARKS | LONGITUDE | LATITUDE | ZIP | DISTRICTID | NAME | REPNAME
1293419400 | Yes | ORLEANS | FAIR | 2018-07-13 07:13 | 2018-07-13 07:13 | 2018-07-13 08:46 | 1553 | ENOI | PRIM | 3907846953 | 3907846953 | DLIN | 1 | 1 | 92 | 92 | ANIMAL | ASQL | Animal - Squirrel | N | refuse ok | -90.0994 | 29.9523 | 70125 | B | Council District B | Kristin Palmer
1291274302 | Yes | ORLEANS | FAIR | 2018-06-07 08:38 | 2018-06-07 08:38 | 2018-06-07 09:38 | 2147 | ENOI | SERV | METER | 39499459466 | DLIN | 1 | 1 | 60 | 60 | HUMAN FACTORS | HCDC | Contractor - Distribution Line (Describe in remarks) | N | Changed **TFUS 61066 * 12 to SERV 61066 * [count]** --- service was active, but boots were behind mtr with a good red seal, restored power to customer 6/7/1104 dgrison | -90.0865 | 29.9244 | 70115 | B | Council District B | Jared Brossett
1292371195 | Yes | EAST ORLEANS | FAIR | 2018-06-25 14:33 | 2018-06-25 14:33 | 2018-06-25 15:17 | 1601 | ENOI | SERV | 1105837 | 44452500897 | DLIN | 6 | 1 | 44 | 44 | OTHER | FOBJ | Foreign Objects - Other | N | Changed **TFUS 1105837 7 to SERV 1105837 1** --- Repaired hot leg on underground service due to cust damaging with shovel jvickna | -89.9285 | 30.0368 | 70129 | E | Council District E | Joseph Giarrusso
1293263430 | Yes | ORLEANS | FAIR | 2018-07-10 16:31 | 2018-07-10 16:31 | 2018-07-10 17:21 | 1916 | ENOI | SERV | 1415631 | 38804466873 | DLIN | 1 | 1 | 50 | 50 | OTHER | FOBJ | Foreign Objects - Other | N | Changed **TFUS 1415631 3 to SERV 1415631 3** --- contract crew transferred pole and had neutral and hot leg swapped jtatma1 | -90.1082 | 29.9451 | 70125 | B | Council District B | Kristin Palmer
1294136641 | NO | ORLEANS CBD | HEAT | 2018-07-22 15:13 | 2018-07-22 15:13 | 2018-07-22 16:46 | 1845 | ENOI | SUBN | 1845 | 4015046694 | DSUB | 4 | 1 | 93 | 93 | OTHER | FOBJ | Foreign Objects - Other | N | Balloons have been found on ground burnt which took out bus on T4 at Notre Dame | -90.0657 | 29.9448 | 70130 | B | Council District B | Jared Brossett
1294138064 | NO | ORLEANS CBD | HEAT | 2018-07-22 15:13 | 2018-07-22 15:13 | 2018-07-22 16:46 | 1846 | ENOI | SUBN | 1846 | 4015046692 | DSUB | 4 | 1 | 93 | 93 | OTHER | FOBJ | Foreign Objects - Other | N | Balloons have been found on ground burnt which took out bus on T4 at Notre Dame | -90.0657 | 29.9448 | 70130 | B | Council District B | Jay Banks
1290918158 | Yes | EAST ORLEANS | FAIR | 2018-06-01 17:25 | 2018-06-01 17:59 | 2018-06-01 20:24 | 2215 | ENOI | SERV | SERVICE | 43056506837 | DLIN | 6 | 1 | 179 | 179 | OTHER | FOBJ | Foreign Objects - Other | N | Changed **TFUS 32998 13 to SERV 32998 1** --- Tree cut hot legs on service--Replaced both hot leg connections on service jvickna | -89.9724 | 30.0537 | 70128 | E | Council District E | Kristin Palmer
1292671424 | Yes | ORLEANS | HEAT | 2018-07-01 17:08 | 2018-07-01 17:08 | 2018-07-01 18:22 | 627 | ENOI | TFUS | 1336804 | 40248482382 | DLIN | 1 | 1 | 74 | 74 | LIGHTNING | LGHT | Lightning | N | Old fuse barrel burned up and customer did not have his C phase transformer operating. droser | -90.062 | 29.9873 | 70122 | D | Council District D | Jay Banks
1291661786 | Yes | ALGIERS | RAIN | 2018-06-13 11:18 | 2018-06-13 11:18 | 2018-06-13 13:16 | W1715 | ENOI | TFUS | 1358461 | 4338945413 | DLIN | 81 | 1 | 118 | 118 | LIGHTNING | LGHT | Lightning | N | refuse transformer and lateral ddesroc | -89.9641 | 29.9086 | 70131 | C | Council District C | Joseph Giarrusso
1291922374 | Yes | ORLEANS | FAIR | 2018-06-18 05:02 | 2018-06-18 05:02 | 2018-06-18 07:08 | 2012 | ENOI | SERV | METER | 3871848107 | DLIN | 1 | 1 | 126 | 126 | HUMAN FACTORS | MALD | Malicious Damage | N | Changed **TFUS 550024 * 2 to METER 550024 * 1** --- someone pulled meter out of panel repaired advised jbologn | -90.1103 | 29.9841 | 70124 | A | Council District A | Cyndi Nguyen
1294248394 | NO | ORLEANS | FAIR | 2018-07-24 10:38 | 2018-07-24 10:38 | 2018-07-24 12:46 | 1554 | ENOI | TFUS | 33396 * | 39547466578 | DLIN | 1 | 1 | 0 | 0 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 33396 * 17 to CUST 33396 * 17** --- THE CREWS ARE WORKING IN THIS AREA jmondy | -90.0847 | 29.9441 | 70113 | B | Council District B | Cyndi Nguyen
1293433752 | NO | ORLEANS | FAIR | 2018-07-13 15:02 | 2018-07-13 15:04 | 2018-07-13 15:04 | 409 | ENOI | DIS | 13988 | 3839949391 | DLIN | 1 | 1 | 2 | 2 | OTHER | SCHD | Scheduled Interruption | N | tree on feeder drop out to cut tree | -90.1201 | 30.0196 | 70124 | A | Council District A | Kristin Palmer
1291240367 | NO | EAST ORLEANS | FAIR | 2018-06-06 12:03 | 2018-06-06 12:03 | 2018-06-06 12:06 | 2215 | ENOI | TFUS | 57278 | 42674502888 | DLIN | 6 | 1 | 3 | 3 | OTHER | SCHD | Scheduled Interruption | N | service man drop out to make repaires | -89.9847 | 30.0428 | 70127 | E | Council District E | Cyndi Nguyen
1291828515 | NO | EAST ORLEANS | FAIR | 2018-06-16 06:33 | 2018-06-16 06:33 | 2018-06-16 06:37 | 2216 | ENOI | SERV | SERVICE | 42761501097 | DLIN | 6 | 1 | 4 | 4 | OTHER | SCHD | Scheduled Interruption | N | crew working on line down the road bad cable | -89.9819 | 30.0379 | 70127 | E | Council District E | Cyndi Nguyen
1292168427 | NO | EAST ORLEANS | FAIR | 2018-06-22 10:56 | 2018-06-22 10:56 | 2018-06-22 11:00 | 506 | ENOI | TFUS | 23547 | 40678493770 | DLIN | 6 | 1 | 4 | 4 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0481 | 30.0184 | 70122 | D | Council District D | Cyndi Nguyen
1291830141 | Yes | EAST ORLEANS | FAIR | 2018-06-16 08:54 | 2018-06-16 09:00 | 2018-06-16 09:09 | 2347 | ENOI | SERV | SERVICE | 4121647380 | DLIN | 6 | 1 | 14 | 14 | OTHER | SCHD | Scheduled Interruption | N | crew working | -90.0317 | 29.9634 | 70117 | C | Council District C | Jay Banks
1293291939 | Yes | ORLEANS | FAIR | 2018-07-11 12:31 | 2018-07-11 12:31 | 2018-07-11 12:49 | 1916 | ENOI | TFUS | 68243 | 38614464925 | DLIN | 1 | 1 | 18 | 18 | OTHER | SCHD | Scheduled Interruption | N |  | -90.1143 | 29.9397 | 70115 | A | Council District A | Jared Brossett
1291494536 | Yes | ALGIERS | FAIR | 2018-06-11 10:36 | 2018-06-11 10:38 | 2018-06-11 11:03 | W0725 | ENOI | TFUS | 1303091 | 4134346256 | DLIN | 81 | 1 | 27 | 27 | OTHER | SCHD | Scheduled Interruption | N | crew working | -90.0282 | 29.9324 | 70114 | C | Council District C | Jared Brossett
1294279823 | Yes | ORLEANS | FAIR | 2018-07-25 11:34 | 2018-07-25 11:34 | 2018-07-25 12:01 | 1709 | ENOI | TFUS | 55692 | 39982483143 | DLIN | 1 | 1 | 27 | 27 | OTHER | SCHD | Scheduled Interruption | N | crew on site making repairs | -90.0705 | 29.9893 | 70119 | D | Council District D | Jared Brossett
1291935748 | Yes | ALGIERS | FAIR | 2018-06-18 09:52 | 2018-06-18 09:52 | 2018-06-18 10:26 | W0725 | ENOI | SERV | SERVICE | 4147946209 | DLIN | 81 | 1 | 34 | 34 | OTHER | SCHD | Scheduled Interruption | N | crew to make repairs | -90.0238 | 29.9311 | 70114 | C | Council District C | Kristin Palmer
1292240813 | Yes | EAST ORLEANS | FAIR | 2018-06-23 10:13 | 2018-06-23 10:18 | 2018-06-23 10:50 | 2347 | ENOI | TFUS | 57722 | 41268474137 | DLIN | 6 | 1 | 37 | 37 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0301 | 29.9643 | 70117 | C | Council District C | Kristin Palmer
1292075782 | Yes | ALGIERS | FAIR | 2018-06-20 14:31 | 2018-06-20 14:31 | 2018-06-20 15:11 | W0713 | ENOI | SERV | SERVICE | 4154145893 | DLIN | 81 | 1 | 40 | 40 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0219 | 29.9223 | 70114 | C | Council District C | Joseph Giarrusso
1292066391 | Yes | EAST ORLEANS | HEAT | 2018-06-20 10:46 | 2018-06-20 10:46 | 2018-06-20 11:27 | 2217 | ENOI | TFUS | 1333180 | 43782511424 | DLIN | 6 | 1 | 41 | 41 | OTHER | SCHD | Scheduled Interruption | N | PREPLANNED OUTAGE, CONTR CREW WRKING, ADVISED 1315, 6/20/18 rbeaco | -89.9494 | 30.066 | 70128 | E | Council District E | Jay Banks
1291578591 | Yes | ALGIERS | FAIR | 2018-06-12 13:30 | 2018-06-12 13:53 | 2018-06-12 14:13 | W1725 | ENOI | TFUS | BY25359 | 4119146602 | DLIN | 81 | 1 | 43 | 43 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0328 | 29.942 | 70114 | C | Council District C | Joseph Giarrusso
1293133688 | Yes | EAST ORLEANS | FAIR | 2018-07-08 09:18 | 2018-07-08 09:18 | 2018-07-08 11:01 | 1710 | ENOI | TFUS | 1416330 | 40563486723 | DLIN | 6 | 1 | 103 | 103 | OTHER | SCHD | Scheduled Interruption | N | REPAIRED | -90.0519 | 29.9991 | 70122 | D | Council District D | Jared Brossett
1292231980 | Yes | EAST ORLEANS | FAIR | 2018-06-23 07:59 | 2018-06-23 08:21 | 2018-06-23 09:45 | 2347 | ENOI | TFUS | 61766 | 41225473774 | DLIN | 6 | 1 | 106 | 106 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0315 | 29.9634 | 70117 | C | Council District C | Joseph Giarrusso
1291245573 | Yes | ORLEANS | FAIR | 2018-06-06 13:27 | 2018-06-06 13:27 | 2018-06-06 15:40 | 2021 | ENOI | TFUS | 62464 | 39330467440 | DLIN | 1 | 1 | 132 | 132 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0916 | 29.9465 | 70125 | B | Council District B | Kristin Palmer
1294523782 | Yes | ORLEANS | FAIR | 2018-07-30 12:24 | 2018-07-30 12:24 | 2018-07-30 14:37 | 1915 | ENOI | TFUS | 1355993 | 39466466447 | DLIN | 1 | 1 | 133 | 133 | OTHER | SCHD | Scheduled Interruption | N | CREW ON SITE | -90.0873 | 29.9436 | 70113 | B | Council District B | Cyndi Nguyen
1294310293 | Yes | EAST ORLEANS | FAIR | 2018-07-26 09:41 | 2018-07-26 09:41 | 2018-07-26 12:16 | 611 | ENOI | TFUS | 1171328 | 41072478105 | DLIN | 6 | 1 | 155 | 155 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.0363 | 29.9752 | 70117 | D | Council District D | Joseph Giarrusso
1291244453 | Yes | ORLEANS | FAIR | 2018-06-06 12:51 | 2018-06-06 13:10 | 2018-06-06 15:30 | 614 | ENOI | TFUS | 1520553 | 40309474066 | DLIN | 1 | 1 | 159 | 159 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0605 | 29.9644 | 70116 | C | Council District C | Jared Brossett
1293551812 | Yes | ORLEANS | FAIR | 2018-07-16 09:58 | 2018-07-16 12:33 | 2018-07-16 13:05 | 1705 | ENOI | TFUS | 58874 | 39785477152 | DLIN | 1 | 1 | 187 | 187 | OTHER | SCHD | Scheduled Interruption | N | crew on site transfering pole | -90.0768 | 29.973 | 70119 | D | Council District D | Jay Banks
1291568391 | Yes | ORLEANS | FAIR | 2018-06-12 09:55 | 2018-06-12 10:12 | 2018-06-12 13:11 | 1925 | ENOI | LFUS | 21508 | 3915146429 | DLIN | 1 | 1 | 196 | 196 | OTHER | SCHD | Scheduled Interruption | N | maintance | -90.0973 | 29.9378 | 70115 | B | Council District B | Joseph Giarrusso
1292012356 | Yes | ORLEANS | FAIR | 2018-06-19 11:32 | 2018-06-19 13:40 | 2018-06-19 14:50 | 1513 | ENOI | TFUS | 65750 | 39418476117 | DLIN | 1 | 1 | 198 | 198 | OTHER | SCHD | Scheduled Interruption | N | crew transfering pole | -90.0884 | 29.9703 | 70119 | B | Council District B | Jay Banks
1291937546 | Yes | ORLEANS | THDR | 2018-06-18 10:22 | 2018-06-18 10:22 | 2018-06-18 13:46 | 2135 | ENOI | TFUS | 1000793 | 39905462004 | DLIN | 1 | 1 | 203 | 203 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0736 | 29.9313 | 70130 | B | Council District B | Joseph Giarrusso
1294098950 | Yes | EAST ORLEANS | FAIR | 2018-07-22 07:05 | 2018-07-22 09:00 | 2018-07-22 10:49 | 1608 | ENOI | DIS | 27361 | 4155648719 | DLIN | 6 | 1 | 224 | 224 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.0205 | 30.0001 | 70126 | E | Council District E | Jay Banks
1292984982 | Yes | ORLEANS | THDR | 2018-07-06 11:01 | 2018-07-06 11:01 | 2018-07-06 11:43 | 2012 | ENOI | LFUS | 30746 | 38847481119 | DLIN | 1 | 1 | 42 | 42 | HUMAN FACTORS | VHCL | Vehicle | N | - unknown vehicle made turn at Toulouse and N. Bernodotte side swiped pole took out A phase only of lat. 21564 jbolog. **PID Added to July Minimal Claims" | -90.1063 | 29.9842 | 70124 | A | Council District A | Jay Banks
1294237968 | Yes | EAST ORLEANS | FAIR | 2018-07-24 05:53 | 2018-07-24 05:53 | 2018-07-24 07:33 | 501 | ENOI | SERV | SERVICE COND | 4103649193 | DLIN | 6 | 1 | 100 | 100 | HUMAN FACTORS | VHCL | Vehicle | N | River Parish Disposal snagged customer secondary pipe HOLD FOR PERMIT Mtr-7277758 CT metering at location see PID form made customer contact cbower1 | -90.0368 | 30.0132 | 70126 | D | Council District D | Kristin Palmer
1292608090 | Yes | ORLEANS | FAIR | 2018-06-30 07:32 | 2018-06-30 07:32 | 2018-06-30 11:16 | 1915 | ENOI | SERV | SERVICE | 39448467195 | DLIN | 1 | 1 | 224 | 224 | HUMAN FACTORS | VHCL | Vehicle | N | Changed **TFUS 60953 4 to SERV 60953 1** --- truck took down signal light service, reconnected droser **added to July Minimal Claims** | -90.0878 | 29.9458 | 70113 | B | Council District B | Jared Brossett
1292987194 | NO | ORLEANS | RAIN | 2018-07-06 12:16 | 2018-07-06 13:42 | 2018-07-06 15:16 | 1921 | ENOI | SERV | SERVICE | 38925458280 | DLIN | 1 | 1 | 0 | 0 | HUMAN FACTORS | HECD | Company - Distribution Line (Describe in remarks) | N | Changed **TFUS 31160 15 to ERR 31160 1** --- FOUND OFF WITH TIGHT YELLOW SEAL..TURNED ON FOR ACTIVE CUST PER JBROGGI djohn26 | -90.1047 | 29.9215 | 70115 | B | Council District B | Jared Brossett
1294246852 | NO | EAST ORLEANS | HEAT | 2018-07-24 09:49 | 2018-07-24 09:49 | 2018-07-24 11:35 | 1611 | ENOI | TFUS | 56232 * | 43329495745 | DLIN | 6 | 1 | 0 | 0 | HUMAN FACTORS | HECD | Company - Distribution Line (Describe in remarks) | N | Changed **TFUS 56232 * 6 to ERR 56232 * [count]** --- MT RMV IN ERR, MTR RMV FOR NON CONSM, REPLC, 1107,24JUL18 rbeaco | -89.9642 | 30.023 | 70127 | E | Council District E | Cyndi Nguyen
1290914229 | Yes | ORLEANS | HEAT | 2018-06-01 15:46 | 2018-06-01 15:46 | 2018-06-01 16:53 | 2024 | ENOI | SERV | METER | 38540464391 | DLIN | 1 | 1 | 67 | 67 | HUMAN FACTORS | HECD | Company - Distribution Line (Describe in remarks) | N | Changed **TFUS 1145580 * 7 to ERR 1145580 * 1** --- Meter was cut out in error, rmvd boots on meter. droser | -90.1167 | 29.9383 | 70118 | A | Council District A | Jay Banks
1292435804 | Yes | ALGIERS | HEAT | 2018-06-27 10:05 | 2018-06-27 10:05 | 2018-06-27 13:30 | W0723 | ENOI | TFUS | 569472 | 4160046539 | DLIN | 81 | 1 | 205 | 205 | OTHER | EMER | Emergency Switching | N | maintenance | -90.02 | 29.9401 | 70114 | C | Council District C | Jay Banks
1291177524 | Yes | EAST ORLEANS | THDR | 2018-06-05 14:25 | 2018-06-05 14:25 | 2018-06-05 15:53 | 1203 | ENOI | TFUS | 1452358 | 44592496638 | DLIN | 6 | 1 | 88 | 88 | EQUIPMENT | EARR | Equipment - Arrestor | N | lightning hit terminal pole blowing arrestor/cleared refused ok dfahr | -89.9243 | 30.025 | 70129 | E | Council District E | Jay Banks
1293420038 | Yes | EAST ORLEANS | FAIR | 2018-07-13 08:03 | 2018-07-13 11:03 | 2018-07-13 12:45 | 1612 | ENOI | TFUS | 32991 | 43012492413 | DLIN | 6 | 1 | 282 | 282 | EQUIPMENT | EARR | Equipment - Arrestor | N | blown arrestor on c phase terminal pole feeding padmount-cleared arrestor and re fused-cust back on swalsh1 7-13-18 swalsh1 | -89.9743 | 30.0139 | 70127 | E | Council District E | Cyndi Nguyen
1292194419 | Yes | EAST ORLEANS | FAIR | 2018-06-22 18:09 | 2018-06-22 18:14 | 2018-06-22 18:45 | 2217 | ENOI | SERV | 1285160 | 43573509237 | DLIN | 6 | 1 | 36 | 36 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1285160 5 to SERV 1285160 5** --- hot leg connection burning up-changed connection-cust back on swalsh1 | -89.956 | 30.0601 | 70128 | E | Council District E | Joseph Giarrusso
1293268285 | Yes | ORLEANS | FAIR | 2018-07-10 19:12 | 2018-07-10 19:30 | 2018-07-10 20:03 | 2016 | ENOI | SERV | 65725 | 38236472706 | DLIN | 1 | 1 | 51 | 51 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 65725 12 to SERV 65725 12** --- changed connections on wilson rack jtatma1 | -90.1259 | 29.9612 | 70118 | A | Council District A | Jay Banks
1292086477 | Yes | EAST ORLEANS | FAIR | 2018-06-20 18:25 | 2018-06-20 18:56 | 2018-06-20 19:31 | 1001 | ENOI | SERV | 25812 | 41749492521 | DLIN | 6 | 1 | 66 | 66 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 25812 4 to SERV 25812 4** --- bad connections feeding wilson rack-changed connections-cust back on-voltage ok swalsh1 | -90.0142 | 30.0147 | 70126 | D | Council District D | Jay Banks
1292907471 | Yes | ALGIERS | FAIR | 2018-07-05 09:21 | 2018-07-05 09:21 | 2018-07-05 10:45 | W0115 | ENOI | SERV | 1529213 * | 4069746426 | DLIN | 81 | 1 | 84 | 84 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1529213 * 2 to SERV 1529213 * 1** --- connector at weatherhead nwashi1 | -90.0486 | 29.9372 | 70114 | C | Council District C | Jay Banks
1292300765 | Yes | EAST ORLEANS | FAIR | 2018-06-24 16:56 | 2018-06-24 16:56 | 2018-06-24 18:31 | 2212 | ENOI | SERV | 1414001 | 41541498537 | DLIN | 6 | 1 | 95 | 95 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Bad Main, spliced out, customers back in lights mjack11 | -90.0207 | 30.0312 | 70126 | E | Council District E | Jay Banks
1293783765 | Yes | ORLEANS | HEAT | 2018-07-19 12:13 | 2018-07-19 12:13 | 2018-07-19 13:50 | 2132 | ENOI | SERV | 1001056 | 39823460094 | DLIN | 1 | 1 | 96 | 96 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1001056 10 to SERV 1001056 1** --- changed hot leg connection at pole advised jbologn | -90.0763 | 29.9262 | 70130 | B | Council District B | Cyndi Nguyen
1292284697 | Yes | ORLEANS | FAIR | 2018-06-24 09:08 | 2018-06-24 09:08 | 2018-06-24 11:12 | 1912 | ENOI | SERV | 549283 | 38397456574 | DLIN | 1 | 1 | 124 | 124 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 549283 7 to SERV 549283 7** --- Made customer contact and repaired hot leg at the pole. Tested voltage 121/121/242 bmorvan | -90.1213 | 29.9169 | 70115 | A | Council District A | Jay Banks
1291680423 | Yes | ORLEANS | HEAT | 2018-06-13 15:07 | 2018-06-13 15:08 | 2018-06-13 17:12 | 1513 | ENOI | SERV | 73740 | 39320476474 | DLIN | 1 | 1 | 125 | 125 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 73740 6 to SECO 73740 6** --- tree fell when storm passed through area breaking connector at wilson rack. reepaired connector dsmit36 | -90.0916 | 29.9712 | 70119 | B | Council District B | Jay Banks
1293851748 | Yes | EAST ORLEANS | FAIR | 2018-07-20 12:01 | 2018-07-20 12:01 | 2018-07-20 16:04 | 1204 | ENOI | SERV | 1137688 * | 47368512889 | DLIN | 6 | 1 | 242 | 242 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1137688 * 2 to SERV 1137688 * 1** --- bad connection on hot leg on lighting pot-changed out connection-checked voltage ok-no cust contact swalsh1 7-20-18 swalsh1 | -89.8359 | 30.0687 | 70129 | E | Council District E | Jay Banks
1292568777 | Yes | EAST ORLEANS | HEAT | 2018-06-29 13:49 | 2018-06-29 13:49 | 2018-06-29 14:42 | 2217 | ENOI | SERV | 527123 | 43977513338 | DLIN | 6 | 1 | 53 | 53 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | fixed hot led in hand hole cbowden | -89.9432 | 30.0712 | 70128 | E | Council District E | Jared Brossett
1293265801 | Yes | EAST ORLEANS | FAIR | 2018-07-10 17:51 | 2018-07-10 17:51 | 2018-07-10 19:19 | 1610 | ENOI | SERV | SERVICE COND | 41781495437 | DLIN | 6 | 1 | 88 | 88 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | changed bad hot leg connection in hand hole cbowden | -90.0132 | 30.0227 | 70126 | E | Council District E | Jay Banks
1293395619 | Yes | ORLEANS | FAIR | 2018-07-12 19:11 | 2018-07-12 19:11 | 2018-07-12 20:40 | 1704 | ENOI | SERV | 687085 | 39697487407 | DLIN | 1 | 1 | 88 | 88 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | Changed **TFUS 687085 12 to SERV 687085 12** --- repaired broken neutral on pole jtatma1 | -90.0794 | 30.0012 | 70122 | D | Council District D | Jared Brossett
1294417168 | Yes | EAST ORLEANS | FAIR | 2018-07-28 19:14 | 2018-07-28 19:14 | 2018-07-28 21:25 | 1601 | ENOI | SERV | 1236281 | 44274500687 | DLIN | 6 | 1 | 130 | 130 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | made repairs in meter pan cscale1 | -89.9342 | 30.0363 | 70129 | E | Council District E | Kristin Palmer
1291939385 | Yes | EAST ORLEANS | FAIR | 2018-06-18 11:02 | 2018-06-18 11:02 | 2018-06-18 11:36 | 626 | ENOI | TFUS | 74893 | 41081482196 | DLIN | 6 | 1 | 34 | 34 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Lateral was blown refuse ok no customer contact cbower1 | -90.0358 | 29.9865 | 70126 | D | Council District D | Kristin Palmer
1291007987 | Yes | ALGIERS | HEAT | 2018-06-03 06:28 | 2018-06-03 06:28 | 2018-06-03 08:06 | W1715 | ENOI | TFUS | 1032742 | 4464545153 | DLIN | 81 | 1 | 98 | 98 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused bcleme1 | -89.9244 | 29.901 | 70131 | C | Council District C | Cyndi Nguyen
1290905240 | Yes | EAST ORLEANS | FAIR | 2018-06-01 10:47 | 2018-06-01 10:47 | 2018-06-01 13:46 | 1608 | ENOI | TFUS | 1052363 | 4175348603 | DLIN | 6 | 1 | 179 | 179 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | bad switch crew to fix | -90.0144 | 29.9968 | 70126 | E | Council District E | Kristin Palmer
1292371396 | Yes | ORLEANS CBD | COLD | 2018-06-25 14:38 | 2018-06-25 14:39 | 2018-06-25 15:30 | COMMO | ENOI | NTWK | XXX | 3989646938 | DLIN | 4 | 1 | 52 | 52 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | Went out with Delta feeder 269, restored thru field switching |  |  | 70122 | B | Council District B | Jay Banks
1294524039 | Yes | ORLEANS | FAIR | 2018-07-30 12:34 | 2018-07-30 12:34 | 2018-07-30 14:16 | 2025 | ENOI | ATS | ATS | 3923647087 | DLIN | 1 | 1 | 102 | 102 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | ATS for Times Picayune was hung up on feeder 1554 which was out due to a burnt open jumper |  |  | 70125 | B | Council District B | Kristin Palmer
1291158930 | Yes | EAST ORLEANS | THDR | 2018-06-05 12:25 | 2018-06-05 12:25 | 2018-06-05 14:09 | 1608 | ENOI | TFUS | 1052363 | 4175348603 | DLIN | 6 | 1 | 104 | 104 | CONDUCTOR | EOSC | Equipment - Shield Conductor | N | crew to pickup wire | -90.0144 | 29.9968 | 70126 | E | Council District E | Kristin Palmer
1292464553 | Yes | ORLEANS | FAIR | 2018-06-28 02:20 | 2018-06-28 02:20 | 2018-06-28 04:36 | 1912 | ENOI | TFUS | 622349 | 38317455698 | DLIN | 1 | 1 | 136 | 136 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.1239 | 29.9144 | 70118 | A | Council District A | Jay Banks
1293651021 | Yes | EAST ORLEANS | FAIR | 2018-07-17 10:11 | 2018-07-17 10:11 | 2018-07-17 14:05 | 1009 | ENOI | XFMR | 27226 | 41451496447 | DLIN | 6 | 1 | 234 | 234 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew replaced bad transformer (pwd) | -90.0235 | 30.0255 | 70126 | D | Council District D | Kristin Palmer
1292597874 | Yes | ALGIERS | FAIR | 2018-06-29 20:48 | 2018-06-29 20:48 | 2018-06-30 01:21 | W0725 | ENOI | TFUS | 1291710 | 4124846241 | DLIN | 81 | 1 | 273 | 273 | EQUIPMENT | ETRD | Equipment - Transformer | N | Transformer | -90.0312 | 29.9321 | 70114 | C | Council District C | Kristin Palmer
1294258059 | NO | EAST ORLEANS | HEAT | 2018-07-24 14:12 | 2018-07-24 14:12 | 2018-07-24 15:32 | 611 | ENOI | TFUS | 68173 | 41024475392 | DLIN | 6 | 1 | 0 | 0 | OTHER | UNKN | Inspected Unknown | N | Changed **TFUS 68173 17 to ERR 68173 [count]** --- MTR # 8054963, READ* 03729, MTR S PPOD TO BE ON, WAS OFF, 1107, 24JUL18 rbeaco | -90.0377 | 29.9678 | 70117 | D | Council District D | Kristin Palmer
1291282702 | Yes | EAST ORLEANS | FAIR | 2018-06-07 12:29 | 2018-06-07 12:29 | 2018-06-07 14:49 | 508 | ENOI | TFUS | 14318 | 40969493422 | DLIN | 6 | 1 | 140 | 140 | OTHER | UNKN | Inspected Unknown | N | found C phase transformer fuse blown-re fused ok-cust back on-voltage ok swalsh1 6-7-18 swalsh1 | -90.0389 | 30.0175 | 70126 | D | Council District D | Jay Banks
1291939819 | Yes | ORLEANS | THDR | 2018-06-18 11:12 | 2018-06-18 11:12 | 2018-06-18 13:09 | 2011 | ENOI | SERV | METER | 38359474189 | DLIN | 1 | 1 | 117 | 117 | HUMAN FACTORS | HECO | Other Error - Company (Describe in Remarks Field) | N | Changed **TFUS 65788 11 to SERV 65788 [count]** --- active acct, off at breaker with a company lock and yellow seal 6/18/1104 dgrison | -90.122 | 29.9652 | 70118 | A | Council District A | Kristin Palmer
1293264448 | Yes | EAST ORLEANS | FAIR | 2018-07-10 17:17 | 2018-07-10 17:17 | 2018-07-10 18:10 | 1702 | ENOI | SERV | SERVICE COND | 40362490171 | DLIN | 6 | 1 | 53 | 53 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | service brunt apart in tree splice together customer back on cbowden | -90.0582 | 30.0086 | 70122 | D | Council District D | Kristin Palmer
1294529133 | Yes | EAST ORLEANS | FAIR | 2018-07-30 14:13 | 2018-07-30 14:13 | 2018-07-30 15:25 | 1604 | ENOI | SERV | 1340962 * | 42745492716 | DLIN | 6 | 1 | 72 | 72 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 1340962 * 1 to SERV 1340962 * 1** --- repaired hot leg at transformer-aluminum burned out of lug-installed firecrackers swalsh1 | -89.9828 | 30.0149 | 70127 | E | Council District E | Kristin Palmer
1293518223 | Yes | ORLEANS | FAIR | 2018-07-15 19:36 | 2018-07-15 19:36 | 2018-07-15 21:28 | 907 | ENOI | SERV | 58559 | 40048476028 | DLIN | 1 | 1 | 112 | 112 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 58559 4 to SERV 58559 4** --- replaced service jtatma1 | -90.0685 | 29.9698 | 70116 | D | Council District D | Kristin Palmer
1293463337 | Yes | ORLEANS | FAIR | 2018-07-14 04:15 | 2018-07-14 04:24 | 2018-07-14 06:08 | 1913 | ENOI | SERV | 59836 * | 38699457852 | DLIN | 1 | 1 | 113 | 113 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | spliced out service jtatma1 | -90.1118 | 29.9203 | 70115 | B | Council District B | Jared Brossett
1293765343 | Yes | ORLEANS | RAIN | 2018-07-18 22:18 | 2018-07-18 22:18 | 2018-07-19 00:18 | 1913 | ENOI | SERV | 1486846 | 38717457840 | DLIN | 1 | 1 | 120 | 120 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | changed service from #4 to 1/O BP back in power jruffi1 | -90.1112 | 29.9203 | 70115 | B | Council District B | Kristin Palmer
1293157685 | Yes | ORLEANS | FAIR | 2018-07-08 20:13 | 2018-07-08 20:14 | 2018-07-08 22:36 | 1916 | ENOI | SERV | SERVICE | 38762466234 | DLIN | 1 | 1 | 143 | 143 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 57296 * 8 to SERV 57296 * 8** --- service burnt ran new service abengst | -90.1095 | 29.9433 | 70125 | A | Council District A | Jared Brossett
1291608053 | Yes | ALGIERS | FAIR | 2018-06-12 17:40 | 2018-06-12 17:40 | 2018-06-12 20:49 | W1713 | ENOI | SERV | 1170839 * | 4260745717 | DLIN | 81 | 1 | 189 | 189 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 1170839 * 9 to SERV 1170839 * 1** --- trees rubbing service wire bare/respliced customer good nwashi1 | -89.9885 | 29.9172 | 70131 | C | Council District C | Kristin Palmer
1291788191 | Yes | EAST ORLEANS | FAIR | 2018-06-15 06:27 | 2018-06-15 06:27 | 2018-06-15 11:06 | 2213 | ENOI | SERV | SERVICE | 44338508587 | DLIN | 6 | 1 | 279 | 279 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | crew to put drycell | -89.9319 | 30.058 | 70129 | E | Council District E | Kristin Palmer
1290914124 | Yes | EAST ORLEANS | FAIR | 2018-06-01 15:42 | 2018-06-01 15:42 | 2018-06-01 17:04 | 1203 | ENOI | TFUS | 1452358 | 44592496638 | DLIN | 6 | 1 | 82 | 82 | OTHER | UNKI | Unknown - Under Investigation | N | Refused B phase on terminal pole feeding transformer jvickna | -89.9243 | 30.025 | 70129 | E | Council District E | Kristin Palmer
1291827426 | Yes | EAST ORLEANS | FAIR | 2018-06-16 04:53 | 2018-06-16 04:53 | 2018-06-16 07:56 | 1603 | ENOI | TFUS | 1429309 | 42959501362 | DLIN | 6 | 1 | 183 | 183 | OTHER | UNKI | Unknown - Under Investigation | N | single phase underground out crew to check | -89.9757 | 30.0387 | 70127 | E | Council District E | Cyndi Nguyen
1292597771 | Yes | ALGIERS | THDR | 2018-06-29 20:41 | 2018-06-29 20:59 | 2018-06-29 22:27 | W1715 | ENOI | TFUS | 634932 | 4471045199 | DLIN | 81 | 2 | 212 | 106 | LIGHTNING | LGHT | Lightning | N | bad 25kva transformer changed out. customers back on. good volt check after install mtaruc | -89.9222 | 29.9022 | 70131 | C | Council District C | Kristin Palmer
1292075914 | Yes | ORLEANS | FAIR | 2018-06-20 14:35 | 2018-06-20 14:35 | 2018-06-20 18:48 | 907 | ENOI | TFUS | 1332528 | 39432474661 | DLIN | 1 | 2 | 506 | 253 | VEGETATION | VOHL | Overhanging Limb | N | tree limbs got in fuse ba cut in clear transformer refused ok jruffi1 | -90.0881 | 29.9662 | 70119 | B | Council District B | Jared Brossett
1291828529 | NO | EAST ORLEANS | FAIR | 2018-06-16 06:32 | 2018-06-16 06:35 | 2018-06-16 06:37 | 2216 | ENOI | SERV | SERVICE | 4282650283 | DLIN | 6 | 2 | 10 | 5 | OTHER | SCHD | Scheduled Interruption | N | crew working on line down the road bad cable | -97.0758 | 27.9066 | 70127 | E | Council District E | Kristin Palmer
1294371394 | Yes | EAST ORLEANS | HEAT | 2018-07-27 19:15 | 2018-07-27 19:19 | 2018-07-27 19:36 | 1710 | ENOI | TFUS | 79362 | 40478487725 | DLIN | 6 | 2 | 42 | 21 | OTHER | SCHD | Scheduled Interruption | N | Crew dropped out to make repairs. | -90.0545 | 30.0018 | 70122 | D | Council District D | Cyndi Nguyen
1292433595 | Yes | ALGIERS | FAIR | 2018-06-27 08:52 | 2018-06-27 08:56 | 2018-06-27 09:16 | W1725 | ENOI | TFUS | BY49453 | 4171846618 | DLIN | 81 | 2 | 48 | 24 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS BY49453 * 13 to TFUS BY49453 * 1** --- SEC crew changing transformer nwashi1 | -90.0161 | 29.9422 | 70114 | C | Council District C | Kristin Palmer
1292119728 | Yes | ALGIERS | FAIR | 2018-06-21 08:08 | 2018-06-21 08:36 | 2018-06-21 08:40 | W1725 | ENOI | SERV | SERVICE | 4263546048 | DLIN | 81 | 2 | 64 | 32 | OTHER | SCHD | Scheduled Interruption | N | crew | -89.9874 | 29.9263 | 70131 | C | Council District C | Kristin Palmer
1291100867 | Yes | ORLEANS | FAIR | 2018-06-04 11:25 | 2018-06-04 11:28 | 2018-06-04 12:48 | 2013 | ENOI | TFUS | 1336815 | 38362466415 | DLIN | 1 | 2 | 166 | 83 | OTHER | SCHD | Scheduled Interruption | N | PLANNED OUTAGE, CREW WORK 1315, 4/JUN/18 rbeaco | -90.1221 | 29.944 | 70118 | A | Council District A | Kristin Palmer
1294311639 | Yes | ORLEANS | FAIR | 2018-07-26 10:28 | 2018-07-26 10:37 | 2018-07-26 12:10 | 410 | ENOI | LFUS | SERVICE | 3852748733 | DLIN | 1 | 2 | 204 | 102 | OTHER | SCHD | Scheduled Interruption | N | crew on stie | -90.1162 | 30.0014 | 70124 | A | Council District A | Jared Brossett
1292005416 | Yes | ORLEANS | FAIR | 2018-06-19 08:45 | 2018-06-19 08:48 | 2018-06-19 11:30 | 1712 | ENOI | TFUS | 58921 | 39440475551 | DLIN | 1 | 2 | 330 | 165 | OTHER | SCHD | Scheduled Interruption | N | contractor opened in order to make repairs on pole and other equipment..........PC Jimmy Mathis......... | -90.0879 | 29.9687 | 70119 | B | Council District B | Jay Banks
1293355217 | Yes | ORLEANS | FAIR | 2018-07-12 09:57 | 2018-07-12 10:05 | 2018-07-12 13:30 | 1712 | ENOI | TFUS | SERVICE | 39784473061 | DLIN | 1 | 2 | 426 | 213 | OTHER | SCHD | Scheduled Interruption | N |  | -90.077 | 29.9617 | 70112 | B | Council District B | Joseph Giarrusso
1293713906 | Yes | ORLEANS | FAIR | 2018-07-18 09:00 | 2018-07-18 13:11 | 2018-07-18 14:25 | 1924 | ENOI | LFUS | 21478 | 3908246060 | DLIN | 1 | 2 | 650 | 325 | OTHER | SCHD | Scheduled Interruption | N | SCHEDULED OUTAGE, crew replacing pole, de-energized for workers safety | -90.0997 | 29.9276 | 70115 | B | Council District B | Jared Brossett
1293852912 | Yes | ALGIERS | HEAT | 2018-07-20 12:29 | 2018-07-20 12:29 | 2018-07-20 14:35 | W1713 | ENOI | TFUS | 478070 | 4231745770 | DLIN | 81 | 2 | 252 | 126 | VEGETATION | VINE | Vine Growing into Line | N | vines caused outage gcharl1 | -89.9976 | 29.9187 | 70131 | C | Council District C | Joseph Giarrusso
1291092439 | Yes | ORLEANS | FAIR | 2018-06-04 08:09 | 2018-06-04 08:28 | 2018-06-04 09:50 | 1921 | ENOI | SECO | 78049 | 38737460947 | DLIN | 1 | 2 | 202 | 101 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | repaired jumper on wilson rack advised jbologn | -90.1106 | 29.9287 | 70115 | B | Council District B | Jared Brossett
1292025466 | Yes | ORLEANS | FAIR | 2018-06-19 14:21 | 2018-06-19 15:01 | 2018-06-19 16:15 | 1705 | ENOI | TFUS | 32664 | 39784479447 | DLIN | 1 | 2 | 228 | 114 | EQUIPMENT | EARM | Equipment - Crossarm | N | broken wilson rack. changing out. shudso3 | -90.0769 | 29.9794 | 70119 | D | Council District D | Jared Brossett
1293484222 | Yes | EAST ORLEANS | FAIR | 2018-07-14 20:05 | 2018-07-14 20:05 | 2018-07-14 20:54 | 1612 | ENOI | TFUS | 79408 | 43498491194 | DLIN | 6 | 2 | 98 | 49 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refuse trans customers back in cbowden | -89.9591 | 30.0105 | 70129 | E | Council District E | Jared Brossett
1292867095 | Yes | ORLEANS | HEAT | 2018-07-04 09:38 | 2018-07-04 09:38 | 2018-07-04 10:32 | 1917 | ENOI | TFUS | 66165 | 39010458882 | DLIN | 1 | 2 | 108 | 54 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | transformer tested good and refused ok.. dsmit36 | -90.1019 | 29.923 | 70115 | B | Council District B | Kristin Palmer
1291147298 | Yes | EAST ORLEANS | FAIR | 2018-06-05 10:18 | 2018-06-05 10:18 | 2018-06-05 12:28 | 2216 | ENOI | TFUS | 1257304 | 42933501451 | DLIN | 6 | 2 | 260 | 130 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **TFUS 1257304 * 2 to TFUS 1257304 * 1** --- blown sand fuse feeding stiner transformer/refused ok/ dfahr | -89.9765 | 30.0388 | 70127 | E | Council District E | Joseph Giarrusso
1293097103 | Yes | EAST ORLEANS | FAIR | 2018-07-07 15:11 | 2018-07-07 15:11 | 2018-07-07 18:31 | 1601 | ENOI | TFUS | 3004042 | 4437449761 | DLIN | 6 | 2 | 400 | 200 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | crew to refuse lateral couldnt reach with truck crew to get 55 to refuse | -89.9306 | 30.028 | 70129 | E | Council District E | Jay Banks
1292875717 | Yes | ORLEANS | HEAT | 2018-07-04 14:12 | 2018-07-04 14:12 | 2018-07-04 15:24 | 2025 | ENOI | LFUS | 27765 | 39516471598 | DLIN | 1 | 2 | 144 | 72 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | latteral fuse blown refused ok... dsmit36 | -90.0855 | 29.9579 | 70112 | B | Council District B | Jay Banks
1292068000 | Yes | ORLEANS | FAIR | 2018-06-20 11:29 | 2018-06-20 11:29 | 2018-06-20 13:46 | 1915 | ENOI | TFUS | 1335239 | 39611466057 | DLIN | 1 | 2 | 272 | 136 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad 100 by crew to fix | -90.0828 | 29.9426 | 70113 | B | Council District B | Jay Banks
1290910652 | Yes | ALGIERS | FAIR | 2018-06-01 14:24 | 2018-06-01 14:24 | 2018-06-01 17:03 | W1726 | ENOI | TFUS | 1135197 | 4212246295 | DLIN | 81 | 2 | 318 | 159 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew | -90.0035 | 29.9332 | 70131 | C | Council District C | Joseph Giarrusso
1293008685 | Yes | ORLEANS | FAIR | 2018-07-06 16:00 | 2018-07-06 16:00 | 2018-07-06 20:56 | 907 | ENOI | XFMR | 1332528 | 39432474661 | DLIN | 1 | 2 | 592 | 296 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer | -90.0881 | 29.9662 | 70119 | B | Council District B | Jared Brossett
1293584130 | Yes | ORLEANS | FAIR | 2018-07-16 17:34 | 2018-07-16 18:03 | 2018-07-16 19:09 | 2011 | ENOI | SERV | 1400854 | 39268479955 | DLIN | 1 | 2 | 190 | 95 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | service burned near weatherhead spliced out ok jruffi1 | -90.0931 | 29.9809 | 70119 | A | Council District A | Cyndi Nguyen
1292057666 | Yes | ORLEANS | FAIR | 2018-06-20 07:30 | 2018-06-20 07:30 | 2018-06-20 08:30 | 2137 | ENOI | TFUS | 1000650 | 39838466018 | DLIN | 1 | 3 | 180 | 60 | HUMAN FACTORS | HNWK | Human Error - Non-Entergy Workers (Describe in Remarks) | N | Changed **TFUS 729711 14 to LFUS 729711 14** --- contactor diging up street bumbed pole and blew lat at clio and carondelet switches not in system no damage | -90.0756 | 29.9423 | 70113 | B | Council District B | Kristin Palmer
1292717288 | Yes | EAST ORLEANS | THDR | 2018-07-02 15:03 | 2018-07-02 15:03 | 2018-07-02 16:00 | 1601 | ENOI | TFUS | 1254224 | 4440749777 | DLIN | 6 | 3 | 171 | 57 | LIGHTNING | LGHT | Lightning | N |  | -89.9301 | 30.0282 | 70129 | E | Council District E | Kristin Palmer
1291591502 | Yes | ALGIERS | THDR | 2018-06-12 15:59 | 2018-06-12 19:36 | 2018-06-13 00:12 | W0713 | ENOI | TFUS | BY147599 | 4154845953 | DLIN | 81 | 3 | 1479 | 493 | LIGHTNING | LGHT | Lightning | N |  | -90.0219 | 29.924 | 70114 | C | Council District C | Joseph Giarrusso
1290959076 | Yes | ORLEANS | FAIR | 2018-06-02 16:57 | 2018-06-02 17:20 | 2018-06-02 20:38 | 1921 | ENOI | TFUS | 79334 | 38736460290 | DLIN | 1 | 3 | 660 | 220 | VEGETATION | VOHL | Overhanging Limb | N | tree branch across top side of transformer, cleared and refused ok droser | -90.1107 | 29.9269 | 70115 | B | Council District B | Jay Banks
1294259281 | NO | ORLEANS | FAIR | 2018-07-24 14:46 | 2018-07-24 15:09 | 2018-07-24 15:36 | 1914 | ENOI | TFUS | 529420 * | 38373459684 | DLIN | 1 | 3 | 0 | 0 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 529420 * 10 to CUST 529420 * 10** --- RELIABLE CREWS ARE WORKING ON THE LINES jmondy | -90.122 | 29.9253 | 70118 | A | Council District A | Jared Brossett
1292611481 | NO | ORLEANS | HEAT | 2018-06-30 09:51 | 2018-06-30 09:53 | 2018-06-30 09:56 | 408 | ENOI | TFUS | 603660 | 38702489258 | DLIN | 1 | 3 | 15 | 5 | OTHER | SCHD | Scheduled Interruption | N | crew outage | -90.1107 | 30.0066 | 70124 | A | Council District A | Jay Banks
1291800517 | Yes | ORLEANS | FAIR | 2018-06-15 13:54 | 2018-06-15 14:12 | 2018-06-15 14:46 | 1712 | ENOI | SERV | SERVICE | 3972447286 | DLIN | 1 | 3 | 156 | 52 | OTHER | SCHD | Scheduled Interruption | N | crew working | -90.0788 | 29.9612 | 70112 | B | Council District B | Joseph Giarrusso
1291446535 | Yes | EAST ORLEANS | FAIR | 2018-06-10 09:55 | 2018-06-10 12:03 | 2018-06-10 12:28 | 1203 | ENOI | TFUS | 1214554 | 44587497323 | DLIN | 6 | 3 | 459 | 153 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -89.9245 | 30.0269 | 70129 | E | Council District E | Joseph Giarrusso
1292981876 | Yes | EAST ORLEANS | FAIR | 2018-07-06 09:08 | 2018-07-06 09:50 | 2018-07-06 14:00 | 617 | ENOI | TFUS | 74444 | 41187489941 | DLIN | 6 | 3 | 876 | 292 | OTHER | SCHD | Scheduled Interruption | N | crew on sitre making repairs | -90.0321 | 30.0078 | 70126 | D | Council District D | Kristin Palmer
1293985051 | Yes | EAST ORLEANS | FAIR | 2018-07-21 06:59 | 2018-07-21 07:17 | 2018-07-21 08:43 | 2347 | ENOI | TFUS | 73813 | 41970477030 | DLIN | 6 | 3 | 312 | 104 | VEGETATION | VINE | Vine Growing into Line | N | vines refused okay | -90.0079 | 29.972 | 70117 | E | Council District E | Jared Brossett
1292152983 | Yes | EAST ORLEANS | FAIR | 2018-06-22 00:33 | 2018-06-22 00:53 | 2018-06-22 02:23 | 2347 | ENOI | TFUS | 73813 | 41970477030 | DLIN | 6 | 3 | 330 | 110 | VEGETATION | VINE | Vine Growing into Line | N | vines on transformer blew fuse-cleared vines on pole and re fused ok-cust back on swalsh1 | -90.0079 | 29.972 | 70117 | E | Council District E | Joseph Giarrusso
1294224070 | Yes | EAST ORLEANS | FAIR | 2018-07-23 18:58 | 2018-07-23 19:00 | 2018-07-23 20:48 | 2345 | ENOI | SECO | 1269952 | 41880473921 | DLIN | 6 | 3 | 330 | 110 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | hot leg down by sec conect/ repaired.. tbrock | -90.0107 | 29.9635 | 70117 | E | Council District E | Joseph Giarrusso
1292347786 | Yes | ORLEANS | FAIR | 2018-06-25 08:04 | 2018-06-25 08:04 | 2018-06-25 11:12 | 1708 | ENOI | TFUS | 1173367 | 40277486053 | DLIN | 1 | 3 | 564 | 188 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | someone must have bumped pole knock barrells open refused ok jbologn | -90.061 | 29.9973 | 70122 | D | Council District D | Jay Banks
1293572652 | Yes | ALGIERS | THDR | 2018-07-16 15:27 | 2018-07-16 18:47 | 2018-07-16 19:14 | W1715 | ENOI | TFUS | 1134763 | 4332745590 | DLIN | 81 | 3 | 681 | 227 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **TFUS 1134763 3 to TFUS 1134763 2** --- fuse link blown/ refused ok nwashi1 | -89.9658 | 29.9135 | 70131 | C | Council District C | Joseph Giarrusso
1291373904 | Yes | ORLEANS | FAIR | 2018-06-08 19:14 | 2018-06-08 19:14 | 2018-06-09 05:27 | 1712 | ENOI | TFUS | 69044 | 39878471421 | DLIN | 1 | 3 | 1839 | 613 | EQUIPMENT | EPOL | Equipment - Pole | N | Crew changing out pole at location | -90.0742 | 29.9572 | 70112 | C | Council District C | Cyndi Nguyen
1293478831 | Yes | EAST ORLEANS | FAIR | 2018-07-14 16:20 | 2018-07-14 17:52 | 2018-07-14 19:40 | 612 | ENOI | XFMR | 58275 | 41181478143 | DLIN | 6 | 3 | 600 | 200 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -90.0326 | 29.9753 | 70117 | D | Council District D | Cyndi Nguyen
1292395905 | Yes | EAST ORLEANS | FAIR | 2018-06-26 08:23 | 2018-06-26 09:24 | 2018-06-26 12:00 | 2214 | ENOI | TFUS | 646305 | 43056503158 | DLIN | 6 | 3 | 651 | 217 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew replaced bad trasns. jar | -89.9726 | 30.0435 | 70127 | E | Council District E | Jared Brossett
1292031808 | Yes | ALGIERS | FAIR | 2018-06-19 15:18 | 2018-06-19 15:18 | 2018-06-19 18:56 | W1713 | ENOI | TFUS | 1161233 | 4245845782 | DLIN | 81 | 3 | 654 | 218 | EQUIPMENT | ETRD | Equipment - Transformer | N | Leaking transformer crew changed out | -89.9931 | 29.919 | 70131 | C | Council District C | Kristin Palmer
1294289595 | Yes | EAST ORLEANS | FAIR | 2018-07-25 13:42 | 2018-07-25 13:42 | 2018-07-25 17:58 | 1605 | ENOI | XFMR | 618840 | 43369502475 | DLIN | 6 | 3 | 768 | 256 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace transformer...complete | -89.9628 | 30.0415 | 70128 | E | Council District E | Joseph Giarrusso
1293872116 | Yes | ORLEANS | FAIR | 2018-07-20 17:03 | 2018-07-20 23:37 | 2018-07-21 01:34 | 2135 | ENOI | XFMR | 1106785 | 39865463537 | DLIN | 1 | 3 | 1530 | 510 | EQUIPMENT | ETRD | Equipment - Transformer | N | Crew to change 50by transformer | -90.0747 | 29.9356 | 70130 | B | Council District B | Kristin Palmer
1294246751 | Yes | ALGIERS | HEAT | 2018-07-24 09:47 | 2018-07-24 09:47 | 2018-07-24 10:53 | W1726 | ENOI | TFUS | 680179 | 4214446283 | DLIN | 81 | 4 | 264 | 66 | ANIMAL | RBRD | Animal - Bird Reportable Incident (Mortality or Injury) | N | refused ok zwashin | -90.0028 | 29.9329 | 70131 | C | Council District C | Jared Brossett
1291562168 | Yes | ORLEANS | FAIR | 2018-06-12 07:43 | 2018-06-12 09:15 | 2018-06-12 09:33 | 2013 | ENOI | TFUS | 530883 | 38075466184 | DLIN | 1 | 4 | 440 | 110 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | removed rat off transformer installed guad refude ok jbologn | -90.1313 | 29.9433 | 70118 | A | Council District A | Kristin Palmer
1292398574 | Yes | ORLEANS | FAIR | 2018-06-26 09:49 | 2018-06-26 09:49 | 2018-06-26 11:41 | 2132 | ENOI | TFUS | 1000710 | 39736463869 | DLIN | 1 | 4 | 448 | 112 | VEGETATION | VOHL | Overhanging Limb | N | refused ok taken out by tree trimmers advised jbologn | -90.0789 | 29.9364 | 70130 | B | Council District B | Kristin Palmer
1291234810 | Yes | EAST ORLEANS | FAIR | 2018-06-06 09:20 | 2018-06-06 09:47 | 2018-06-06 09:49 | 2346 | ENOI | DIS | 23110 | 4189747238 | DLIN | 6 | 4 | 116 | 29 | OTHER | SCHD | Scheduled Interruption | N | Crew On Site working | -90.0102 | 29.9592 | 70117 | E | Council District E | Kristin Palmer
1294459645 | Yes | EAST ORLEANS | FAIR | 2018-07-29 07:25 | 2018-07-29 08:27 | 2018-07-29 08:45 | 613 | ENOI | LFUS | SERVICE | 4062148302 | DLIN | 6 | 4 | 320 | 80 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0503 | 29.9889 | 70122 | D | Council District D | Cyndi Nguyen
1291321545 | Yes | EAST ORLEANS | FAIR | 2018-06-07 21:56 | 2018-06-07 22:03 | 2018-06-08 06:00 | 2212 | ENOI | TFUS | 3007423 | 4217850203 | DLIN | 6 | 4 | 1936 | 484 | VEGETATION | VINE | Vine Growing into Line | N | vines covering transf here | -90.0003 | 30.0407 | 70126 | E | Council District E | Kristin Palmer
1293167743 | Yes | ORLEANS | FAIR | 2018-07-09 07:21 | 2018-07-09 08:46 | 2018-07-09 08:28 | 615 | ENOI | SBKR | 615 | 4081248420 | DLIN | 1 | 4 | 268 | 67 | EQUIPMENT | EARR | Equipment - Arrestor | N | customer ct on disc 55999. case | -90.0442 | 29.9921 | 70126 | D | Council District D | Jared Brossett
1293543140 | NO | ALGIERS | FAIR | 2018-07-16 07:13 | 2018-07-16 07:16 | 2018-07-16 07:41 | W0113 | ELA | TFUS | 1042913 | 4089346410 | DLIN | 81 | 4 | 112 | 28 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | fuse link blown/ refused ok nwashi1 | -90.0423 | 29.9368 | 70114 | C | Council District C | Kristin Palmer
1291440130 | Yes | ORLEANS | HEAT | 2018-06-10 05:45 | 2018-06-10 06:27 | 2018-06-10 09:00 | 400 | ENOI | TFUS | 24127 | 38338480226 | DLIN | 1 | 4 | 780 | 195 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | fuse link open in fuse not blown but broken tail . refused and back in lights advised customer jdomang | -90.1225 | 29.9819 | 70124 | A | Council District A | Jay Banks
1293476648 | Yes | EAST ORLEANS | FAIR | 2018-07-14 16:20 | 2018-07-14 16:48 | 2018-07-14 17:39 | 612 | ENOI | LFUS | 21126 | 4120947834 | DLIN | 6 | 4 | 316 | 79 | EQUIPMENT | ETRD | Equipment - Transformer | N | Changed **LFUS 21126 4 to LFUS 21126 7** --- Refused lateral--C phase sw# 21126---Transformer bad at 2018 Bartholomew, called crew jvickna | -90.0319 | 29.9758 | 70117 | D | Council District D | Jay Banks
1291444015 | Yes | ORLEANS | FAIR | 2018-06-10 09:06 | 2018-06-10 09:19 | 2018-06-10 11:14 | 400 | ENOI | TFUS | 24127 | 38338480226 | DLIN | 1 | 4 | 512 | 128 | EQUIPMENT | ETRD | Equipment - Transformer | N | transformer failed crew to replace | -90.1225 | 29.9819 | 70124 | A | Council District A | Jared Brossett
1292266737 | Yes | ORLEANS | FAIR | 2018-06-23 20:44 | 2018-06-23 20:44 | 2018-06-24 00:30 | 1915 | ENOI | TFUS | 70502 | 39382464977 | DLIN | 1 | 4 | 904 | 226 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change transformer | -90.0901 | 29.9396 | 70113 | B | Council District B | Kristin Palmer
1294501891 | Yes | EAST ORLEANS | FAIR | 2018-07-29 21:37 | 2018-07-29 21:37 | 2018-07-30 03:16 | 2215 | ENOI | TFUS | 1048550 | 43158506354 | DLIN | 6 | 4 | 1356 | 339 | EQUIPMENT | ETRD | Equipment - Transformer | N | changed transformer | -89.9693 | 30.0522 | 70128 | E | Council District E | Jared Brossett
1294132362 | Yes | EAST ORLEANS | FAIR | 2018-07-22 14:35 | 2018-07-22 15:05 | 2018-07-22 16:40 | 611 | ENOI | TFUS | 74727 | 40968478122 | DLIN | 6 | 4 | 500 | 125 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | repaired lead on transformer | -90.0394 | 29.9752 | 70117 | D | Council District D | Jay Banks
1292588845 | NO | ORLEANS | THDR | 2018-06-29 17:52 | 2018-06-29 17:52 | 2018-06-29 17:52 | 1541 | ENOI | SBKR | 1541 | 3950946991 | DLIN | 1 | 4 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N |  | -90.0858 | 29.9532 | 70113 | B | Council District B | Jay Banks
1292591650 | Yes | ORLEANS | THDR | 2018-06-29 18:29 | 2018-06-29 21:07 | 2018-06-29 22:41 | 1916 | ENOI | TFUS | 63201 | 38971464569 | DLIN | 1 | 5 | 1260 | 252 | LIGHTNING | LGHT | Lightning | N | bad pot | -90.103 | 29.9386 | 70115 | B | Council District B | Jay Banks
1292403232 | Yes | ORLEANS | FAIR | 2018-06-26 12:44 | 2018-06-26 13:04 | 2018-06-26 14:00 | 1711 | ENOI | LFUS | 67965 | 3961148021 | DLIN | 1 | 5 | 380 | 76 | OTHER | SCHD | Scheduled Interruption | N | lone is out for repairs. jar | -90.0822 | 29.9815 | 70119 | A | Council District A | Cyndi Nguyen
1293641840 | Yes | EAST ORLEANS | RAIN | 2018-07-17 06:34 | 2018-07-17 06:34 | 2018-07-17 08:46 | 2345 | ENOI | TFUS | 27698 | 42133476625 | DLIN | 6 | 5 | 660 | 132 | EQUIPMENT | EARR | Equipment - Arrestor | N | Changed **TFUS 73729 5 to TFUS 27698 5** --- loc fed from b phase lateral sw 27698-outage from arrestor blowing lateral swalsh1 | -90.0026 | 29.9708 | 70117 | E | Council District E | Cyndi Nguyen
1293507610 | Yes | ORLEANS | HEAT | 2018-07-15 16:05 | 2018-07-15 16:11 | 2018-07-15 17:18 | 1705 | ENOI | SECO | X3422 | 39567477906 | DLIN | 1 | 5 | 365 | 73 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 21 to SECO [id] 5** --- tfus not out. sec connector at another pole was open dsmit36 | -90.0838 | 29.9751 | 70119 | A | Council District A | Jared Brossett
1294388743 | Yes | EAST ORLEANS | FAIR | 2018-07-28 11:27 | 2018-07-28 11:27 | 2018-07-28 14:43 | 1204 | ENOI | LFUS | 35367 | 50073540415 | DLIN | 6 | 5 | 980 | 196 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Refused Lat# 35367 due to machine hit primary wire at 25815 chef hwy made customer contact cbower1 NO PID REQUIRED PER NETWORK (BOWERS) | -89.7491 | 30.1434 | 70129 | E | Council District E | Kristin Palmer
1291577437 | Yes | ORLEANS | FAIR | 2018-06-12 12:54 | 2018-06-12 12:54 | 2018-06-12 14:46 | 1513 | ENOI | TFUS | 64632 | 39402476384 | DLIN | 1 | 5 | 560 | 112 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -90.0889 | 29.971 | 70119 | B | Council District B | Kristin Palmer
1291458075 | Yes | EAST ORLEANS | THDR | 2018-06-10 13:08 | 2018-06-10 13:32 | 2018-06-10 15:29 | 2211 | ENOI | TFUS | 1048973 | 42449499518 | DLIN | 6 | 5 | 705 | 141 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace transformer | -89.9918 | 30.0336 | 70127 | E | Council District E | Joseph Giarrusso
1293426113 | Yes | EAST ORLEANS | FAIR | 2018-07-13 09:56 | 2018-07-13 09:56 | 2018-07-13 13:20 | 2213 | ENOI | XFMR | 80267 | 43838507814 | DLIN | 6 | 5 | 1020 | 204 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -89.9477 | 30.0562 | 70128 | E | Council District E | Joseph Giarrusso
1292458880 | Yes | EAST ORLEANS | HEAT | 2018-06-27 19:53 | 2018-06-27 19:59 | 2018-06-27 23:34 | 2211 | ENOI | TFUS | 1048973 | 42449499518 | DLIN | 6 | 5 | 1105 | 221 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change transformer | -89.9918 | 30.0336 | 70127 | E | Council District E | Jay Banks
1294367922 | Yes | ALGIERS | FAIR | 2018-07-27 14:51 | 2018-07-27 16:30 | 2018-07-27 18:35 | W1715 | ENOI | ELBO | 4377645137 | 4377645137 | DLIN | 81 | 5 | 1120 | 224 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot crew changed out. | -97.0758 | 27.9066 | 70131 | C | Council District C | Jay Banks
1294200398 | Yes | ALGIERS | HEAT | 2018-07-23 14:11 | 2018-07-23 14:11 | 2018-07-23 15:27 | W1715 | ENOI | TFUS | BY180483 | 4387345102 | DLIN | 81 | 5 | 380 | 76 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | changed bus bar zwashin | -89.9488 | 29.8999 | 70131 | C | Council District C | Jay Banks
1291808815 | Yes | ALGIERS | FAIR | 2018-06-15 16:07 | 2018-06-15 17:38 | 2018-06-15 18:03 | W0115 | ENOI | TFUS | 1296460 | 4073846378 | DLIN | 81 | 6 | 696 | 116 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | non reportable bird gcharl1 | -90.0473 | 29.936 | 70114 | C | Council District C | Joseph Giarrusso
1291028010 | Yes | EAST ORLEANS | FAIR | 2018-06-03 14:32 | 2018-06-03 14:48 | 2018-06-03 15:06 | 626 | ENOI | TFUS | 58285 | 41044484517 | DLIN | 6 | 6 | 204 | 34 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel took out transformer, refused ok, INSTALLED ANIMAL GAURD, made cust contact atampl1 | -90.0368 | 29.9928 | 70126 | D | Council District D | Joseph Giarrusso
1291253800 | Yes | ORLEANS | FAIR | 2018-06-06 17:24 | 2018-06-06 17:52 | 2018-06-06 18:14 | 2021 | ENOI | LFUS | 28040 | 3936746714 | DLIN | 1 | 6 | 300 | 50 | OTHER | SCHD | Scheduled Interruption | N | crew to fix broken pole | -90.0903 | 29.9454 | 70125 | B | Council District B | Jay Banks
1293130307 | Yes | EAST ORLEANS | FAIR | 2018-07-08 06:50 | 2018-07-08 07:53 | 2018-07-08 08:05 | 1710 | ENOI | LFUS | 21868 | 4061848676 | DLIN | 6 | 6 | 450 | 75 | OTHER | SCHD | Scheduled Interruption | N | CREW ON SITE MAKING REPAIRS | -90.0501 | 29.9993 | 70122 | D | Council District D | Cyndi Nguyen
1293776626 | Yes | ORLEANS | FAIR | 2018-07-19 09:38 | 2018-07-19 09:42 | 2018-07-19 10:11 | 2015 | ENOI | LFUS | 69508 | 38538470858 | DLIN | 1 | 6 | 198 | 33 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | Changed **TFUS 54061 * 6 to LFUS 54061 * 6** --- refused C phase of lat. 69508 vegation in rear property may have taken it out refused ok jbologn | -90.1165 | 29.956 | 70125 | A | Council District A | Jared Brossett
1294360925 | Yes | ALGIERS | HEAT | 2018-07-27 11:32 | 2018-07-27 11:34 | 2018-07-27 12:47 | W1726 | ENOI | TFUS | 1210645 | 4218045811 | DLIN | 81 | 6 | 450 | 75 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | tree pulled down service line open wire secondary slipped together hold meter number 812994 for inspection and permit zwashin | -90.0019 | 29.9199 | 70131 | C | Council District C | Cyndi Nguyen
1292302580 | Yes | EAST ORLEANS | FAIR | 2018-06-24 16:48 | 2018-06-24 18:16 | 2018-06-24 18:32 | 2212 | ENOI | SECO | 14970 | 4152649910 | DLIN | 6 | 6 | 624 | 104 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **LFUS 14970 48 to LFUS 14970 5** --- Fixed bad main underground. Customers back in lights mjack11 | -90.0211 | 30.0327 | 70126 | E | Council District E | Jared Brossett
1292243608 | Yes | EAST ORLEANS | FAIR | 2018-06-23 10:37 | 2018-06-23 10:37 | 2018-06-23 11:36 | 613 | ENOI | TFUS | 61194 | 40537480229 | DLIN | 6 | 6 | 354 | 59 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew onsite making repairs | -90.0531 | 29.9812 | 70117 | D | Council District D | Joseph Giarrusso
1292420069 | Yes | EAST ORLEANS | FAIR | 2018-06-26 18:25 | 2018-06-26 18:31 | 2018-06-26 22:23 | 623 | ENOI | TFUS | 1320889 | 40419477091 | DLIN | 6 | 6 | 1428 | 238 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lat 21153lights back on weather cschexn | -90.0568 | 29.9726 | 70117 | C | Council District C | Jay Banks
1291101038 | Yes | EAST ORLEANS | FOGG | 2018-06-04 11:30 | 2018-06-04 11:30 | 2018-06-04 14:01 | 2212 | ENOI | TFUS | 1181069 | 41357498850 | DLIN | 6 | 6 | 906 | 151 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | BT-TRANSFORMER FUSE BLOWN jmondy | -90.0265 | 30.0322 | 70126 | D | Council District D | Jared Brossett
1292696481 | Yes | EAST ORLEANS | FAIR | 2018-07-02 06:32 | 2018-07-02 09:21 | 2018-07-02 13:20 | 1612 | ENOI | LFUS | 21779 | 4294149194 | DLIN | 6 | 6 | 2448 | 408 | EQUIPMENT | EPOL | Equipment - Pole | N |  | -89.9766 | 30.0127 | 70127 | E | Council District E | Jared Brossett
1291578450 | Yes | EAST ORLEANS | FAIR | 2018-06-12 13:24 | 2018-06-12 13:24 | 2018-06-12 15:11 | 2223 | ENOI | TFUS | 3005248 | 43296508218 | DLIN | 6 | 6 | 642 | 107 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -89.9649 | 30.0573 | 70128 | E | Council District E | Cyndi Nguyen
1292365163 | Yes | ORLEANS | FAIR | 2018-06-25 11:59 | 2018-06-25 11:59 | 2018-06-25 14:31 | 1923 | ENOI | TFUS | 60907 | 39099458618 | DLIN | 1 | 6 | 912 | 152 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew replaced bad trans. jar | -90.0992 | 29.9222 | 70115 | B | Council District B | Cyndi Nguyen
1292069724 | Yes | EAST ORLEANS | FAIR | 2018-06-20 12:44 | 2018-06-20 12:44 | 2018-06-20 15:41 | 1002 | ENOI | TFUS | 22812 | 42133491503 | DLIN | 6 | 6 | 1062 | 177 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to fix | -90.0022 | 30.0118 | 70126 | E | Council District E | Joseph Giarrusso
1293469242 | Yes | ORLEANS | FAIR | 2018-07-14 10:09 | 2018-07-14 10:27 | 2018-07-14 14:15 | 2147 | ENOI | XFMR | 61445 | 39459460118 | DLIN | 1 | 6 | 1476 | 246 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -90.0878 | 29.9262 | 70115 | B | Council District B | Joseph Giarrusso
1293829751 | Yes | ALGIERS | FAIR | 2018-07-20 06:17 | 2018-07-20 06:20 | 2018-07-20 11:18 | W1714 | ENOI | XFMR | 1192239 | 4249345685 | DLIN | 81 | 6 | 1806 | 301 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change transformer | -89.9921 | 29.9163 | 70131 | C | Council District C | Jay Banks
1291741909 | Yes | ORLEANS | FAIR | 2018-06-14 06:43 | 2018-06-14 08:37 | 2018-06-14 10:41 | 406 | ENOI | TFUS | 17075 | 38928491918 | DLIN | 1 | 6 | 1428 | 238 | OTHER | UNKN | Inspected Unknown | N | FUSE AROUND AT 13212 WAS OUT REFUSED OKAY | -90.1034 | 30.0138 | 70124 | A | Council District A | Jared Brossett
1294307339 | Yes | ORLEANS | HEAT | 2018-07-26 08:33 | 2018-07-26 08:39 | 2018-07-26 09:42 | 503 | ENOI | TFUS | 50559 | 40040494170 | DLIN | 1 | 7 | 483 | 69 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel took it out refused ok and tested fine per 305 jruffi1 | -90.0681 | 30.0197 | 70122 | D | Council District D | Kristin Palmer
1291101021 | Yes | ALGIERS | FAIR | 2018-06-04 11:29 | 2018-06-04 11:29 | 2018-06-04 11:51 | W1725 | ENOI | TFUS | BY174250 | 4143946615 | DLIN | 81 | 7 | 154 | 22 | HUMAN FACTORS | HCSC | Contractor - Substation (Describe in remarks) | N | Changed **TFUS BY174250 14 to TFUS BY174250 1** --- contractor on site/ customer back on nwashi1 | -90.025 | 29.9423 | 70114 | C | Council District C | Jared Brossett
1293282664 | Yes | EAST ORLEANS | FAIR | 2018-07-11 08:16 | 2018-07-11 08:16 | 2018-07-11 09:33 | 510 | ENOI | TFUS | 1364833 | 40523493250 | DLIN | 6 | 7 | 539 | 77 | HUMAN FACTORS | HNWK | Human Error - Non-Entergy Workers (Describe in Remarks) | N | refused transformer ok. tree trimming crew got limb across open wire secondary. made contact with tree crew. cbower1 | -90.0529 | 30.0172 | 70122 | D | Council District D | Kristin Palmer
1294523136 | Yes | ALGIERS | FAIR | 2018-07-30 12:08 | 2018-07-30 13:43 | 2018-07-30 13:52 | W1715 | ENOI | TFUS | BY90480 | 4287945628 | DLIN | 81 | 7 | 728 | 104 | LIGHTNING | LGHT | Lightning | N | refused ok zwashin | -89.9799 | 29.9147 | 70131 | C | Council District C | Jared Brossett
1291741888 | Yes | ORLEANS | FAIR | 2018-06-14 06:40 | 2018-06-14 06:40 | 2018-06-14 07:36 | 2013 | ENOI | TFUS | 531586 | 38048464501 | DLIN | 1 | 7 | 385 | 55 | VEGETATION | VOHL | Overhanging Limb | N | refused transformer found limb on trans jbologn | -90.1322 | 29.9387 | 70118 | A | Council District A | Joseph Giarrusso
1293705199 | Yes | EAST ORLEANS | HEAT | 2018-07-18 01:41 | 2018-07-18 01:43 | 2018-07-18 04:22 | 1604 | ENOI | TFUS | 3007421 | 42699493971 | DLIN | 6 | 7 | 1120 | 160 | HUMAN FACTORS | VHCL | Vehicle | N | car struck pole. took out TFUS AND SECONDARY DOWN. PICK UP SECONDARY AND REFUSE TRANSFROMER CUST. BACK IN LIGHTS tduncan | -89.9843 | 30.0184 | 70127 | E | Council District E | Jared Brossett
1293247437 | Yes | EAST ORLEANS | FAIR | 2018-07-10 08:34 | 2018-07-10 08:38 | 2018-07-10 11:03 | 2347 | ENOI | TFUS | 71281 | 41144472535 | DLIN | 6 | 7 | 1043 | 149 | VEGETATION | VINE | Vine Growing into Line | N | cleared vines from pole and transformer. created ticket for vegetation to completely clear vines. refused transformer. made customer contact. cbower1 | -90.0341 | 29.9598 | 70117 | C | Council District C | Jay Banks
1293362293 | Yes | ALGIERS | HEAT | 2018-07-12 11:31 | 2018-07-12 11:35 | 2018-07-12 13:39 | W1726 | ENOI | XFMR | SERVICE | 4215245787 | DLIN | 81 | 7 | 896 | 128 | EQUIPMENT | EARR | Equipment - Arrestor | N | Changed **LFUS 34256 13 to XFMR [id] 13** --- changed arrestor on transformer zwashin | -90.0028 | 29.9192 | 70131 | C | Council District C | Cyndi Nguyen
1292797845 | Yes | ORLEANS | FAIR | 2018-07-03 12:37 | 2018-07-03 17:18 | 2018-07-03 20:06 | 1917 | ENOI | TFUS | 63584 | 39009458966 | DLIN | 1 | 7 | 3143 | 449 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | riser repaired | -90.1019 | 29.9232 | 70115 | B | Council District B | Jared Brossett
1292061751 | Yes | ORLEANS | HEAT | 2018-06-20 08:43 | 2018-06-20 08:50 | 2018-06-20 13:46 | 2147 | ENOI | TFUS | 75940 | 39453461258 | DLIN | 1 | 7 | 2121 | 303 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **TFUS 75940 * 7 to TFUS 75940 * 1** --- stinger pot blew last week during storm. refused ok dsmit36 | -90.0879 | 29.9293 | 70115 | B | Council District B | Cyndi Nguyen
1294139989 | Yes | ALGIERS | FAIR | 2018-07-22 16:05 | 2018-07-22 16:34 | 2018-07-22 17:44 | W1726 | ENOI | TFUS | 1407229 | 4207245684 | DLIN | 81 | 7 | 693 | 99 | Summary Missing | EONE | Equipment - Neutral / Shield Conductor | N | open wire neutral down in rear splice back sag and restore power clear vines off of transformer pole dchiass | -90.0053 | 29.9165 | 70131 | C | Council District C | Jared Brossett
1292787471 | Yes | EAST ORLEANS | FAIR | 2018-07-03 08:30 | 2018-07-03 08:30 | 2018-07-03 10:23 | 2346 | ENOI | TFUS | 73042 | 41375473032 | DLIN | 6 | 7 | 791 | 113 | EQUIPMENT | ETRD | Equipment - Transformer | N | Replaced ok | -90.0267 | 29.9613 | 70117 | E | Council District E | Kristin Palmer
1293772067 | Yes | ORLEANS | FAIR | 2018-07-19 06:06 | 2018-07-19 07:00 | 2018-07-19 10:20 | 1709 | ENOI | XFMR | 69580 | 39931480106 | DLIN | 1 | 7 | 1778 | 254 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -90.0722 | 29.981 | 70119 | D | Council District D | Jared Brossett
1292465426 | Yes | EAST ORLEANS | FAIR | 2018-06-28 05:06 | 2018-06-28 05:12 | 2018-06-28 09:21 | 1205 | ENOI | TFUS | 1048742 | 44864501765 | DLIN | 6 | 7 | 1785 | 255 | EQUIPMENT | ETRD | Equipment - Transformer | N | replaced transformer | -89.9155 | 30.0391 | 70129 | E | Council District E | Kristin Palmer
1291735356 | Yes | ALGIERS | FAIR | 2018-06-13 21:15 | 2018-06-13 22:48 | 2018-06-13 23:06 | W1713 | ENOI | TFUS | 1417734 | 4264345881 | DLIN | 81 | 7 | 770 | 110 | OTHER | UNKN | Inspected Unknown | N |  | -89.9873 | 29.9217 | 70131 | C | Council District C | Kristin Palmer
1294437604 | Yes | ORLEANS | FAIR | 2018-07-29 02:28 | 2018-07-29 07:37 | 2018-07-29 08:10 | 1914 | ENOI | SECO | 77590 * | 38903461840 | DLIN | 1 | 7 | 2394 | 342 | Summary Missing | SECF | Secondary cable | N | Changed **TFUS 77590 * 13 to SECO 77590 * 7** --- secondary burnt down spliced out rdeano | -90.1052 | 29.9311 | 70115 | B | Council District B | Cyndi Nguyen
1294148446 | Yes | ALGIERS | HEAT | 2018-07-22 17:48 | 2018-07-22 18:07 | 2018-07-22 18:15 | W1726 | ENOI | TFUS | 1407229 | 4207245684 | DLIN | 81 | 7 | 189 | 27 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | secondary down | -90.0053 | 29.9165 | 70131 | C | Council District C | Cyndi Nguyen
1294152363 | Yes | ALGIERS | HEAT | 2018-07-22 18:29 | 2018-07-22 18:38 | 2018-07-22 19:01 | W1726 | ENOI | TFUS | 1407229 | 4207245684 | DLIN | 81 | 7 | 224 | 32 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | picked up secondaries in the rear at this location | -90.0053 | 29.9165 | 70131 | C | Council District C | Cyndi Nguyen
1291292240 | Yes | EAST ORLEANS | HEAT | 2018-06-07 17:45 | 2018-06-07 17:53 | 2018-06-07 18:34 | 2213 | ENOI | TFUS | 677354 | 44503508573 | DLIN | 6 | 7 | 343 | 49 | OTHER | UNKI | Unknown - Under Investigation | N | nothing found jsoniat | -89.9267 | 30.0579 | 70129 | E | Council District E | Kristin Palmer
1291656497 | Yes | EAST ORLEANS | FAIR | 2018-06-13 09:19 | 2018-06-13 11:15 | 2018-06-13 11:47 | 1710 | ENOI | TFUS | 58117 | 40689485669 | DLIN | 6 | 8 | 1176 | 147 | ANIMAL | ASQL | Animal - Squirrel | N | Refused transformer due to squirrel jvickna | -90.048 | 29.9962 | 70122 | D | Council District D | Jay Banks
1294269408 | Yes | EAST ORLEANS | FAIR | 2018-07-24 22:26 | 2018-07-24 22:41 | 2018-07-24 22:43 | 626 | ENOI | LFUS | 21216 | 4109648387 | DLIN | 6 | 8 | 136 | 17 | OTHER | SCHD | Scheduled Interruption | N | crew had out to make repairs | -90.0354 | 29.9911 | 70126 | D | Council District D | Kristin Palmer
1293641150 | Yes | ORLEANS | FAIR | 2018-07-17 05:16 | 2018-07-17 06:24 | 2018-07-17 07:16 | 1922 | ENOI | TFUS | 62945 | 39085466625 | DLIN | 1 | 8 | 960 | 120 | VEGETATION | VINE | Vine Growing into Line | N | cleared vines and refused transformer jtatma1 | -90.0992 | 29.9443 | 70125 | B | Council District B | Cyndi Nguyen
1292477485 | Yes | ALGIERS | FAIR | 2018-06-28 12:23 | 2018-06-28 12:23 | 2018-06-28 14:52 | W1725 | ENOI | TFUS | BY122479 | 4114546281 | DLIN | 81 | 8 | 1192 | 149 | VEGETATION | VINE | Vine Growing into Line | N | Changed **TFUS BY122479 14 to TFUS BY122479 1** --- vines growing on transformer / cleared thwe base but follow up still needed nwashi1 | -90.0344 | 29.9332 | 70114 | C | Council District C | Kristin Palmer
1290949690 | Yes | EAST ORLEANS | FAIR | 2018-06-02 13:45 | 2018-06-02 13:45 | 2018-06-02 15:25 | 611 | ENOI | TFUS | 28279 | 41228476664 | DLIN | 6 | 8 | 800 | 100 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | sec down | -90.0312 | 29.9712 | 70117 | D | Council District D | Jared Brossett
1294428021 | Yes | ORLEANS | THDR | 2018-07-28 21:48 | 2018-07-28 23:18 | 2018-07-29 00:26 | 406 | ENOI | LFUS | 17707 | 3888149319 | DLIN | 1 | 8 | 1264 | 158 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | crew picking up primary in alley | -90.1048 | 30.0174 | 70124 | A | Council District A | Kristin Palmer
1291569903 | Yes | ALGIERS | FAIR | 2018-06-12 10:39 | 2018-06-12 10:39 | 2018-06-12 12:09 | W1725 | ENOI | TFUS | BY65450 | 4119346636 | DLIN | 81 | 8 | 720 | 90 | EQUIPMENT | ETRD | Equipment - Transformer | N | - Transformer change | -90.0328 | 29.9429 | 70114 | C | Council District C | Kristin Palmer
1292301512 | Yes | EAST ORLEANS | HEAT | 2018-06-24 17:35 | 2018-06-24 17:38 | 2018-06-24 21:36 | 623 | ENOI | TFUS | 70538 | 40741474710 | DLIN | 6 | 8 | 1928 | 241 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer | -90.0467 | 29.966 | 70117 | C | Council District C | Jay Banks
1291949022 | Yes | ORLEANS | THDR | 2018-06-18 12:55 | 2018-06-18 12:55 | 2018-06-18 13:29 | 503 | ENOI | TFUS | 1395464 | 40072493272 | DLIN | 1 | 8 | 272 | 34 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | #2 cu secondary got together in span burnt down repaired refused ok jbologn | -90.0671 | 30.0172 | 70122 | D | Council District D | Cyndi Nguyen
1293864271 | Yes | ORLEANS | HEAT | 2018-07-20 15:26 | 2018-07-20 15:26 | 2018-07-20 18:03 | 407 | ENOI | TFUS | 16980 | 38646491227 | DLIN | 1 | 8 | 1256 | 157 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | bad lead on trans...changed out and repaired ok jruffi1 | -90.1123 | 30.012 | 70124 | A | Council District A | Joseph Giarrusso
1291290967 | Yes | ORLEANS | FAIR | 2018-06-07 17:02 | 2018-06-07 17:02 | 2018-06-07 17:57 | 614 | ENOI | TFUS | 56134 | 40238476154 | DLIN | 1 | 9 | 495 | 55 | ANIMAL | ASQL | Animal - Squirrel | N | placed animal guards on transformer. per 310 treed3 | -90.0626 | 29.9702 | 70116 | C | Council District C | Kristin Palmer
1293570870 | Yes | ALGIERS | HEAT | 2018-07-16 15:11 | 2018-07-16 16:17 | 2018-07-16 18:02 | W0722 | ENOI | TFUS | 1136 | 4182146253 | DLIN | 81 | 9 | 1530 | 170 | LIGHTNING | LGHT | Lightning | N | Changed **RCLR 1136 162 to TFUS 1136 4** --- lightening hitting feeder/ knock several transformers out nwashi1 | -90.013 | 29.9323 | 70114 | C | Council District C | Kristin Palmer
1292268889 | Yes | ALGIERS | HEAT | 2018-06-23 23:34 | 2018-06-24 02:10 | 2018-06-24 03:34 | W1726 | ENOI | TFUS | 1052374 | 4235646160 | DLIN | 81 | 9 | 2160 | 240 | EQUIPMENT | EARR | Equipment - Arrestor | N | back n now bad arrestor brizzut | -89.9962 | 29.9294 | 70131 | C | Council District C | Joseph Giarrusso
1291465863 | Yes | EAST ORLEANS | THDR | 2018-06-10 14:47 | 2018-06-10 16:50 | 2018-06-10 18:20 | 622 | ENOI | TFUS | 77994 | 40870478454 | DLIN | 6 | 9 | 1917 | 213 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to replace transformer and repair secondary arm | -90.0426 | 29.9762 | 70117 | D | Council District D | Cyndi Nguyen
1292442898 | Yes | ALGIERS | HEAT | 2018-06-27 14:08 | 2018-06-27 18:13 | 2018-06-27 16:00 | W0726 | ENOI | TFUS | BY88030 | 4182946487 | DLIN | 81 | 9 | 1008 | 112 | EQUIPMENT | EPOL | Equipment - Pole | N |  | -90.0127 | 29.9386 | 70131 | C | Council District C | Cyndi Nguyen
1291512883 | Yes | ORLEANS | THDR | 2018-06-11 14:45 | 2018-06-11 15:09 | 2018-06-11 17:35 | 1922 | ENOI | TFUS | 62302 | 39156465735 | DLIN | 1 | 9 | 1530 | 170 | EQUIPMENT | EPOL | Equipment - Pole | N | rotten pole , line crew to make repairs, trans 62302 is out | -90.0971 | 29.9418 | 70125 | B | Council District B | Jared Brossett
1290952404 | Yes | ORLEANS | FAIR | 2018-06-02 14:13 | 2018-06-02 14:24 | 2018-06-02 17:01 | 2016 | ENOI | TFUS | 29927 | 38588470012 | DLIN | 1 | 9 | 1512 | 168 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -90.115 | 29.9538 | 70125 | A | Council District A | Cyndi Nguyen
1293796505 | Yes | ORLEANS | FAIR | 2018-07-19 18:44 | 2018-07-19 20:07 | 2018-07-19 20:08 | 407 | ENOI | XFMR | 51092 | 38643484085 | DLIN | 1 | 9 | 756 | 84 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.1125 | 29.9924 | 70124 | A | Council District A | Kristin Palmer
1294605582 | Yes | ORLEANS | THDR | 2018-07-31 20:43 | 2018-07-31 21:08 | 2018-08-01 00:42 | 512 | ENOI | XFMR | 1468016 | 39930490110 | DLIN | 1 | 9 | 2151 | 239 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer crew to change | -90.0718 | 30.0085 | 70122 | D | Council District D | Kristin Palmer
1293578786 | Yes | ALGIERS | FAIR | 2018-07-16 16:34 | 2018-07-16 22:17 | 2018-07-17 02:26 | W1713 | ENOI | XFMR | 1256180 | 4250845819 | DLIN | 81 | 9 | 5328 | 592 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer | -89.9916 | 29.92 | 70131 | C | Council District C | Jared Brossett
1291827776 | Yes | ORLEANS | FAIR | 2018-06-16 05:47 | 2018-06-16 07:36 | 2018-06-16 08:34 | 907 | ENOI | TFUS | 66066 | 40151476175 | DLIN | 1 | 10 | 1670 | 167 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel made contact with primary and ground. refused tfus. cwill20 | -90.0652 | 29.9701 | 70116 | C | Council District C | Kristin Palmer
1293677242 | NO | ORLEANS | FAIR | 2018-07-17 16:03 | 2018-07-17 16:03 | 2018-07-17 16:03 | 1915 | ENOI | TFUS | 1319745 | 3925946516 | DLIN | 1 | 10 | 0 | 0 | LIGHTNING | LGHT | Lightning | N | refused | -90.0939 | 29.9402 | 70115 | B | Council District B | Cyndi Nguyen
1291603935 | Yes | ALGIERS | THDR | 2018-06-12 17:17 | 2018-06-12 17:27 | 2018-06-12 19:39 | W1713 | ENOI | TFUS | 1288944 | 4266645880 | DLIN | 81 | 10 | 1420 | 142 | LIGHTNING | LGHT | Lightning | N | Changed **TFUS 1288944 17 to TFUS 1288944 3** --- fuse switch and arrestor blown up/ lightening/replaced w cust bk in nwashi1 | -89.9865 | 29.9216 | 70131 | C | Council District C | Joseph Giarrusso
1292181112 | Yes | EAST ORLEANS | FAIR | 2018-06-22 13:53 | 2018-06-22 13:58 | 2018-06-22 14:08 | 2216 | ENOI | LFUS | 25735-F | 4282650283 | DLIN | 6 | 10 | 150 | 15 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption | -97.0758 | 27.9066 | 70127 | E | Council District E | Joseph Giarrusso
1293756041 | Yes | EAST ORLEANS | THDR | 2018-07-18 18:45 | 2018-07-18 18:45 | 2018-07-18 20:11 | 1009 | ENOI | TFUS | 1181490 | 41668496078 | DLIN | 6 | 10 | 860 | 86 | EQUIPMENT | EARM | Equipment - Crossarm | N | bad secondary arms | -90.0166 | 30.0245 | 70126 | D | Council District D | Joseph Giarrusso
1292419377 | Yes | EAST ORLEANS | FAIR | 2018-06-26 18:06 | 2018-06-26 18:06 | 2018-06-26 22:16 | 622 | ENOI | TFUS | 528654 | 40737477609 | DLIN | 6 | 10 | 2500 | 250 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lat 21153 a phase weather cschexn | -90.0467 | 29.974 | 70117 | D | Council District D | Jared Brossett
1292277877 | Yes | ALGIERS | FAIR | 2018-06-24 06:00 | 2018-06-24 06:38 | 2018-06-24 06:52 | W1714 | ENOI | LFUS | 34348 | 4220945368 | DLIN | 81 | 10 | 520 | 52 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew changed out bad 100 by padmount | -90.0012 | 29.9077 | 70131 | C | Council District C | Jared Brossett
1292185392 | Yes | ORLEANS | FAIR | 2018-06-22 14:57 | 2018-06-22 15:02 | 2018-06-22 18:00 | 403 | ENOI | TFUS | 1527752 | 38973491142 | DLIN | 1 | 10 | 1830 | 183 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer | -90.102 | 30.0118 | 70124 | A | Council District A | Jared Brossett
1291391569 | Yes | EAST ORLEANS | FAIR | 2018-06-09 08:17 | 2018-06-09 11:07 | 2018-06-09 11:49 | 613 | ENOI | TFUS | 73743 | 40410479676 | DLIN | 6 | 10 | 2120 | 212 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer called crew to replace 50kva 14400 cschexn | -90.057 | 29.9797 | 70117 | D | Council District D | Jared Brossett
1292268878 | Yes | ALGIERS | FAIR | 2018-06-23 23:28 | 2018-06-24 05:27 | 2018-06-24 06:53 | W1714 | ENOI | TFUS | BY175952 | 4223245359 | DLIN | 81 | 10 | 4450 | 445 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew changed out bad 100 by padmount | -90.0004 | 29.9075 | 70131 | C | Council District C | Cyndi Nguyen
1293733664 | Yes | ALGIERS | FAIR | 2018-07-18 15:15 | 2018-07-18 19:22 | 2018-07-18 19:23 | W1715 | ENOI | TFUS | BY181687 | 4290845891 | DLIN | 81 | 10 | 2480 | 248 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Secondary/Service Conductor, open wire in backyard | -89.9788 | 29.9219 | 70131 | C | Council District C | Joseph Giarrusso
1291172674 | Yes | EAST ORLEANS | RAIN | 2018-06-05 13:54 | 2018-06-05 13:58 | 2018-06-05 14:59 | 622 | ENOI | TFUS | 78570 | 40968473936 | DLIN | 6 | 11 | 715 | 65 | LIGHTNING | LGHT | Lightning | N | Check Secondary and Transformer. Refused and its holding. Customer in lights mjack11 | -90.0397 | 29.9638 | 70117 | C | Council District C | Jared Brossett
1291453319 | Yes | ALGIERS | FAIR | 2018-06-10 12:32 | 2018-06-10 12:32 | 2018-06-10 14:32 | W1713 | ENOI | TFUS | 1335175 | 4251946018 | DLIN | 81 | 11 | 1320 | 120 | LIGHTNING | LGHT | Lightning | N | refused ok zwashin | -89.9911 | 29.9255 | 70131 | C | Council District C | Kristin Palmer
1291757199 | Yes | ORLEANS | THDR | 2018-06-14 12:43 | 2018-06-14 12:49 | 2018-06-14 13:36 | 615 | ENOI | LFUS | 1164730 | 39890477923 | DLIN | 1 | 11 | 572 | 52 | VEGETATION | VOHL | Overhanging Limb | N | Changed **TFUS 1164730 11 to LFUS 1164730 11** --- refused lat 97780 taking out by tree limbs first span off lat switch jbologn | -90.0734 | 29.9751 | 70119 | D | Council District D | Cyndi Nguyen
1293222390 | Yes | EAST ORLEANS | FAIR | 2018-07-09 18:23 | 2018-07-09 18:27 | 2018-07-09 20:02 | 2212 | ENOI | TFUS | 1061596 | 41919500805 | DLIN | 6 | 11 | 1089 | 99 | VEGETATION | VOHL | Overhanging Limb | N | tree got into top of trans cut switch took out c phase lattral customers back on cbowden | -90.0087 | 30.0374 | 70126 | E | Council District E | Jay Banks
1291478487 | Yes | ORLEANS | FAIR | 2018-06-10 17:54 | 2018-06-10 18:13 | 2018-06-10 18:06 | 2014 | ENOI | TFUS | 527810 | 38169466189 | DLIN | 1 | 11 | 132 | 12 | EQUIPMENT | EARM | Equipment - Crossarm | N | broken crossarm behind lateral switch | -90.1282 | 29.9434 | 70118 | A | Council District A | Joseph Giarrusso
1293336210 | Yes | ORLEANS | FAIR | 2018-07-11 19:53 | 2018-07-11 19:53 | 2018-07-11 20:39 | 614 | ENOI | TFUS | 75004 | 40272479311 | DLIN | 1 | 11 | 506 | 46 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.0613 | 29.9788 | 70119 | D | Council District D | Jay Banks
1292662506 | Yes | EAST ORLEANS | HEAT | 2018-07-01 12:00 | 2018-07-01 12:00 | 2018-07-01 12:45 | 626 | ENOI | TFUS | 1561832 | 40889484090 | DLIN | 6 | 11 | 495 | 45 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refuse cphase on latural tduncan | -90.0417 | 29.9918 | 70126 | D | Council District D | Cyndi Nguyen
1292381690 | Yes | ORLEANS | HEAT | 2018-06-25 18:30 | 2018-06-25 20:49 | 2018-06-25 22:00 | 615 | ENOI | TFUS | 58899 | 39849478003 | DLIN | 1 | 11 | 2310 | 210 | EQUIPMENT | ETRD | Equipment - Transformer | N | transformer failed, crew to replace | -90.0747 | 29.9753 | 70119 | D | Council District D | Jay Banks
1293073471 | Yes | ORLEANS | FAIR | 2018-07-07 08:27 | 2018-07-07 10:35 | 2018-07-07 13:01 | 503 | ENOI | XFMR | 27682 | 40062494539 | DLIN | 1 | 11 | 3014 | 274 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace transformer | -90.0674 | 30.0207 | 70122 | D | Council District D | Cyndi Nguyen
1291462687 | Yes | EAST ORLEANS | THDR | 2018-06-10 13:56 | 2018-06-10 17:58 | 2018-06-10 19:34 | 611 | ENOI | TFUS | 21177 | 4091548020 | DLIN | 6 | 11 | 3718 | 338 | EQUIPMENT | ETRD | Equipment - Transformer | N | Changed **LFUS 21177 29 to TFUS 21177 29** --- bad 50kva 14400 120-240 cschexn | -90.0411 | 29.9811 | 70117 | D | Council District D | Joseph Giarrusso
1294253813 | Yes | ORLEANS | FAIR | 2018-07-24 12:43 | 2018-07-24 13:06 | 2018-07-24 13:10 | 627 | ENOI | TFUS | 60882 | 40091480502 | DLIN | 1 | 12 | 312 | 26 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | refused transformer taken out by pigeon installed animal guard jtatma1 | -90.0671 | 29.9822 | 70119 | D | Council District D | Cyndi Nguyen
1294354943 | Yes | ORLEANS | HEAT | 2018-07-27 08:38 | 2018-07-27 08:38 | 2018-07-27 09:40 | 2014 | ENOI | TFUS | 33399 | 38072468577 | DLIN | 1 | 12 | 744 | 62 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel took out fuse refused ok jruffi1 | -90.1313 | 29.9499 | 70118 | A | Council District A | Cyndi Nguyen
1292176390 | Yes | ORLEANS | FAIR | 2018-06-22 11:48 | 2018-06-22 13:12 | 2018-06-22 13:40 | 2027 | ENOI | TFUS | 64980 | 38685470208 | DLIN | 1 | 12 | 1344 | 112 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok installed animal guard advised jbologn | -90.1118 | 29.9543 | 70125 | B | Council District B | Cyndi Nguyen
1292797151 | Yes | ORLEANS | FAIR | 2018-07-03 09:20 | 2018-07-03 12:58 | 2018-07-03 13:00 | 1917 | ENOI | LFUS | 21078 | 3855245919 | DLIN | 1 | 12 | 2640 | 220 | ANIMAL | ASQL | Animal - Squirrel | N | Animal - Squirrel | -90.1163 | 29.924 | 70115 | A | Council District A | Cyndi Nguyen
1292644988 | Yes | ORLEANS | RAIN | 2018-07-01 00:48 | 2018-07-01 01:11 | 2018-07-01 01:57 | 911 | ENOI | TFUS | 67611 | 3936647457 | DLIN | 1 | 12 | 828 | 69 | LIGHTNING | LGHT | Lightning | N | refused ok rdeano | -90.0903 | 29.966 | 70119 | B | Council District B | Jared Brossett
1293255040 | Yes | ORLEANS | FAIR | 2018-07-10 12:32 | 2018-07-10 12:52 | 2018-07-10 12:53 | 1705 | ENOI | LFUS | 27868 | 3966847557 | DLIN | 1 | 12 | 252 | 21 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | limb on xarm at n dorgenois and st peter removed refused ok jbologn | -90.0806 | 29.9686 | 70119 | D | Council District D | Cyndi Nguyen
1290943032 | Yes | EAST ORLEANS | FAIR | 2018-06-02 06:44 | 2018-06-02 06:51 | 2018-06-02 07:27 | 611 | ENOI | LFUS | 21115 | 4100248045 | DLIN | 6 | 12 | 516 | 43 | EQUIPMENT | EARR | Equipment - Arrestor | N | found bad arrestor tracking over at dead end pole. clear arrestor and refused lateral atampl1 | -90.0383 | 29.9817 | 70117 | D | Council District D | Jay Banks
1291529858 | Yes | ORLEANS | THDR | 2018-06-11 17:23 | 2018-06-11 21:04 | 2018-06-11 21:06 | 1513 | ENOI | TFUS | 60296 | 39395475907 | DLIN | 1 | 12 | 2676 | 223 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.0893 | 29.9697 | 70119 | B | Council District B | Jared Brossett
1292160142 | Yes | ORLEANS | FAIR | 2018-06-22 08:31 | 2018-06-22 09:19 | 2018-06-22 09:07 | 2027 | ENOI | TFUS | 64980 | 38685470208 | DLIN | 1 | 12 | 432 | 36 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | BT-FUSE BARREL OPEN jmondy | -90.1118 | 29.9543 | 70125 | B | Council District B | Jared Brossett
1292165700 | Yes | ORLEANS | FAIR | 2018-06-22 09:56 | 2018-06-22 10:07 | 2018-06-22 11:11 | 2027 | ENOI | TFUS | 64980 | 38685470208 | DLIN | 1 | 12 | 900 | 75 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | BT- FUSE BARREL OPEN jmondy | -90.1118 | 29.9543 | 70125 | B | Council District B | Jared Brossett
1293466823 | Yes | ALGIERS | HEAT | 2018-07-14 09:21 | 2018-07-14 09:32 | 2018-07-14 11:09 | W0112 | ENOI | TFUS | 10041 | 4072546568 | DLIN | 81 | 12 | 1284 | 107 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **LFUS 10041 66 to TFUS 10041 10** --- refused ok zwashin | -90.0475 | 29.9412 | 70114 | C | Council District C | Jared Brossett
1291410829 | Yes | EAST ORLEANS | FAIR | 2018-06-09 15:02 | 2018-06-09 16:05 | 2018-06-09 17:14 | 613 | ENOI | LFUS | 27988 | 4040448308 | DLIN | 6 | 12 | 1572 | 131 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lateral take out by weather cschexn | -90.0572 | 29.9891 | 70122 | D | Council District D | Jared Brossett
1291466839 | Yes | EAST ORLEANS | THDR | 2018-06-10 15:06 | 2018-06-10 17:59 | 2018-06-10 18:12 | 2346 | ENOI | LFUS | 27874 | 4169347325 | DLIN | 6 | 12 | 2232 | 186 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lat line weather cschexn | -90.0167 | 29.9616 | 70117 | E | Council District E | Jared Brossett
1294362804 | Yes | EAST ORLEANS | FAIR | 2018-07-27 12:39 | 2018-07-27 12:39 | 2018-07-27 14:30 | 611 | ENOI | TFUS | 66559 | 41056475302 | DLIN | 6 | 12 | 1332 | 111 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | crew to work on switch | -90.0368 | 29.9676 | 70117 | D | Council District D | Joseph Giarrusso
1292069841 | Yes | ORLEANS | FAIR | 2018-06-20 08:11 | 2018-06-20 11:52 | 2018-06-20 12:36 | 407 | ENOI | TFUS | 1053509 | 38647487258 | DLIN | 1 | 12 | 3180 | 265 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | fuse cwas out refuse ok | -90.1124 | 30.0011 | 70124 | A | Council District A | Jared Brossett
1291040734 | Yes | EAST ORLEANS | FAIR | 2018-06-03 17:46 | 2018-06-03 18:21 | 2018-06-03 18:22 | 1610 | ENOI | OPEN | 4219649694 | 4219649694 | DLIN | 6 | 12 | 432 | 36 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  |  |  | 70126 | E | Council District E | Jay Banks
1294423339 | Yes | ORLEANS | THDR | 2018-07-28 20:29 | 2018-07-28 21:33 | 2018-07-29 00:25 | 406 | ENOI | TFUS | 659399 | 38880493081 | DLIN | 1 | 12 | 2832 | 236 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | wire down is alley, crew enroute to pick up. | -90.1048 | 30.0171 | 70124 | A | Council District A | Jared Brossett
1292056700 | Yes | ORLEANS | FAIR | 2018-06-20 06:25 | 2018-06-20 06:25 | 2018-06-20 07:46 | 627 | ENOI | TFUS | 55625 | 40172478114 | DLIN | 1 | 13 | 1040 | 80 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok installed animal guard jbologn | -90.0645 | 29.9756 | 70116 | D | Council District D | Joseph Giarrusso
1292056705 | Yes | ORLEANS | FAIR | 2018-06-20 06:26 | 2018-06-20 08:08 | 2018-06-20 09:12 | 1917 | ENOI | TFUS | 77670 | 38562459623 | DLIN | 1 | 13 | 2158 | 166 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok already had animal guard advised jbologn | -90.116 | 29.9252 | 70115 | A | Council District A | Cyndi Nguyen
1293673500 | Yes | ALGIERS | THDR | 2018-07-17 15:13 | 2018-07-17 18:18 | 2018-07-17 18:24 | W1713 | ENOI | TFUS | 478861 | 4264845848 | DLIN | 81 | 13 | 2483 | 191 | LIGHTNING | LGHT | Lightning | N | back on weather brizzut | -89.9871 | 29.9208 | 70131 | C | Council District C | Jared Brossett
1293725391 | Yes | ALGIERS | RAIN | 2018-07-18 12:09 | 2018-07-18 12:25 | 2018-07-18 13:10 | W1713 | ENOI | TFUS | 478861 | 4264845848 | DLIN | 81 | 13 | 793 | 61 | VEGETATION | VOHL | Overhanging Limb | N | removed over hanging limb at 6300 dover pl zwashin | -89.9871 | 29.9208 | 70131 | C | Council District C | Jared Brossett
1292396054 | Yes | EAST ORLEANS | HEAT | 2018-06-26 07:59 | 2018-06-26 08:30 | 2018-06-26 09:50 | 2212 | ENOI | TFUS | 37191 | 4216250235 | DLIN | 6 | 13 | 1443 | 111 | VEGETATION | VINE | Vine Growing into Line | N | Changed **LFUS 37191 13 to TFUS 37191 13** --- vines on transformer/cleared dfahr | -90.0008 | 30.0415 | 70126 | E | Council District E | Cyndi Nguyen
1294430715 | Yes | ALGIERS | RAIN | 2018-07-28 22:42 | 2018-07-29 00:21 | 2018-07-29 00:46 | W1713 | ENOI | TFUS | 478861 | 4264845848 | DLIN | 81 | 13 | 1612 | 124 | VEGETATION | VINE | Vine Growing into Line | N | Changed **TFUS 478861 24 to TFUS 478861 4** --- vines taking out transformer/ follow up needed asap nwashi1 | -89.9871 | 29.9208 | 70131 | C | Council District C | Jared Brossett
1294522000 | Yes | ALGIERS | FAIR | 2018-07-30 11:47 | 2018-07-30 11:48 | 2018-07-30 13:37 | W1713 | ENOI | TFUS | 478861 | 4264845848 | DLIN | 81 | 13 | 1430 | 110 | EQUIPMENT | EARR | Equipment - Arrestor | N | cut off arrestor on transformer zwashin | -89.9871 | 29.9208 | 70131 | C | Council District C | Jared Brossett
1292025576 | Yes | ORLEANS | FAIR | 2018-06-19 14:26 | 2018-06-19 14:26 | 2018-06-19 15:57 | 1705 | ENOI | TFUS | 634303 | 39772479289 | DLIN | 1 | 13 | 1183 | 91 | EQUIPMENT | EARM | Equipment - Crossarm | N | changed out crossarm . which caused transformer to go out of lights everyone back in. shudso3 | -90.0773 | 29.9789 | 70119 | D | Council District D | Jay Banks
1291769301 | Yes | ORLEANS | THDR | 2018-06-14 15:28 | 2018-06-14 16:22 | 2018-06-14 18:21 | 1711 | ENOI | TFUS | 56841 | 39533479932 | DLIN | 1 | 13 | 2249 | 173 | EQUIPMENT | EARM | Equipment - Crossarm | N | CREW TO REPLACE BOX CONSTRUCTION SECONDARY CROSSARMS | -90.0848 | 29.9807 | 70119 | A | Council District A | Jared Brossett
1293579899 | Yes | ALGIERS | FAIR | 2018-07-16 16:46 | 2018-07-16 16:46 | 2018-07-16 17:01 | W1713 | ENOI | TFUS | 478861 | 4264845848 | DLIN | 81 | 13 | 195 | 15 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused transformer | -89.9871 | 29.9208 | 70131 | C | Council District C | Joseph Giarrusso
1292418692 | Yes | EAST ORLEANS | FAIR | 2018-06-26 17:44 | 2018-06-26 21:08 | 2018-06-26 22:12 | 623 | ENOI | TFUS | 1527004 | 40449477224 | DLIN | 6 | 13 | 3484 | 268 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refuse lat line 21153weather customers back on cschexn | -90.0559 | 29.973 | 70117 | C | Council District C | Jay Banks
1294411911 | Yes | EAST ORLEANS | THDR | 2018-07-28 17:37 | 2018-07-28 17:40 | 2018-07-28 22:31 | 2223 | ENOI | LFUS | 25974 | 4342551022 | DLIN | 6 | 13 | 3822 | 294 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | switched underground out from T.P. 25974 to V-21, closed N/O in V-24, power has been restored. | -89.9607 | 30.0628 | 70128 | E | Council District E | Jay Banks
1291560402 | Yes | ORLEANS | FAIR | 2018-06-12 07:04 | 2018-06-12 07:12 | 2018-06-12 09:25 | 2026 | ENOI | TFUS | 68067 | 38766478609 | DLIN | 1 | 13 | 1833 | 141 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -90.1089 | 29.9773 | 70119 | A | Council District A | Joseph Giarrusso
1291435084 | Yes | ORLEANS | FAIR | 2018-06-09 20:39 | 2018-06-09 20:39 | 2018-06-09 23:02 | 2016 | ENOI | TFUS | 66849 | 38460468106 | DLIN | 1 | 13 | 1859 | 143 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew changed out tyransf here | -90.1191 | 29.9486 | 70118 | A | Council District A | Joseph Giarrusso
1291744708 | Yes | EAST ORLEANS | FAIR | 2018-06-14 07:40 | 2018-06-14 07:44 | 2018-06-14 08:30 | 2212 | ENOI | TFUS | 80293 | 42020500872 | DLIN | 6 | 13 | 650 | 50 | OTHER | UNKN | Inspected Unknown | N |  | -90.0054 | 30.0376 | 70126 | E | Council District E | Joseph Giarrusso
1292057105 | Yes | ORLEANS | FAIR | 2018-06-20 06:58 | 2018-06-20 07:11 | 2018-06-20 08:26 | 2137 | ENOI | LFUS | 729711 | 39856465870 | DLIN | 1 | 14 | 1232 | 88 | HUMAN FACTORS | HNWK | Human Error - Non-Entergy Workers (Describe in Remarks) | N | Changed **TFUS 729711 14 to LFUS 729711 14** --- contactor diging up street bumbed pole and blew lat at clio and carondelet switches not in system no damage jbologn | -90.0751 | 29.9419 | 70130 | B | Council District B | Jared Brossett
1292300740 | Yes | ORLEANS | FAIR | 2018-06-24 16:54 | 2018-06-24 16:56 | 2018-06-24 18:41 | 1913 | ENOI | TFUS | 500414 | 38346457304 | DLIN | 1 | 14 | 1498 | 107 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | City tree fell on 412 and 414 State St. service line. Made customer contact and advised to contact the city to cut the tree. DOC has also made an attempt at contacting the city to remove the tree. Transformer refused | -90.1229 | 29.9189 | 70118 | A | Council District A | Jay Banks
1291721350 | Yes | EAST ORLEANS | FAIR | 2018-06-13 19:43 | 2018-06-13 19:43 | 2018-06-13 21:02 | 2212 | ENOI | TFUS | 58820 | 42273502630 | DLIN | 6 | 14 | 1092 | 78 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | took out transfomer and pick up a span of 1/0 Aluminum made repairs customer back in lights made customer contact cbower1 | -89.9974 | 30.0424 | 70127 | E | Council District E | Jay Banks
1291844349 | Yes | ORLEANS | HEAT | 2018-06-16 19:59 | 2018-06-16 20:05 | 2018-06-16 21:44 | 1923 | ENOI | TFUS | 69846 | 39360458744 | DLIN | 1 | 14 | 1470 | 105 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused ok. no signs of a fault dsmit36 | -90.0908 | 29.9225 | 70115 | B | Council District B | Joseph Giarrusso
1294364479 | Yes | ALGIERS | HEAT | 2018-07-27 13:46 | 2018-07-27 14:31 | 2018-07-27 14:56 | W1714 | ENOI | LFUS | 5607 | 4250745653 | DLIN | 81 | 14 | 980 | 70 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | changed switch zwashin | -89.9916 | 29.9154 | 70131 | C | Council District C | Jared Brossett
1292593222 | Yes | EAST ORLEANS | FAIR | 2018-06-29 19:13 | 2018-06-29 20:38 | 2018-06-29 20:26 | 1610 | ENOI | LFUS | 27522 | 4223449606 | DLIN | 6 | 14 | 1022 | 73 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -97.0758 | 27.9066 | 70126 | E | Council District E | Kristin Palmer
1294233993 | Yes | ALGIERS | HEAT | 2018-07-23 22:30 | 2018-07-24 01:19 | 2018-07-24 01:28 | W1714 | ENOI | LFUS | 5607 | 4250745653 | DLIN | 81 | 14 | 2492 | 178 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | broken riser repaired on fuse switch 5607. re energized ok mtaruc | -89.9916 | 29.9154 | 70131 | C | Council District C | Jay Banks
1292598007 | Yes | EAST ORLEANS | FAIR | 2018-06-29 19:06 | 2018-06-29 20:30 | 2018-06-29 23:39 | 1610 | ENOI | ELBO | 42256496972 | 42256496972 | DLIN | 6 | 14 | 3822 | 273 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -97.0758 | 27.9066 | 70126 | E | Council District E | Cyndi Nguyen
1294366273 | Yes | ALGIERS | FAIR | 2018-07-27 14:51 | 2018-07-27 15:57 | 2018-07-27 16:30 | W1715 | ENOI | LFUS | 35050 | 4374345108 | DLIN | 81 | 14 | 1386 | 99 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -89.9528 | 29.9001 | 70037 | C | Council District C | Jay Banks
1292715367 | Yes | EAST ORLEANS | FAIR | 2018-07-02 14:39 | 2018-07-02 15:06 | 2018-07-02 16:50 | 505 | ENOI | TFUS | 1413738 | 40660496102 | DLIN | 6 | 14 | 1834 | 131 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad trans | -90.0486 | 30.0248 | 70122 | D | Council District D | Jay Banks
1294447981 | Yes | EAST ORLEANS | THDR | 2018-07-29 03:09 | 2018-07-29 05:40 | 2018-07-29 08:20 | 617 | ENOI | TFUS | 29354 | 40829489579 | DLIN | 6 | 14 | 4354 | 311 | EQUIPMENT | ETRD | Equipment - Transformer | N | Bad 100-- crew to change out | -90.0433 | 30.0069 | 70126 | D | Council District D | Jay Banks
1291411529 | Yes | ORLEANS | FAIR | 2018-06-09 15:21 | 2018-06-09 15:21 | 2018-06-09 16:40 | 1921 | ENOI | TFUS | 77802 | 38823458690 | DLIN | 1 | 15 | 1185 | 79 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | Changed **TFUS 77802 * 15 to TFUS 77802 * 1** --- taken out by non reportable bird jdomang | -90.1079 | 29.9225 | 70115 | B | Council District B | Jay Banks
1292642985 | Yes | ALGIERS | THDR | 2018-06-30 23:42 | 2018-07-01 03:59 | 2018-07-01 04:16 | W1714 | ENOI | TFUS | 1205799 | 4278345633 | DLIN | 81 | 15 | 4110 | 274 | LIGHTNING | LGHT | Lightning | N | back n brizzut | -89.9829 | 29.9148 | 70131 | C | Council District C | Cyndi Nguyen
1292181203 | Yes | EAST ORLEANS | FAIR | 2018-06-22 13:53 | 2018-06-22 14:04 | 2018-06-22 14:06 | 2216 | ENOI | LFUS | 27127 | UNK | DLIN | 6 | 16 | 208 | 13 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption | -97.0758 | 27.9066 | 70127 | E | Council District E | Cyndi Nguyen
1294491090 | Yes | ORLEANS | FAIR | 2018-07-29 19:29 | 2018-07-29 19:45 | 2018-07-29 20:18 | 907 | ENOI | TFUS | 76137 | 40058476163 | DLIN | 1 | 16 | 784 | 49 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole and blew transformer fuse one span down pole and transfemer good gkathma - 8/1/2018 Added to Minimal claims List. Will forward to D.Gault | -90.0682 | 29.9702 | 70116 | D | Council District D | Cyndi Nguyen
1292470193 | Yes | ALGIERS | HEAT | 2018-06-28 08:05 | 2018-06-28 09:25 | 2018-06-28 10:10 | W1725 | ENOI | TFUS | BY58138 | 4103346722 | DLIN | 81 | 16 | 2000 | 125 | OTHER | EMER | Emergency Switching | N | replace transformer | -90.0378 | 29.9453 | 70114 | C | Council District C | Cyndi Nguyen
1291788207 | Yes | ALGIERS | FAIR | 2018-06-15 06:28 | 2018-06-15 06:46 | 2018-06-15 07:29 | W1726 | ENOI | TFUS | BY95866 | 4211146087 | DLIN | 81 | 17 | 1037 | 61 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok cmulhea | -90.004 | 29.9276 | 70131 | C | Council District C | Cyndi Nguyen
1291582740 | Yes | ALGIERS | THDR | 2018-06-12 14:43 | 2018-06-12 15:30 | 2018-06-12 16:40 | W1713 | ENOI | LFUS | 5695 | 4261445883 | DLIN | 81 | 17 | 1989 | 117 | LIGHTNING | LGHT | Lightning | N | Changed **LFUS 5695 30 to LFUS 5695 4** --- weather/bk in/refused ok nwashi1 | -89.9882 | 29.9217 | 70131 | C | Council District C | Cyndi Nguyen
1292545332 | Yes | ORLEANS | FAIR | 2018-06-29 07:04 | 2018-06-29 07:05 | 2018-06-29 07:48 | 614 | ENOI | TFUS | 30456 | 40333473620 | DLIN | 1 | 17 | 731 | 43 | VEGETATION | VOHL | Overhanging Limb | N | refused ok cleared tree limb advised jbologn | -90.0596 | 29.9632 | 70116 | C | Council District C | Jared Brossett
1293570800 | Yes | ALGIERS | FAIR | 2018-07-16 15:05 | 2018-07-16 15:10 | 2018-07-16 16:00 | W1713 | ENOI | LFUS | 5694 | 4261345850 | DLIN | 81 | 17 | 935 | 55 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused ok | -89.9883 | 29.9208 | 70131 | C | Council District C | Kristin Palmer
1292032997 | Yes | ORLEANS | FAIR | 2018-06-19 15:53 | 2018-06-19 16:17 | 2018-06-19 18:45 | 2132 | ENOI | TFUS | 63058 | 39246461133 | DLIN | 1 | 17 | 2924 | 172 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | BT- TRANSFORMER NEED TO BE REFUSE jmondy, wilson rack ffailed causing secondary to get togwether............PC | -90.0944 | 29.9291 | 70115 | B | Council District B | Cyndi Nguyen
1290955784 | Yes | EAST ORLEANS | FAIR | 2018-06-02 15:33 | 2018-06-02 16:17 | 2018-06-02 18:15 | 2346 | ENOI | LFUS | 32640 | 4176847139 | DLIN | 6 | 17 | 2754 | 162 | EQUIPMENT | EPOL | Equipment - Pole | N | top of pole bad let shield fall on lateral | -90.0144 | 29.9565 | 70117 | E | Council District E | Jay Banks
1292598019 | Yes | EAST ORLEANS | FAIR | 2018-06-29 19:06 | 2018-06-29 20:30 | 2018-06-29 22:35 | 1610 | ENOI | ELBO | 42258496735 | 42258496735 | DLIN | 6 | 17 | 3553 | 209 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -97.0758 | 27.9066 | 70126 | E | Council District E | Cyndi Nguyen
1293770153 | Yes | ORLEANS | THDR | 2018-07-19 00:55 | 2018-07-19 01:14 | 2018-07-19 04:55 | 2013 | ENOI | OPEN | 3817046229 | 3817046229 | DLIN | 1 | 17 | 4080 | 240 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -90.1284 | 29.9326 | 70118 | A | Council District A | Cyndi Nguyen
1294064184 | Yes | ORLEANS | HEAT | 2018-07-21 16:34 | 2018-07-21 17:05 | 2018-07-21 20:03 | 1916 | ENOI | XFMR | 1355811 | 38980460508 | DLIN | 1 | 17 | 3553 | 209 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace transformer...complete | -90.1028 | 29.9274 | 70115 | B | Council District B | Jared Brossett
1291408473 | Yes | EAST ORLEANS | FAIR | 2018-06-09 13:14 | 2018-06-09 13:14 | 2018-06-09 16:59 | 1205 | ENOI | TFUS | 80287 | 44527502726 | DLIN | 6 | 17 | 3808 | 224 | EQUIPMENT | ETRD | Equipment - Transformer | N | cerw to replace transformer | -89.9261 | 30.0418 | 70129 | E | Council District E | Kristin Palmer
1294311275 | Yes | ALGIERS | HEAT | 2018-07-26 10:15 | 2018-07-26 10:29 | 2018-07-26 11:53 | W0112 | ENOI | TFUS | BY178892 | 4090046820 | DLIN | 81 | 18 | 1746 | 97 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | bird took out transformer ok sphill1 | -90.0419 | 29.9481 | 70114 | C | Council District C | Kristin Palmer
1293488444 | Yes | ORLEANS | FAIR | 2018-07-14 22:20 | 2018-07-14 23:06 | 2018-07-14 23:31 | 1917 | ENOI | LFUS | 21083 | 3852946097 | DLIN | 1 | 18 | 1278 | 71 | OTHER | FOBJ | Foreign Objects - Other | N | refused b phase cause unknown jtatma1 | -90.117 | 29.9288 | 70115 | A | Council District A | Joseph Giarrusso
1291591271 | Yes | ALGIERS | THDR | 2018-06-12 15:58 | 2018-06-12 23:41 | 2018-06-13 00:16 | W0726 | ENOI | TFUS | BY9-477 | 4185746472 | DLIN | 81 | 18 | 8964 | 498 | LIGHTNING | LGHT | Lightning | N | back n weather brizzut | -90.0118 | 29.9382 | 70131 | C | Council District C | Cyndi Nguyen
1293469611 | Yes | ORLEANS | FAIR | 2018-07-14 10:29 | 2018-07-14 11:14 | 2018-07-14 12:40 | 2013 | ENOI | TFUS | 31261 | 38380466917 | DLIN | 1 | 18 | 2358 | 131 | VEGETATION | VOHL | Overhanging Limb | N | Secondary/Service Conductor | -90.1217 | 29.9453 | 70118 | A | Council District A | Kristin Palmer
1291014510 | Yes | EAST ORLEANS | FAIR | 2018-06-03 08:37 | 2018-06-03 13:34 | 2018-06-03 14:03 | 1610 | ENOI | DIS | 24720 | 4282549624 | DLIN | 6 | 18 | 5868 | 326 | HUMAN FACTORS | VHCL | Vehicle | N | crew | -89.9801 | 30.0245 | 70127 | E | Council District E | Jay Banks
1293652194 | Yes | EAST ORLEANS | FAIR | 2018-07-17 10:33 | 2018-07-17 10:34 | 2018-07-17 11:28 | 611 | ENOI | TFUS | 74880 | 41202475172 | DLIN | 6 | 18 | 990 | 55 | VEGETATION | VINE | Vine Growing into Line | N | vines on pole blew transformer fuse-cleared vines down to cable lines-re fused ok cust back on-turned in ticket for vegetation swalsh1 7-17-18 swalsh1 | -90.0321 | 29.9672 | 70117 | D | Council District D | Jared Brossett
1294286677 | Yes | EAST ORLEANS | FAIR | 2018-07-25 13:50 | 2018-07-25 14:12 | 2018-07-25 14:45 | 1605 | ENOI | LFUS | 25656 | 4321250236 | DLIN | 6 | 18 | 990 | 55 | EQUIPMENT | ETRD | Equipment - Transformer | N | crw to replace transformer | -97.0758 | 27.9066 | 70128 | E | Council District E | Jared Brossett
1291327644 | Yes | EAST ORLEANS | FAIR | 2018-06-08 06:26 | 2018-06-08 08:53 | 2018-06-08 09:08 | 1710 | ENOI | TFUS | 1067074 | 40387486845 | DLIN | 6 | 18 | 2916 | 162 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change transformer | -90.0575 | 29.9994 | 70122 | D | Council District D | Jay Banks
1294100719 | Yes | EAST ORLEANS | HEAT | 2018-07-22 07:33 | 2018-07-22 10:22 | 2018-07-22 11:53 | 1609 | ENOI | XFMR | 1105811 | 43756499043 | DLIN | 6 | 18 | 4680 | 260 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace bad transformer | -89.9506 | 30.032 | 70128 | E | Council District E | Jay Banks
1294345359 | NO | ALGIERS | HEAT | 2018-07-26 21:39 | 2018-07-26 21:40 | 2018-07-26 21:42 | W1725 | ENOI | TFUS | BY95549 | 4112546569 | DLIN | 81 | 18 | 54 | 3 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | hot leg at transformer sparking...dropped out to make repairs | -90.0349 | 29.9411 | 70114 | C | Council District C | Kristin Palmer
1291504932 | Yes | EAST ORLEANS | THDR | 2018-06-11 13:15 | 2018-06-11 13:27 | 2018-06-11 14:38 | 611 | ENOI | LFUS | 28072 | 41053477349 | DLIN | 6 | 19 | 1577 | 83 | LIGHTNING | LGHT | Lightning | N | Changed **TFUS 78276 19 to LFUS 78276 19** --- found B and C phase blown at 28072 refused ok taken out by lightning dfahr | -90.0369 | 29.9732 | 70117 | D | Council District D | Jared Brossett
1291506243 | Yes | ALGIERS | THDR | 2018-06-11 13:25 | 2018-06-11 13:39 | 2018-06-11 14:50 | W1715 | ENOI | LFUS | 5531 | 4413045773 | DLIN | 81 | 19 | 1615 | 85 | LIGHTNING | LGHT | Lightning | N | lat 5531 back n staton and paterson brizzut | -89.9405 | 29.9182 | 70131 | C | Council District C | Cyndi Nguyen
1294400656 | Yes | EAST ORLEANS | FAIR | 2018-07-28 15:20 | 2018-07-28 15:54 | 2018-07-28 17:33 | 1204 | ENOI | LFUS | 35369 | 4978453740 | DLIN | 6 | 19 | 2527 | 133 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused line fuse ok unknown cause made customer contact cbower1 | -89.7586 | 30.1354 | 70129 | E | Council District E | Kristin Palmer
1292651115 | Yes | EAST ORLEANS | THDR | 2018-06-30 22:59 | 2018-07-01 02:20 | 2018-07-01 02:43 | 612 | ENOI | DIS | 23753 | 4127247791 | DLIN | 6 | 20 | 4480 | 224 | LIGHTNING | LGHT | Lightning | N |  | -90.0298 | 29.9746 | 70117 | D | Council District D | Kristin Palmer
1292090422 | Yes | ORLEANS | FAIR | 2018-06-20 19:40 | 2018-06-21 05:55 | 2018-06-21 05:50 | 510 | ENOI | LFUS | 17894 | 3983349272 | DLIN | 1 | 20 | 12200 | 610 | HUMAN FACTORS | VHCL | Vehicle | N | Truck hit 2 poles, crew enroute to replace. *Emailed PID 7/9/2018* | -90.0749 | 30.0158 | 70122 | D | Council District D | Jay Banks
1292652341 | Yes | EAST ORLEANS | FAIR | 2018-07-01 03:19 | 2018-07-01 07:37 | 2018-07-01 07:40 | 2211 | ENOI | LFUS | 27323 | 4239650063 | DLIN | 6 | 20 | 5220 | 261 | EQUIPMENT | ETRD | Equipment - Transformer | N | Changed out transformer and elbow, power is back on. | -97.0758 | 27.9066 | 70127 | E | Council District E | Kristin Palmer
1294523575 | Yes | EAST ORLEANS | THDR | 2018-07-30 12:16 | 2018-07-30 15:02 | 2018-07-30 16:01 | 2346 | ENOI | LFUS | 32796 | 4190647322 | DLIN | 6 | 21 | 4725 | 225 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to repair crossarm | -90.01 | 29.9616 | 70117 | E | Council District E | Cyndi Nguyen
1292588831 | NO | ORLEANS | THDR | 2018-06-29 17:52 | 2018-06-29 17:52 | 2018-06-29 17:52 | 1506 | ENOI | SBKR | 1506 | 3951946979 | DLIN | 1 | 21 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N |  | -90.0855 | 29.9528 | 70113 | B | Council District B | Kristin Palmer
1293572154 | Yes | ALGIERS | THDR | 2018-07-16 15:15 | 2018-07-16 16:21 | 2018-07-16 16:28 | W1713 | ENOI | LFUS | 5714 | 4261145816 | DLIN | 81 | 22 | 1606 | 73 | LIGHTNING | LGHT | Lightning | N | Changed **LFUS 5714 35 to LFUS 5714 3** --- lightening tagge feeder knockinc out laterals and transformers nwashi1 | -89.9884 | 29.9199 | 70131 | C | Council District C | Kristin Palmer
1291588360 | Yes | ALGIERS | THDR | 2018-06-12 15:26 | 2018-06-12 16:27 | 2018-06-12 16:54 | W1725 | ENOI | TFUS | BY90860 | 4112946637 | DLIN | 81 | 22 | 1936 | 88 | LIGHTNING | LGHT | Lightning | N | refused ok zwashin | -90.0348 | 29.943 | 70114 | C | Council District C | Kristin Palmer
1293641744 | Yes | EAST ORLEANS | RAIN | 2018-07-17 06:26 | 2018-07-17 08:26 | 2018-07-17 08:44 | 2346 | ENOI | LFUS | 27698 | 42121477413 | DLIN | 6 | 22 | 3014 | 137 | EQUIPMENT | EARR | Equipment - Arrestor | N | fnd b phase sw 27698 blown-rode out line and fnd line arrestor blown into clear-re fused sw 27698 ok- cust back on swalsh1 7-17-18 swalsh1 | -90.003 | 29.9729 | 70117 | E | Council District E | Cyndi Nguyen
1291760363 | Yes | ALGIERS | THDR | 2018-06-14 13:59 | 2018-06-14 14:12 | 2018-06-14 14:42 | W1725 | ENOI | TFUS | BY90860 | 4112946637 | DLIN | 81 | 22 | 946 | 43 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **TFUS BY90860 32 to TFUS BY90860 2** --- fuse link blown/refused ok nwashi1 | -90.0348 | 29.943 | 70114 | C | Council District C | Joseph Giarrusso
1291408760 | Yes | EAST ORLEANS | THDR | 2018-06-09 14:32 | 2018-06-09 15:05 | 2018-06-09 15:20 | 623 | ENOI | LFUS | 21162 | 4062847457 | DLIN | 6 | 22 | 1056 | 48 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused b phase lateral weather in area cschexn | -90.0502 | 29.9656 | 70117 | C | Council District C | Jared Brossett
1291748953 | Yes | ALGIERS | FAIR | 2018-06-14 09:37 | 2018-06-14 09:52 | 2018-06-14 10:38 | W1725 | ENOI | TFUS | BY90860 | 4112946637 | DLIN | 81 | 22 | 1342 | 61 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **TFUS BY90860 32 to TFUS BY90860 3** --- fuse link blown/ refused ok nwashi1 | -90.0348 | 29.943 | 70114 | C | Council District C | Jared Brossett
1291777421 | Yes | ALGIERS | HEAT | 2018-06-14 18:19 | 2018-06-14 21:18 | 2018-06-14 22:21 | W1725 | ENOI | TFUS | BY90860 | 4112946637 | DLIN | 81 | 22 | 5324 | 242 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew replaced bad 100BY at this location (pwd) | -90.0348 | 29.943 | 70114 | C | Council District C | Cyndi Nguyen
1294463562 | Yes | ORLEANS | FAIR | 2018-07-29 08:49 | 2018-07-29 08:49 | 2018-07-29 15:36 | 2021 | ENOI | TFUS | 68267 | 39334466254 | DLIN | 1 | 22 | 8954 | 407 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad padmount | -90.0915 | 29.9432 | 70113 | B | Council District B | Jay Banks
1292437850 | Yes | EAST ORLEANS | HEAT | 2018-06-27 10:59 | 2018-06-27 11:43 | 2018-06-27 12:00 | 1604 | ENOI | LFUS | 21418 | 4284249407 | DLIN | 6 | 23 | 1403 | 61 | ANIMAL | ASQL | Animal - Squirrel | N | found B phaae blown at 21418 cleared squirrel and refused dfahr | -89.9797 | 30.0185 | 70127 | E | Council District E | Jared Brossett
1293323511 | Yes | EAST ORLEANS | FAIR | 2018-07-11 17:41 | 2018-07-11 21:11 | 2018-07-11 20:01 | 1605 | ENOI | LFUS | 26058 | 4328650129 | DLIN | 6 | 23 | 3220 | 140 | EQUIPMENT | EELB | Equipment - Elbow | N |  | -97.0758 | 27.9066 | 70128 | E | Council District E | Jared Brossett
1293342318 | Yes | EAST ORLEANS | FAIR | 2018-07-11 17:41 | 2018-07-11 17:41 | 2018-07-11 21:15 | 1605 | ENOI | ELBO | 43176500909 | 43176500909 | DLIN | 6 | 23 | 4922 | 214 | EQUIPMENT | EELB | Equipment - Elbow | N |  | -97.0758 | 27.9066 | 70127 | E | Council District E | Joseph Giarrusso
1292247315 | Yes | ALGIERS | FAIR | 2018-06-23 11:58 | 2018-06-23 12:22 | 2018-06-23 12:48 | W1714 | ENOI | LFUS | 5607 | 4250745653 | DLIN | 81 | 23 | 1150 | 50 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Changed **LFUS 5607 37 to LFUS 5607 3** --- riser burnt on switch/ changed/ bk in nwashi1 | -89.9916 | 29.9154 | 70131 | C | Council District C | Kristin Palmer
1292262744 | Yes | ALGIERS | FAIR | 2018-06-23 18:02 | 2018-06-23 21:00 | 2018-06-23 22:05 | W1726 | ENOI | TFUS | 1052374 | 4235646160 | DLIN | 81 | 23 | 5589 | 243 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change transformer | -89.9962 | 29.9294 | 70131 | C | Council District C | Jay Banks
1294363245 | Yes | ORLEANS | HEAT | 2018-07-27 13:04 | 2018-07-27 13:11 | 2018-07-27 14:00 | 2014 | ENOI | LFUS | 33112 | 3804046887 | DLIN | 1 | 24 | 1344 | 56 | ANIMAL | ASQL | Animal - Squirrel | N | line fuse taken out by squirrel jruffi1 | -90.1323 | 29.9507 | 70118 | A | Council District A | Joseph Giarrusso
1292446763 | Yes | EAST ORLEANS | RAIN | 2018-06-27 15:25 | 2018-06-27 16:25 | 2018-06-27 16:30 | 1702 | ENOI | LFUS | 21617 | 4063248970 | DLIN | 6 | 24 | 1560 | 65 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew repaired, back on | -90.0496 | 30.0072 | 70122 | D | Council District D | Kristin Palmer
1293507594 | Yes | ORLEANS | THDR | 2018-07-15 16:04 | 2018-07-15 18:17 | 2018-07-15 20:04 | 1705 | ENOI | LFUS | 27868 | 3966847557 | DLIN | 1 | 24 | 5760 | 240 | EQUIPMENT | EARM | Equipment - Crossarm | N | bad arm | -90.0806 | 29.9686 | 70119 | D | Council District D | Kristin Palmer
1294495973 | Yes | EAST ORLEANS | FAIR | 2018-07-29 21:39 | 2018-07-29 21:49 | 2018-07-29 23:59 | 2215 | ENOI | LFUS | 25973 | 4312350638 | DLIN | 6 | 24 | 3360 | 140 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer at 37 Marywood | -89.9703 | 30.0524 | 70128 | E | Council District E | Joseph Giarrusso
1292047973 | Yes | EAST ORLEANS | FAIR | 2018-06-19 19:17 | 2018-06-19 20:01 | 2018-06-19 20:39 | 1710 | ENOI | LFUS | 32053 | 4064648475 | DLIN | 6 | 25 | 2050 | 82 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel blew transformer fuse in front of 2520 sage and also took out c phase lateral switch on the corner of franklin and sage (no lateral switch number on pole) re fused transformer and lateral ok-cust back on swa | -90.0494 | 29.9937 | 70122 | D | Council District D | Jay Banks
1291584749 | Yes | ALGIERS | THDR | 2018-06-12 14:43 | 2018-06-12 16:20 | 2018-06-12 16:20 | W1713 | ENOI | LFUS | 5641 | 4234346069 | DLIN | 81 | 27 | 2619 | 97 | LIGHTNING | LGHT | Lightning | N | Changed **LFUS 5641 46 to LFUS 5641 4** --- lightening took out lateral nwashi1 | -89.9967 | 29.9269 | 70131 | C | Council District C | Jay Banks
1293191932 | Yes | ORLEANS | FAIR | 2018-07-09 07:16 | 2018-07-09 09:57 | 2018-07-09 10:20 | 2014 | ENOI | XFMR | 33142 | 3803446892 | DLIN | 1 | 27 | 4968 | 184 | EQUIPMENT | EARR | Equipment - Arrestor | N | Changed **LFUS 33142 60 to XFMR 33142 60** --- arester failed on tank cleared refused ok made a ticket to replace jbologn | -90.1325 | 29.9508 | 70118 | A | Council District A | Jay Banks
1291942685 | Yes | ORLEANS | THDR | 2018-06-18 11:54 | 2018-06-18 12:09 | 2018-06-18 14:53 | 1923 | ENOI | LFUS | 27792 | 3925145879 | DLIN | 1 | 28 | 4984 | 178 | VEGETATION | VOHL | Overhanging Limb | N | REMOVED REFUSED | -90.0944 | 29.9227 | 70115 | B | Council District B | Cyndi Nguyen
1291410841 | Yes | EAST ORLEANS | FAIR | 2018-06-09 15:02 | 2018-06-09 18:26 | 2018-06-09 18:27 | 2346 | ENOI | LFUS | 27848 | 4181447129 | DLIN | 6 | 28 | 5740 | 205 | EQUIPMENT | EARM | Equipment - Crossarm | N | in front of 818 Tupelo broken arms crew to replace | -90.0129 | 29.9562 | 70117 | E | Council District E | Cyndi Nguyen
1292683801 | Yes | EAST ORLEANS | THDR | 2018-07-01 21:03 | 2018-07-01 22:19 | 2018-07-01 22:45 | 2212 | ENOI | LFUS | 23024 | 4187250055 | DLIN | 6 | 29 | 2958 | 102 | LIGHTNING | LGHT | Lightning | N | refused oh and ug lateral weather cschexn | -90.01 | 30.0367 | 70126 | E | Council District E | Kristin Palmer
1294553056 | Yes | ORLEANS | FAIR | 2018-07-30 21:11 | 2018-07-30 22:22 | 2018-07-31 00:31 | 1926 | ENOI | XFMR | 29726 | 38778463773 | DLIN | 1 | 31 | 6200 | 200 | EQUIPMENT | ETRD | Equipment - Transformer | N | replaced bad transformer | -90.1092 | 29.9366 | 70115 | B | Council District B | Cyndi Nguyen
1291503289 | Yes | ALGIERS | THDR | 2018-06-11 13:01 | 2018-06-11 15:17 | 2018-06-11 16:47 | W1715 | ENOI | LFUS | 93149 | 4451845424 | DLIN | 81 | 32 | 7232 | 226 | LIGHTNING | LGHT | Lightning | N | lighting ook douwn priamary all back n now brizzut | -89.9283 | 29.9086 | 70131 | C | Council District C | Kristin Palmer
1292782203 | Yes | ALGIERS | THDR | 2018-07-03 06:31 | 2018-07-03 08:12 | 2018-07-03 08:36 | W0712 | ENOI | LFUS | 34314 | 4206845751 | DLIN | 81 | 32 | 4000 | 125 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | tree behind 3336 river oaks dr took out transformer and lateral ok now sphill1 | -90.0054 | 29.9184 | 70131 | C | Council District C | Jay Banks
1293423295 | Yes | EAST ORLEANS | FAIR | 2018-07-13 09:56 | 2018-07-13 10:21 | 2018-07-13 11:25 | 2213 | ENOI | LFUS | 27037 | 4394850834 | DLIN | 6 | 32 | 2848 | 89 | EQUIPMENT | ETRD | Equipment - Transformer | N | c phase lateral out from switch 27037-bad pot in vault 54-isolated transformer and re fused switch 27037 and normal opening in vault 57 to pick up the rest of the customers-only cust out are fed from v-54called crew | -97.0758 | 27.9066 | 70128 | E | Council District E | Cyndi Nguyen
1291456026 | NO | EAST ORLEANS | THDR | 2018-06-10 12:36 | 2018-06-10 13:05 | 2018-06-10 13:20 | 2326 | ENOI | TRAN | 2326 | 4214647799 | TLIN | 6 | 32 | 1376 | 43 | OTHER | UNKI | Unknown - Under Investigation | N | Loss of source from Michoud Line to ARABI and Tricou TCCS tried closing DERBNY N9702 but couldnt close substation in route | -90.0023 | 29.9746 | 70117 | E | Council District E | Cyndi Nguyen
1291863225 | Yes | ALGIERS | HEAT | 2018-06-17 09:27 | 2018-06-17 11:22 | 2018-06-17 11:44 | W0714 | ENOI | LFUS | 11162 | 4199645494 | DLIN | 81 | 33 | 4521 | 137 | CONDUCTOR | CFID | Cable in duct | N | Changed **LFUS 11162 60 to LFUS 11162 42** --- bad cable sw#11162 to first to 100by 660081 gcharl1 | -90.0078 | 29.9112 | 70131 | C | Council District C | Jared Brossett
1291785391 | Yes | EAST ORLEANS | HEAT | 2018-06-15 00:08 | 2018-06-15 02:47 | 2018-06-15 04:41 | 2212 | ENOI | LFUS | 25183 | 4224550149 | DLIN | 6 | 33 | 9009 | 273 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | bgad cable between Vault 50 and pole dip 25183 (pwd) | -89.9982 | 30.0392 | 70127 | E | Council District E | Kristin Palmer
1292442183 | Yes | EAST ORLEANS | THDR | 2018-06-27 14:02 | 2018-06-27 19:35 | 2018-06-27 21:08 | 2212 | ENOI | LFUS | 25183 | 4224550149 | DLIN | 6 | 33 | 14058 | 426 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -89.9982 | 30.0392 | 70127 | E | Council District E | Jay Banks
1293512655 | Yes | EAST ORLEANS | FAIR | 2018-07-15 17:36 | 2018-07-15 17:57 | 2018-07-15 18:28 | 616 | ENOI | LFUS | 74488 | 4115847718 | DLIN | 6 | 36 | 1872 | 52 | LIGHTNING | LGHT | Lightning | N | Fuse around switches 23073 blown--closed 600a disconnect switches due to 100a switches burnt jvickna | -90.0334 | 29.9728 | 70117 | D | Council District D | Joseph Giarrusso
1290969736 | Yes | ALGIERS | HEAT | 2018-06-02 20:49 | 2018-06-02 21:21 | 2018-06-02 21:46 | W1715 | ENOI | LFUS | 5541-F | 4447445484 | DLIN | 81 | 37 | 2109 | 57 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | burnt snap tap repaired ok brizzut | -89.9295 | 29.9101 | 70131 | C | Council District C | Joseph Giarrusso
1291475395 | Yes | ORLEANS | FAIR | 2018-06-10 17:05 | 2018-06-10 17:20 | 2018-06-10 18:09 | 1712 | ENOI | TFUS | 21915 | 3961247426 | DLIN | 1 | 38 | 2432 | 64 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | Changed **LFUS 21915 92 to TFUS 21915 92** --- refused transformer ok taken out by non recordable bird needs tree trimming to get to transformer to install bird jdomang | -90.0823 | 29.9651 | 70119 | B | Council District B | Cyndi Nguyen
1291760886 | Yes | ORLEANS | THDR | 2018-06-14 14:10 | 2018-06-14 14:10 | 2018-06-14 16:11 | 615 | ENOI | OPEN | 3985347742 | 3985347742 | DLIN | 1 | 38 | 4598 | 121 | CONDUCTOR | EOSC | Equipment - Shield Conductor | N | SHEILD WIRE DOWN CREW TO PICKUP | -90.0747 | 29.9737 | 70119 | D | Council District D | Joseph Giarrusso
1292442644 | Yes | EAST ORLEANS | THDR | 2018-06-27 14:04 | 2018-06-27 17:32 | 2018-06-27 21:07 | 2212 | ENOI | LFUS | 25217 | 4240450217 | DLIN | 6 | 41 | 17343 | 423 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -89.9932 | 30.041 | 70127 | E | Council District E | Cyndi Nguyen
1291246618 | Yes | ORLEANS | HEAT | 2018-06-06 14:00 | 2018-06-06 14:11 | 2018-06-06 14:52 | 411 | ENOI | LFUS | 17771 | 3855249253 | DLIN | 1 | 42 | 2142 | 51 | EQUIPMENT | EARR | Equipment - Arrestor | N | refused C phase only taking out by old arester mounted on lat arm went to abandoned kicker tranformer jbologn | -90.1152 | 30.0157 | 70124 | A | Council District A | Cyndi Nguyen
1291956834 | Yes | EAST ORLEANS | THDR | 2018-06-18 13:39 | 2018-06-18 16:08 | 2018-06-18 16:20 | 626 | ENOI | LFUS | 27659 | 4104948271 | DLIN | 6 | 43 | 6923 | 161 | EQUIPMENT | EARM | Equipment - Crossarm | N | CREW TO REPAIR BROKEN CROSSARM AT 3124 FELICIANA STREET | -90.0367 | 29.988 | 70126 | D | Council District D | Kristin Palmer
1291758951 | Yes | ALGIERS | THDR | 2018-06-14 13:10 | 2018-06-14 13:22 | 2018-06-14 13:42 | W0715 | ENOI | LFUS | 72409 | 4122245895 | DLIN | 81 | 44 | 1408 | 32 | LIGHTNING | LGHT | Lightning | N | Changed **LFUS 72409 45 to LFUS 72409 4** --- multiple laterals and transformers switches blown/ one pot stiil out bad/crew needed 2924 donner dr nwashi1 | -90.032 | 29.9224 | 70114 | C | Council District C | Cyndi Nguyen
1294540306 | Yes | EAST ORLEANS | FAIR | 2018-07-30 16:34 | 2018-07-30 17:42 | 2018-07-30 18:41 | 1612 | ENOI | LFUS | 27661 | 4347249587 | DLIN | 6 | 46 | 5842 | 127 | LIGHTNING | LGHT | Lightning | N | refused c phase.. tbrock | -89.9597 | 30.0234 | 70127 | E | Council District E | Cyndi Nguyen
1292167298 | Yes | ORLEANS | FAIR | 2018-06-22 10:36 | 2018-06-22 11:05 | 2018-06-22 11:19 | 1513 | ENOI | LFUS | 23124 | 3939447201 | DLIN | 1 | 46 | 1978 | 43 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | UG diP pole at 528 S. Dorgenois took out main lat B pase only refused ok jbologn | -90.0886 | 29.9593 | 70119 | B | Council District B | Joseph Giarrusso
1292411113 | Yes | EAST ORLEANS | FAIR | 2018-06-26 15:53 | 2018-06-26 16:39 | 2018-06-26 16:55 | 2217 | ENOI | LFUS | 22155 | 4360450861 | DLIN | 6 | 47 | 2914 | 62 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lateral over head section blown refused ok cschexn | -89.9551 | 30.0582 | 70128 | E | Council District E | Kristin Palmer
1291717703 | Yes | ORLEANS | FAIR | 2018-06-13 19:15 | 2018-06-13 19:44 | 2018-06-13 19:52 | 2027 | ENOI | LFUS | 38029 | 3869047109 | DLIN | 1 | 48 | 1776 | 37 | OTHER | FOBJ | Foreign Objects - Other | N | ballons took lateral out. removed balloons and refued lateral dsmit36 | -90.1116 | 29.9568 | 70125 | B | Council District B | Cyndi Nguyen
1292642841 | Yes | ORLEANS | THDR | 2018-06-30 23:31 | 2018-07-01 02:47 | 2018-07-01 03:45 | 1709 | ENOI | OPEN | 3983648080 | 3983648080 | DLIN | 1 | 48 | 12192 | 254 | EQUIPMENT | EARM | Equipment - Crossarm | N | bad arm | -90.0751 | 29.983 | 70119 | D | Council District D | Cyndi Nguyen
1291386969 | Yes | EAST ORLEANS | FAIR | 2018-06-09 06:32 | 2018-06-09 09:32 | 2018-06-09 10:36 | 1702 | ENOI | LFUS | 21625 | 4057148946 | DLIN | 6 | 49 | 11956 | 244 | VEGETATION | VOHL | Overhanging Limb | N | tree fell pulled wire down crew to pickup | -90.0515 | 30.0066 | 70122 | D | Council District D | Kristin Palmer
1294057704 | Yes | ORLEANS | HEAT | 2018-07-21 15:25 | 2018-07-21 15:25 | 2018-07-21 16:37 | 1554 | ENOI | TFUS | 677907 | 3967546679 | DLIN | 1 | 51 | 3672 | 72 | ANIMAL | ASQL | Animal - Squirrel | N | squirell took out c phase on terminal pole. refused tsmit29 | -90.0807 | 29.9446 | 70113 | B | Council District B | Cyndi Nguyen
1291737492 | Yes | ALGIERS | HEAT | 2018-06-14 00:57 | 2018-06-14 01:40 | 2018-06-14 02:24 | W1714 | ENOI | LFUS | 33806 | 4245545437 | DLIN | 81 | 51 | 4437 | 87 | CONDUCTOR | CFID | Cable in duct | N | bad cable all back on brizzut | -89.9934 | 29.9095 | 70131 | C | Council District C | Cyndi Nguyen
1292411314 | Yes | EAST ORLEANS | FAIR | 2018-06-26 15:54 | 2018-06-26 16:08 | 2018-06-26 18:35 | 2223 | ENOI | LFUS | 23476 | 4333250949 | DLIN | 6 | 51 | 8211 | 161 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | crew to test cable and repair. jar | -89.9637 | 30.0609 | 70128 | E | Council District E | Cyndi Nguyen
1293885514 | Yes | ORLEANS | FAIR | 2018-07-20 21:22 | 2018-07-20 21:26 | 2018-07-20 22:24 | 1914 | ENOI | LFUS | 27914 | 3884446128 | DLIN | 1 | 52 | 3224 | 62 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | load side riser on c phase burned loose bp s back in power jruffi1 | -90.1071 | 29.9297 | 70115 | B | Council District B | Jared Brossett
1292392241 | Yes | EAST ORLEANS | FAIR | 2018-06-26 02:49 | 2018-06-26 04:27 | 2018-06-26 04:25 | 2214 | ENOI | LFUS | 25878 | 4309450396 | DLIN | 6 | 53 | 5088 | 96 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | Changed **LFUS 25878 112 to LFUS 25878 52** --- open half way on lateral refused called crew to work lateral cschexn | -97.0758 | 27.9066 | 70128 | E | Council District E | Cyndi Nguyen
1292393037 | Yes | EAST ORLEANS | FAIR | 2018-06-26 05:23 | 2018-06-26 06:16 | 2018-06-26 06:56 | 2214 | ENOI | LFUS | 25878 | 4309450396 | DLIN | 6 | 53 | 4929 | 93 | OTHER | UNKN | Inspected Unknown | N | inspected and renewed fuse, no known cause. jar | -97.0758 | 27.9066 | 70128 | E | Council District E | Jay Banks
1292783663 | Yes | EAST ORLEANS | FAIR | 2018-07-03 07:22 | 2018-07-03 07:25 | 2018-07-03 08:30 | 2346 | ENOI | LFUS | 32218 | 4148247277 | DLIN | 6 | 54 | 3672 | 68 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.0234 | 29.9605 | 70117 | E | Council District E | Joseph Giarrusso
1291870093 | Yes | EAST ORLEANS | FAIR | 2018-06-17 11:01 | 2018-06-17 15:10 | 2018-06-17 15:04 | 1604 | ENOI | LFUS | 27966 | 4281449404 | DLIN | 6 | 55 | 13365 | 243 | EQUIPMENT | EPOL | Equipment - Pole | N | crew to fix pole | -89.9805 | 30.0185 | 70127 | E | Council District E | Cyndi Nguyen
1291963983 | Yes | ORLEANS | THDR | 2018-06-18 15:13 | 2018-06-18 16:23 | 2018-06-18 17:21 | 1512 | ENOI | TFUS | 78275 | 39159473209 | DLIN | 1 | 57 | 7296 | 128 | EQUIPMENT | EARM | Equipment - Crossarm | N | BROKEN CROSSARM | -90.0967 | 29.9623 | 70119 | B | Council District B | Joseph Giarrusso
1291949014 | Yes | ORLEANS | THDR | 2018-06-18 12:55 | 2018-06-18 13:39 | 2018-06-18 13:49 | 1916 | ENOI | LFUS | 21383 | 3896546049 | DLIN | 1 | 58 | 3132 | 54 | VEGETATION | VOHL | Overhanging Limb | N | REMOVED TREE REFUSED OKAY | -90.1034 | 29.9273 | 70115 | B | Council District B | Joseph Giarrusso
1292749072 | Yes | ORLEANS | THDR | 2018-07-02 19:34 | 2018-07-02 20:28 | 2018-07-02 21:01 | 2026 | ENOI | LFUS | 43673 | 3856747794 | DLIN | 1 | 58 | 5046 | 87 | VEGETATION | VOHL | Overhanging Limb | N | removed tree on A phase out refused okay | -90.1152 | 29.9755 | 70118 | A | Council District A | Joseph Giarrusso
1292267496 | Yes | ORLEANS | FAIR | 2018-06-23 21:37 | 2018-06-23 22:25 | 2018-06-23 22:52 | 615 | ENOI | LFUS | 50014 | 3994547626 | DLIN | 1 | 58 | 4350 | 75 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | load side riser burned loose fixed ok jruffi1 | -90.0719 | 29.9706 | 70116 | D | Council District D | Joseph Giarrusso
1294526282 | Yes | EAST ORLEANS | THDR | 2018-07-30 12:41 | 2018-07-30 14:18 | 2018-07-30 15:07 | 612 | ENOI | LFUS | 21124 | 4118747946 | DLIN | 6 | 58 | 8468 | 146 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to repair arm | -90.0326 | 29.9789 | 70117 | D | Council District D | Cyndi Nguyen
1292409484 | Yes | ORLEANS | RAIN | 2018-06-26 14:51 | 2018-06-26 16:23 | 2018-06-26 16:32 | 2026 | ENOI | LFUS | 43673 | 3856747794 | DLIN | 1 | 58 | 5858 | 101 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused a phase on lateral cause unknown rdeano | -90.1152 | 29.9755 | 70118 | A | Council District A | Jay Banks
1292918318 | Yes | ORLEANS | HEAT | 2018-07-05 12:57 | 2018-07-05 14:21 | 2018-07-05 17:00 | 2012 | ENOI | LFUS | 21875 | 3882948455 | DLIN | 1 | 60 | 14580 | 243 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.1068 | 29.9937 | 70124 | A | Council District A | Cyndi Nguyen
1293897339 | Yes | ORLEANS | FAIR | 2018-07-21 00:54 | 2018-07-21 02:24 | 2018-07-21 04:07 | 2147 | ENOI | LFUS | 33991 | 3979645919 | DLIN | 1 | 61 | 11773 | 193 | EQUIPMENT | EARM | Equipment - Crossarm | N | broken dead end arm...crew to change...complete | -90.0772 | 29.9236 | 70130 | B | Council District B | Cyndi Nguyen
1294524658 | Yes | ALGIERS | FAIR | 2018-07-30 12:08 | 2018-07-30 12:55 | 2018-07-30 13:10 | W1713 | ENOI | LFUS | 11323-F | 4247145772 | DLIN | 81 | 64 | 3968 | 62 | LIGHTNING | LGHT | Lightning | N | refused ok zwashin | -89.9928 | 29.9187 | 70131 | C | Council District C | Cyndi Nguyen
1292055110 | Yes | ORLEANS | FAIR | 2018-06-20 03:16 | 2018-06-20 06:25 | 2018-06-20 06:23 | 2026 | ENOI | LFUS | 27626 | 3884847852 | DLIN | 1 | 64 | 11968 | 187 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | crew to fix C phase only | -90.1064 | 29.977 | 70119 | A | Council District A | Jared Brossett
1293157381 | Yes | EAST ORLEANS | FAIR | 2018-07-08 19:49 | 2018-07-08 23:40 | 2018-07-09 01:01 | 2215 | ENOI | LFUS | 25973 | 4312350638 | DLIN | 6 | 64 | 19968 | 312 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | bad urd cable | -89.9703 | 30.0524 | 70128 | E | Council District E | Jared Brossett
1294075853 | Yes | ORLEANS | HEAT | 2018-07-21 18:47 | 2018-07-21 20:08 | 2018-07-21 20:15 | 413 | ENOI | LFUS | 17544 | 3900348631 | DLIN | 1 | 65 | 5720 | 88 | Summary Missing | EONE | Equipment - Neutral / Shield Conductor | N | sheild broke st pole, Crew repaired per 305 jruffi1 | -90.1012 | 29.9985 | 70124 | A | Council District A | Joseph Giarrusso
1294003861 | Yes | ORLEANS | HEAT | 2018-07-21 08:56 | 2018-07-21 09:40 | 2018-07-21 10:19 | 413 | ENOI | LFUS | 17544 | 3900348631 | DLIN | 1 | 65 | 5395 | 83 | OTHER | UNKN | Inspected Unknown | N | rose out lateral didnt find any cause for outage refused lateral tsmit29 | -90.1012 | 29.9985 | 70124 | A | Council District A | Jared Brossett
1292554956 | Yes | ORLEANS | FAIR | 2018-06-29 09:27 | 2018-06-29 10:04 | 2018-06-29 09:55 | 1915 | ENOI | LFUS | 27770 | 3934146561 | DLIN | 1 | 67 | 1876 | 28 | OTHER | FOBJ | Foreign Objects - Other | N | Balloons got into phases burning wire down, crew is on site making repairs. | -90.0914 | 29.9414 | 70113 | B | Council District B | Kristin Palmer
1292782771 | Yes | ORLEANS | FAIR | 2018-07-03 07:15 | 2018-07-03 14:22 | 2018-07-03 15:00 | 410 | ENOI | LFUS | 17752 | 3833648607 | DLIN | 1 | 67 | 31155 | 465 | VEGETATION | VOHL | Overhanging Limb | N | crew made repairs | -90.1222 | 29.998 | 70124 | A | Council District A | Jay Banks
1293324207 | Yes | ORLEANS | THDR | 2018-07-11 17:49 | 2018-07-11 19:58 | 2018-07-11 20:00 | 627 | ENOI | LFUS | 27611 | 4026248043 | DLIN | 1 | 67 | 8777 | 131 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -90.0616 | 29.9819 | 70119 | D | Council District D | Kristin Palmer
1291819641 | Yes | ORLEANS | HEAT | 2018-06-15 18:34 | 2018-06-15 18:59 | 2018-06-15 19:22 | 1705 | ENOI | LFUS | 38003 | 3986247643 | DLIN | 1 | 69 | 3312 | 48 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | lfus blew. refused ok. dsmit36 | -90.0743 | 29.971 | 70116 | D | Council District D | Jay Banks
1293477602 | Yes | ORLEANS | FAIR | 2018-07-14 16:43 | 2018-07-14 20:26 | 2018-07-14 22:16 | 1924 | ENOI | LFUS | 21484 | 3923146070 | DLIN | 1 | 70 | 23310 | 333 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.095 | 29.928 | 70115 | B | Council District B | Jared Brossett
1292203116 | Yes | ALGIERS | FAIR | 2018-06-22 20:19 | 2018-06-22 21:00 | 2018-06-22 21:12 | W1713 | ENOI | RCLR | 82765 | 4237046123 | DLIN | 81 | 71 | 3763 | 53 | VEGETATION | VOHL | Overhanging Limb | N | tree on line had to open recloser to make repairs and remove tree | -89.9958 | 29.9284 | 70131 | C | Council District C | Cyndi Nguyen
1290920118 | Yes | ALGIERS | FAIR | 2018-06-01 18:08 | 2018-06-01 18:22 | 2018-06-01 18:23 | W1726 | ENOI | LFUS | 33334 | 4215946276 | DLIN | 81 | 72 | 1080 | 15 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew closed in on bad transformer and blew lateral | -90.0024 | 29.9328 | 70131 | C | Council District C | Kristin Palmer
1291384528 | Yes | EAST ORLEANS | FAIR | 2018-06-09 04:35 | 2018-06-09 04:53 | 2018-06-09 05:00 | 2212 | ENOI | LFUS | 24971 | 4214250165 | DLIN | 6 | 73 | 1825 | 25 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | trouble shooting loop and blew this side of the ug loop | -90.0015 | 30.0396 | 70126 | E | Council District E | Cyndi Nguyen
1291741366 | Yes | EAST ORLEANS | FAIR | 2018-06-14 05:57 | 2018-06-14 06:51 | 2018-06-14 08:31 | 2212 | ENOI | LFUS | 24971 | 4214250165 | DLIN | 6 | 73 | 11242 | 154 | OTHER | UNKN | Inspected Unknown | N |  | -90.0015 | 30.0396 | 70126 | E | Council District E | Jay Banks
1290963712 | Yes | ORLEANS | FAIR | 2018-06-02 18:07 | 2018-06-02 18:37 | 2018-06-02 19:21 | 1915 | ENOI | LFUS | 28054 | 3942246645 | DLIN | 1 | 78 | 5772 | 74 | OTHER | FOBJ | Foreign Objects - Other | N | c phase of lateral taken out by mylar balloons, refused ok droser | -90.0887 | 29.9436 | 70113 | B | Council District B | Jared Brossett
1292585495 | Yes | ALGIERS | THDR | 2018-06-29 16:55 | 2018-06-29 19:48 | 2018-06-29 21:29 | W1715 | ENOI | LFUS | 5503 | 4334745608 | DLIN | 81 | 80 | 21920 | 274 | LIGHTNING | LGHT | Lightning | N | Changed **LFUS 5503 80 to LFUS 5503 54** --- refused switch 5503 from lightning refused sub latt switch 5531 from tree on line cleared. mtaruc | -89.9652 | 29.914 | 70131 | C | Council District C | Joseph Giarrusso
1293347313 | Yes | EAST ORLEANS | FAIR | 2018-07-12 02:07 | 2018-07-12 03:51 | 2018-07-12 04:48 | 1710 | ENOI | LFUS | 98046 | 40472485972 | DLIN | 6 | 80 | 12880 | 161 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | a phase lattral out refused need get tree crew trim trees cbowden | -90.0549 | 29.997 | 70122 | D | Council District D | Jay Banks
1294113762 | Yes | EAST ORLEANS | FAIR | 2018-07-22 10:22 | 2018-07-22 10:57 | 2018-07-22 11:52 | 1609 | ENOI | LFUS | 27177 | 4351250071 | DLIN | 6 | 80 | 7200 | 90 | EQUIPMENT | ETRD | Equipment - Transformer | N | need to minus out the cust. on the transformer case | -97.0758 | 27.9066 | 70128 | E | Council District E | Cyndi Nguyen
1291385103 | Yes | ORLEANS | FAIR | 2018-06-09 05:13 | 2018-06-09 06:44 | 2018-06-09 07:15 | 2014 | ENOI | LFUS | 21179 | 3800746955 | DLIN | 1 | 83 | 10126 | 122 | EQUIPMENT | EARR | Equipment - Arrestor | N | ARRESTOR BLEW C PHASE OUT ONLY | -90.1333 | 29.9528 | 70118 | A | Council District A | Jay Banks
1291475577 | Yes | ORLEANS | THDR | 2018-06-10 17:10 | 2018-06-10 17:26 | 2018-06-10 18:05 | 2014 | ENOI | OPEN | 3822746670 | 3822746670 | DLIN | 1 | 87 | 4785 | 55 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to repair crossarm in trouble | -90.1264 | 29.9447 | 70118 | A | Council District A | Cyndi Nguyen
1292651673 | Yes | ORLEANS | THDR | 2018-06-30 23:32 | 2018-07-01 02:42 | 2018-07-01 02:55 | 2012 | ENOI | OPEN | 3882548031 | 3882548031 | DLIN | 1 | 88 | 17864 | 203 | EQUIPMENT | EARM | Equipment - Crossarm | N | bad arm | -90.1071 | 29.982 | 70119 | A | Council District A | Cyndi Nguyen
1294526202 | Yes | ORLEANS | FAIR | 2018-07-30 13:15 | 2018-07-30 13:26 | 2018-07-30 13:49 | 2135 | ENOI | LFUS | 34187 | 3985346308 | DLIN | 1 | 91 | 3094 | 34 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | tree on line | -90.0753 | 29.9343 | 70130 | B | Council District B | Cyndi Nguyen
1292056464 | Yes | ORLEANS | FAIR | 2018-06-20 06:04 | 2018-06-20 06:57 | 2018-06-20 07:00 | 408 | ENOI | LFUS | F14254 | 3876148880 | DLIN | 1 | 92 | 5152 | 56 | ANIMAL | ASQL | Animal - Squirrel | N | found squirrel in alley of colbert took out A phase of lat 17752 witch took out A phase of F14254 jbologn | -90.1086 | 30.0053 | 70124 | A | Council District A | Kristin Palmer
1293413349 | Yes | EAST ORLEANS | FAIR | 2018-07-13 03:10 | 2018-07-13 08:20 | 2018-07-13 09:32 | 622 | ENOI | LFUS | 50003 | 4068547762 | DLIN | 6 | 92 | 35144 | 382 | HUMAN FACTORS | VHCL | Vehicle | N | crew replaced broken pole | -90.0486 | 29.974 | 70117 | C | Council District C | Cyndi Nguyen
1291104909 | Yes | ORLEANS | HEAT | 2018-06-04 12:39 | 2018-06-04 12:39 | 2018-06-04 13:25 | 2015 | ENOI | LFUS | 35158 | 3845847140 | DLIN | 1 | 94 | 4324 | 46 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | piegon on steel arm for transformer cut-out in front of 2514 camborne took sub lat.on A phase out at apple and cambornne DLOC 3837547216 need switch numbers does show in system jbologn | -90.119 | 29.9575 | 70118 | A | Council District A | Jay Banks
1292011459 | Yes | ORLEANS | FAIR | 2018-06-19 10:56 | 2018-06-19 11:09 | 2018-06-19 11:36 | 1513 | ENOI | LFUS | 23124 | 3939447201 | DLIN | 1 | 95 | 3800 | 40 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | taking out by UG dip pole on S Dorgenois bad cable (21334) refused ok jbologn | -90.0886 | 29.9593 | 70119 | B | Council District B | Cyndi Nguyen
1291825563 | Yes | EAST ORLEANS | RAIN | 2018-06-16 01:41 | 2018-06-16 03:05 | 2018-06-16 03:16 | 2216 | ENOI | LFUS | 26002 | UNK | DLIN | 6 | 95 | 9025 | 95 | OTHER | UNKN | Inspected Unknown | N | B phase target in VFI 506, Serviceman give it a close and it held. Will need to follow up with vault inspections. | -97.0758 | 27.9066 | 70127 | E | Council District E | Jay Banks
1293465317 | Yes | ORLEANS | HEAT | 2018-07-14 07:16 | 2018-07-14 08:06 | 2018-07-14 09:19 | 2147 | ENOI | LFUS | 27679 | 3947245994 | DLIN | 1 | 96 | 11808 | 123 | EQUIPMENT | ETRD | Equipment - Transformer | N | possible fuse link overload. refused lateral ok dsmit36 Sericeman found bad trans | -90.0875 | 29.9258 | 70115 | B | Council District B | Kristin Palmer
1291758345 | Yes | ALGIERS | THDR | 2018-06-14 13:01 | 2018-06-14 14:15 | 2018-06-14 14:25 | W0712 | ENOI | LFUS | 10925 | 4203545671 | DLIN | 81 | 99 | 8316 | 84 | LIGHTNING | LGHT | Lightning | N | refused transformers and lat switches zwashin | -90.0065 | 29.9161 | 70131 | C | Council District C | Cyndi Nguyen
1291447078 | Yes | EAST ORLEANS | FAIR | 2018-06-10 10:08 | 2018-06-10 12:18 | 2018-06-10 11:09 | 2212 | ENOI | LFUS | 24972 | 4199150097 | DLIN | 6 | 103 | 6283 | 61 | EQUIPMENT | EELB | Equipment - Elbow | N | Changed **LFUS 24972 226 to LFUS 24972 98** --- work with crew to restore power on ug lateral replaced bad elbows refuse lateral cschexn | -90.0064 | 30.0378 | 70126 | E | Council District E | Jared Brossett
1294480909 | Yes | ORLEANS | FAIR | 2018-07-29 17:01 | 2018-07-29 17:36 | 2018-07-29 19:04 | 615 | ENOI | LFUS | 36957 | 4004747873 | DLIN | 1 | 103 | 12669 | 123 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused b phase unknown rdeano | -90.0684 | 29.9773 | 70116 | D | Council District D | Cyndi Nguyen
1291739552 | Yes | EAST ORLEANS | FAIR | 2018-06-14 03:42 | 2018-06-14 06:52 | 2018-06-14 07:19 | 2212 | ENOI | LFUS | 24972 | 4199150097 | DLIN | 6 | 103 | 22351 | 217 | OTHER | UNKN | Inspected Unknown | N |  | -90.0064 | 30.0378 | 70126 | E | Council District E | Kristin Palmer
1291434586 | Yes | EAST ORLEANS | FAIR | 2018-06-09 20:24 | 2018-06-10 01:25 | 2018-06-10 01:30 | 2212 | ENOI | LFUS | 21264 | 4197650136 | DLIN | 6 | 105 | 32130 | 306 | EQUIPMENT | EELB | Equipment - Elbow | N |  | -90.0069 | 30.0389 | 70126 | E | Council District E | Kristin Palmer
1292382723 | Yes | ORLEANS | HEAT | 2018-06-25 18:07 | 2018-06-26 03:36 | 2018-06-26 04:15 | 1926 | ENOI | DIS | 23137 | 3867746372 | DLIN | 1 | 107 | 65056 | 608 | EQUIPMENT | EARM | Equipment - Crossarm | N | Broke crossarm at 2300 Joseph St. Crew had to change out angle structure. | -90.1123 | 29.9363 | 70115 | A | Council District A | Joseph Giarrusso
1291825498 | Yes | EAST ORLEANS | RAIN | 2018-06-16 01:39 | 2018-06-16 03:03 | 2018-06-16 03:15 | 2216 | ENOI | VFI | 506 | UNK | DLIN | 6 | 109 | 10464 | 96 | HUMAN FACTORS | HEMC | Mis-Coordination (Describe in remarks) | N | serviceman found 37196 in the tripped position. Closed and holding. Unknown cause.: Engineer did coord. study & will adjust relays | -97.0758 | 27.9066 | 70127 | E | Council District E | Jared Brossett
1294346856 | Yes | EAST ORLEANS | HEAT | 2018-07-27 00:48 | 2018-07-27 05:05 | 2018-07-27 05:26 | 1609 | ENOI | LFUS | 27177 | 4351250071 | DLIN | 6 | 110 | 24798 | 278 | EQUIPMENT | EELB | Equipment - Elbow | N | split b phase in half front half blew....closed back half...crew to troubleshoot front half..reworked elbow at 5449 Stillwater | -97.0758 | 27.9066 | 70128 | E | Council District E | Kristin Palmer
1291382882 | Yes | EAST ORLEANS | FAIR | 2018-06-09 01:19 | 2018-06-09 06:12 | 2018-06-09 07:46 | 2212 | ENOI | LFUS | 24972 | 4199150097 | DLIN | 6 | 112 | 43344 | 387 | EQUIPMENT | ETRD | Equipment - Transformer | N | CREW REPLACED POT | -90.0064 | 30.0378 | 70126 | E | Council District E | Kristin Palmer
1291409209 | Yes | EAST ORLEANS | THDR | 2018-06-09 14:52 | 2018-06-09 17:53 | 2018-06-09 17:55 | 622 | ENOI | LFUS | 32647 | 4123847544 | DLIN | 6 | 118 | 21594 | 183 | EQUIPMENT | EARM | Equipment - Crossarm | N | lateral line down n robertson at lesseps called crew cschexn & broken cross-arms | -90.031 | 29.9678 | 70117 | D | Council District D | Joseph Giarrusso
1291505649 | Yes | ORLEANS | THDR | 2018-06-11 13:30 | 2018-06-11 15:04 | 2018-06-11 15:31 | 627 | ENOI | LFUS | 21205 | 4022848039 | DLIN | 1 | 119 | 14399 | 121 | EQUIPMENT | EPOL | Equipment - Pole | N | crew replacing broken pole | -90.0627 | 29.9817 | 70119 | D | Council District D | Jared Brossett
1293506882 | Yes | EAST ORLEANS | THDR | 2018-07-15 15:54 | 2018-07-15 17:11 | 2018-07-15 16:55 | 616 | ENOI | SBKR | 616 | 4081148420 | DLIN | 6 | 120 | 7200 | 60 | LIGHTNING | LGHT | Lightning | N |  | -90.0442 | 29.9921 | 70126 | D | Council District D | Kristin Palmer
1291739570 | Yes | EAST ORLEANS | FAIR | 2018-06-14 03:43 | 2018-06-14 05:45 | 2018-06-14 05:47 | 2212 | ENOI | LFUS | 27648 | 4212050212 | DLIN | 6 | 122 | 15128 | 124 | OTHER | UNKN | Inspected Unknown | N | unknow | -90.0022 | 30.041 | 70126 | E | Council District E | Jared Brossett
1292783760 | Yes | ORLEANS | FAIR | 2018-07-03 05:46 | 2018-07-03 09:53 | 2018-07-03 10:07 | 2146 | ENOI | DIS | 15134 | 3956946058 | DLIN | 1 | 124 | 32364 | 261 | EQUIPMENT | EARM | Equipment - Crossarm | N | Equipment - Crossarm | -90.0842 | 29.9276 | 70115 | B | Council District B | Jared Brossett
1293671546 | Yes | ORLEANS | THDR | 2018-07-17 15:00 | 2018-07-17 15:49 | 2018-07-17 15:53 | 1915 | ENOI | LFUS | 28059 | 3928646516 | DLIN | 1 | 128 | 6784 | 53 | LIGHTNING | LGHT | Lightning | N | Lightning | -90.0929 | 29.9402 | 70115 | B | Council District B | Jared Brossett
1294431552 | Yes | ORLEANS | FAIR | 2018-07-28 23:24 | 2018-07-29 00:05 | 2018-07-29 00:16 | 2021 | ENOI | LFUS | 21813 | 3928146648 | DLIN | 1 | 128 | 6656 | 52 | OTHER | UNKN | Inspected Unknown | N | Changed **LFUS 21813 134 to LFUS 21813 101** --- customer said someone hit pole found no damaged refused ok jbologn | -90.0932 | 29.9438 | 70125 | B | Council District B | Joseph Giarrusso
1291388808 | Yes | EAST ORLEANS | FAIR | 2018-06-09 05:57 | 2018-06-09 07:33 | 2018-06-09 07:40 | 1605 | ENOI | SWIT | 27069 | 4325249946 | DLIN | 6 | 129 | 13287 | 103 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | A rat flashed up S&WB cub. at 10451 Lake Forest. cub will need to be replaced | -97.0758 | 27.9066 | 70127 | E | Council District E | Joseph Giarrusso
1293863287 | Yes | ORLEANS | FAIR | 2018-07-20 15:02 | 2018-07-20 22:14 | 2018-07-20 23:11 | 1704 | ENOI | LFUS | 27650 | 3977248967 | DLIN | 1 | 135 | 66015 | 489 | VEGETATION | VOHL | Overhanging Limb | N | tree fell pulled down wire crew to pickup...complete | -90.0769 | 30.0073 | 70122 | D | Council District D | Kristin Palmer
1293705596 | Yes | ORLEANS | FAIR | 2018-07-18 00:49 | 2018-07-18 03:28 | 2018-07-18 03:35 | 403 | ENOI | DIS | 14841 | 3904249041 | DLIN | 1 | 138 | 22908 | 166 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Equipment - Primary Conductor | -90.0999 | 30.0098 | 70124 | A | Council District A | Jared Brossett
1294425762 | Yes | ORLEANS | THDR | 2018-07-28 21:02 | 2018-07-28 22:42 | 2018-07-28 23:25 | 1924 | ENOI | LFUS | 27637 | 3917746081 | DLIN | 1 | 140 | 20020 | 143 | EQUIPMENT | EARM | Equipment - Crossarm | N | crossarm down behind 27637, crew to make necessary repairs. | -90.0967 | 29.9283 | 70115 | B | Council District B | Jared Brossett
1290962212 | Yes | ORLEANS | THDR | 2018-06-02 17:53 | 2018-06-02 20:40 | 2018-06-02 21:01 | 2016 | ENOI | LFUS | 27919 | 3843846812 | DLIN | 1 | 141 | 26508 | 188 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.1201 | 29.9487 | 70118 | A | Council District A | Jay Banks
1291388751 | Yes | ORLEANS | HEAT | 2018-06-09 07:14 | 2018-06-09 09:54 | 2018-06-09 10:00 | 1923 | ENOI | LFUS | 21462 | 3916245912 | DLIN | 1 | 142 | 23572 | 166 | ANIMAL | ASQL | Animal - Squirrel | N | Changed **LFUS 21462 151 to LFUS 21462 142** --- refused lateral A phase only taken out by squirrel on transformer in 3900 block of prytania refused xformer ok animal guard installed jdomang | -90.0971 | 29.9236 | 70115 | B | Council District B | Cyndi Nguyen
1291400733 | Yes | EAST ORLEANS | FAIR | 2018-06-09 13:14 | 2018-06-09 14:13 | 2018-06-09 14:10 | 1205 | ENOI | LFUS | 43506-F | 4439250240 | DLIN | 6 | 145 | 8120 | 56 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to work ug transformer burn up switch out lateral to isolate bad transformer cschexn | -97.0758 | 27.9066 | 70129 | E | Council District E | Cyndi Nguyen
1291035305 | Yes | EAST ORLEANS | FAIR | 2018-06-03 17:46 | 2018-06-03 18:29 | 2018-06-03 18:31 | 1610 | ENOI | LFUS | 27522 | 4223449606 | DLIN | 6 | 157 | 7065 | 45 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -97.0758 | 27.9066 | 70126 | E | Council District E | Jared Brossett
1293704523 | Yes | ORLEANS | FAIR | 2018-07-18 00:49 | 2018-07-18 02:23 | 2018-07-18 02:28 | 403 | ENOI | SBKR | 403 | 3847049123 | DLIN | 1 | 163 | 15974 | 98 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Equipment - Primary Conductor | -90.1179 | 30.0121 | 70124 | A | Council District A | Cyndi Nguyen
1292922845 | Yes | ORLEANS | HEAT | 2018-07-05 13:50 | 2018-07-05 18:20 | 2018-07-05 18:25 | 615 | ENOI | LFUS | 65165 | 3984047614 | DLIN | 1 | 184 | 50600 | 275 | HUMAN FACTORS | VHCL | Vehicle | N | Pole being replaced after vehicle hit pole. **emailed PID 7/11/2018** | -90.0751 | 29.9703 | 70119 | D | Council District D | Cyndi Nguyen
1294237214 | Yes | EAST ORLEANS | FAIR | 2018-07-24 04:11 | 2018-07-24 08:16 | 2018-07-24 08:30 | 1603 | ENOI | LFUS | 27320-F | 4235049908 | DLIN | 6 | 192 | 49728 | 259 | EQUIPMENT | EELB | Equipment - Elbow | N |  | -97.0758 | 27.9066 | 70127 | E | Council District E | Kristin Palmer
1291183210 | Yes | ORLEANS | THDR | 2018-06-05 14:50 | 2018-06-05 15:34 | 2018-06-05 15:45 | B0525 | ENOI | SUBN | B0525 | 3788147072 | DLIN | 1 | 208 | 11440 | 55 | LIGHTNING | LGHT | Lightning | N | southport B0510 locked out was reset by substation personal and reenergized with load | -90.1372 | 29.9559 | 70118 | A | Council District A | Jay Banks
1291188000 | Yes | ORLEANS | THDR | 2018-06-05 15:15 | 2018-06-05 17:03 | 2018-06-05 17:17 | 2014 | ENOI | LFUS | 27622 | 3816646701 | DLIN | 1 | 252 | 30744 | 122 | VEGETATION | VOHL | Overhanging Limb | N | removed tree refused line back in confirmed | -90.1281 | 29.9459 | 70118 | A | Council District A | Kristin Palmer
1293706301 | NO | ORLEANS | FAIR | 2018-07-18 03:54 | 2018-07-18 03:55 | 2018-07-18 03:57 | 403 | ENOI | SBKR | 403 | 3847049123 | DLIN | 1 | 301 | 602 | 2 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Equipment - Primary Conductor | -90.1179 | 30.0121 | 70124 | A | Council District A | Cyndi Nguyen
1291385730 | Yes | EAST ORLEANS | FAIR | 2018-06-09 05:57 | 2018-06-09 07:15 | 2018-06-09 07:10 | 1605 | ENOI | SBKR | 1605 | 4350949755 | DLIN | 6 | 302 | 22046 | 73 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | A rat flashed up S&WB cub. at 10451 Lake Forest. Will need to be replaced | -89.9585 | 30.0279 | 70127 | E | Council District E | Jay Banks
1292082920 | Yes | EAST ORLEANS | FAIR | 2018-06-20 16:50 | 2018-06-20 17:31 | 2018-06-20 17:32 | 1002 | ENOI | SBKR | 1002 | 4141549320 | DLIN | 6 | 323 | 13566 | 42 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | two phase got togeather and took out feeder rear of 8001 Downman Rd. Fell into the clear. Sent to Vege Dept. | -90.0248 | 30.0166 | 70126 | D | Council District D | Cyndi Nguyen
1293653276 | Yes | ORLEANS | FAIR | 2018-07-17 10:51 | 2018-07-17 11:37 | 2018-07-17 11:23 | 1712 | ENOI | LFUS | 21825 | 3982547208 | DLIN | 1 | 385 | 12320 | 32 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | refused b phase taken out by pigeon jtatma1 | -90.0757 | 29.9591 | 70112 | C | Council District C | Cyndi Nguyen
1293706091 | Yes | ORLEANS | FAIR | 2018-07-18 00:49 | 2018-07-18 03:58 | 2018-07-18 04:00 | 403 | ENOI | DIS | 14853 | 3949249280 | DLIN | 1 | 385 | 73535 | 191 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Equipment - Primary Conductor | -90.0855 | 30.0161 | 70124 | A | Council District A | Kristin Palmer
1294137089 | NO | ORLEANS CBD | FAIR | 2018-07-22 15:19 | 2018-07-22 16:53 | 2018-07-22 16:46 | NOTRE | ENOI | SUBN | NOTRE | 00000000000 | DSUB | 4 | 437 | 38019 | 87 | OTHER | FOBJ | Foreign Objects - Other | N | Balloons have been found on ground burnt which took out bus on T4 at Notre Dame |  |  | 70130 | B | Council District B | Cyndi Nguyen
1291455802 | NO | EAST ORLEANS | THDR | 2018-06-10 12:36 | 2018-06-10 13:17 | 2018-06-10 13:19 | 2345 | ENOI | TRAN | 2345 | 4214847806 | TLIN | 6 | 448 | 19264 | 43 | OTHER | UNKI | Unknown - Under Investigation | N | Loss of source from Michoud Line to ARABI and Tricou TCCS tried closing DERBNY N9702 but couldnt close substation in route | -90.0022 | 29.9748 | 70117 | E | Council District E | Jay Banks
1294557793 | NO | ORLEANS | FAIR | 2018-07-31 03:46 | 2018-07-31 03:46 | 2018-07-31 03:46 | 2024 | ENOI | SBKR | 2024 | 3847847391 | DLIN | 1 | 520 | 0 | 0 | OTHER | UNKN | Inspected Unknown | N |  | -90.1183 | 29.9645 | 70118 | A | Council District A | Cyndi Nguyen
1292799002 | NO | ORLEANS | FAIR | 2018-07-03 13:10 | 2018-07-03 13:10 | 2018-07-03 13:10 | 2024 | ENOI | SBKR | 2024 | 3847847391 | DLIN | 1 | 529 | 0 | 0 | OTHER | UNKN | Inspected Unknown | N | no cause found | -90.1183 | 29.9645 | 70118 | A | Council District A | Cyndi Nguyen
1293320688 | Yes | ORLEANS | FAIR | 2018-07-11 16:16 | 2018-07-11 16:16 | 2018-07-11 20:54 | 1709 | ENOI | RCLR | 71181 | 4025148173 | DLIN | 1 | 546 | 151788 | 278 | EQUIPMENT | EARM | Equipment - Crossarm | N | WIRE DOWN CREW TO PICKUP | -90.0619 | 29.9855 | 70119 | D | Council District D | Jared Brossett
1292777955 | NO | ORLEANS | THDR | 2018-07-03 05:00 | 2018-07-03 06:52 | 2018-07-03 06:52 | 1911 | ENOI | SUBN | 1911 | 3909145668 | DSUB | 1 | 559 | 62608 | 112 | IMPROPER RELAYING | DEDR | Relay Design Error - Drawing | N | substation was at sub unknow cause; during installation wiring was reversed in A & C phase linear coupler due to incorrect drawings as per P. Cotoya | -90.0995 | 29.9169 | 70115 | B | Council District B | Jared Brossett
1291369713 | Yes | ORLEANS | FAIR | 2018-06-08 19:14 | 2018-06-08 20:03 | 2018-06-08 20:30 | 1712 | ENOI | LFUS | 21825 | 3982547208 | DLIN | 1 | 630 | 47880 | 76 | EQUIPMENT | EPOL | Equipment - Pole | N | Broken pole at location open delta bank pole rotten at base and fell over...svc man cleared and heated lateral back up | -90.0757 | 29.9591 | 70112 | C | Council District C | Joseph Giarrusso
1292858052 | Yes | EAST ORLEANS | FAIR | 2018-07-03 23:37 | 2018-07-04 00:01 | 2018-07-03 23:59 | 1610 | ENOI | RCLR | RCLR | 4243049745 | DLIN | 6 | 647 | 13587 | 21 | OTHER | UNKN | Inspected Unknown | N | closed vfi checked closed found nothing | -97.0758 | 27.9066 | 70127 | E | Council District E | Kristin Palmer
1293083623 | Yes | EAST ORLEANS | FAIR | 2018-07-07 11:31 | 2018-07-07 12:05 | 2018-07-07 12:10 | 612 | ENOI | RCLR | 23282 | 4122747950 | DLIN | 6 | 651 | 25389 | 39 | OTHER | FOTH | Fire - Other (Describe in Remarks Field) | N | recloser wouldn't close & by-passed: Found balloons on primary conductors on Rocheblave St. | -90.0313 | 29.979 | 70117 | D | Council District D | Cyndi Nguyen
1293199589 | Yes | ALGIERS | FAIR | 2018-07-09 13:28 | 2018-07-09 13:36 | 2018-07-09 13:35 | W0723 | ENOI | SBKR | W0723 | 4172545854 | DLIN | 81 | 651 | 4557 | 7 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew fixed broken arm | -90.0163 | 29.9212 | 70114 | C | Council District C | Cyndi Nguyen
1292651741 | Yes | EAST ORLEANS | THDR | 2018-07-01 02:11 | 2018-07-01 03:44 | 2018-07-01 03:59 | 612 | ENOI | RCLR | 23282 | 4122747950 | DLIN | 6 | 652 | 70416 | 108 | LIGHTNING | LGHT | Lightning | N |  | -90.0313 | 29.979 | 70117 | D | Council District D | Joseph Giarrusso
1291784515 | Yes | EAST ORLEANS | HEAT | 2018-06-14 23:09 | 2018-06-14 23:26 | 2018-06-14 23:27 | 1610 | ENOI | VFI | 27120 | 4243049745 | DLIN | 6 | 653 | 11754 | 18 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | local office willl send guy out next week to inspect closer to see why VFI opened (pwd): Need to r/p cub. 230 | -97.0758 | 27.9066 | 70127 | E | Council District E | Cyndi Nguyen
1291786934 | Yes | EAST ORLEANS | FAIR | 2018-06-15 05:18 | 2018-06-15 05:59 | 2018-06-15 06:01 | 1610 | ENOI | VFI | 27120 | 4243049745 | DLIN | 6 | 653 | 27426 | 42 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | crew will check later: Need to r/p cub. 230 | -97.0758 | 27.9066 | 70127 | E | Council District E | Cyndi Nguyen
1291825874 | Yes | EAST ORLEANS | RAIN | 2018-06-16 02:42 | 2018-06-16 03:24 | 2018-06-16 03:25 | 1610 | ENOI | VFI | 27120 | 4243049745 | DLIN | 6 | 653 | 28079 | 43 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | VFI 248 had an A & C phase target, Serviceman was able to close and it held. While need follow up vault inspections. Need to r/p cub. 230 | -97.0758 | 27.9066 | 70127 | E | Council District E | Cyndi Nguyen
1292785204 | Yes | ORLEANS | FAIR | 2018-07-03 07:48 | 2018-07-03 09:59 | 2018-07-03 10:04 | 2147 | ENOI | DIS | 24394 | 3954846024 | DLIN | 1 | 657 | 89352 | 136 | EQUIPMENT | EARM | Equipment - Crossarm | N | wire down due to crossarm | -90.0849 | 29.9267 | 70115 | B | Council District B | Cyndi Nguyen
1293757752 | Yes | ORLEANS | THDR | 2018-07-18 18:59 | 2018-07-18 21:24 | 2018-07-18 21:24 | 1709 | ENOI | RCLR | 23983 | 3992848155 | DLIN | 1 | 702 | 101790 | 145 | CONDUCTOR | EOSC | Equipment - Shield Conductor | N | sheild wire down at abundance and paris | -90.0721 | 29.985 | 70119 | D | Council District D | Jay Banks
1292443239 | NO | EAST ORLEANS | THDR | 2018-06-27 14:15 | 2018-06-27 14:15 | 2018-06-27 14:15 | 1204 | ENOI | SBKR | 1204 | 4544950180 | DLIN | 6 | 706 | 0 | 0 | EQUIPMENT | EARM | Equipment - Crossarm | N | baad weather, back on: Found broken braces at pole # 358 on Hwy 90 up of Bayou Savage | -89.897 | 30.039 | 70129 | E | Council District E | Joseph Giarrusso
1291268556 | Yes | EAST ORLEANS | FAIR | 2018-06-07 02:40 | 2018-06-07 03:53 | 2018-06-07 03:54 | 617 | ENOI | SBKR | 617 | 4081048420 | DLIN | 6 | 714 | 52122 | 73 | EQUIPMENT | EARR | Equipment - Arrestor | N | Equipment - Arrestor , IT CLEARD ITS SELF | -90.0442 | 29.9921 | 70126 | D | Council District D | Joseph Giarrusso
1291455740 | NO | EAST ORLEANS | THDR | 2018-06-10 12:36 | 2018-06-10 13:19 | 2018-06-10 13:19 | 2325 | ENOI | TRAN | 2325 | 4214447800 | TLIN | 6 | 723 | 31089 | 43 | OTHER | UNKI | Unknown - Under Investigation | N | Loss of source from Michoud Line to ARABI and Tricou TCCS tried closing DERBNY N9702 but couldnt close substation in route | -90.0023 | 29.9746 | 70117 | E | Council District E | Cyndi Nguyen
1294426621 | NO | ORLEANS | THDR | 2018-07-28 21:17 | 2018-07-28 21:31 | 2018-07-28 21:19 | 406 | ENOI | SBKR | 406 | 3846949118 | DLIN | 1 | 732 | 732 | 1 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Breaker dropped to allow serviceman to open switch to isolate wire that is down | -90.1179 | 30.012 | 70124 | A | Council District A | Jared Brossett
1293732321 | Yes | EAST ORLEANS | FAIR | 2018-07-18 14:52 | 2018-07-18 15:04 | 2018-07-18 15:00 | 1612 | ENOI | SBKR | 1612 | 4351149759 | DLIN | 6 | 738 | 5904 | 8 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | push brace broke loose and shook pole. pole broke under water and was uncontrollable | -89.9584 | 30.028 | 70127 | E | Council District E | Jay Banks
1291183346 | Yes | ORLEANS | THDR | 2018-06-05 14:50 | 2018-06-05 15:45 | 2018-06-05 15:36 | B0526 | ENOI | SUBN | B0526 | 3788047074 | DLIN | 1 | 758 | 34868 | 46 | LIGHTNING | LGHT | Lightning | N | master breaker b0510 locked out reset master reenergized breakers | -90.1372 | 29.9559 | 70118 | A | Council District A | Cyndi Nguyen
1292776754 | NO | ORLEANS | THDR | 2018-07-03 05:00 | 2018-07-03 06:47 | 2018-07-03 06:51 | 1912 | ENOI | SUBN | 1912 | 3909245668 | DSUB | 1 | 791 | 87801 | 111 | IMPROPER RELAYING | DEDR | Relay Design Error - Drawing | N | substation was at sub unknow cause; during installation wiring was reversed in A & C phase linear coupler due to incorrect drawings as per P. Cotoya | -90.0994 | 29.9169 | 70115 | B | Council District B | Joseph Giarrusso
1292690844 | Yes | ORLEANS | FAIR | 2018-07-01 22:44 | 2018-07-02 03:41 | 2018-07-02 03:44 | 1915 | ENOI | DIS | 25407 | 3939446607 | DLIN | 1 | 912 | 143856 | 300 | EQUIPMENT | EARM | Equipment - Crossarm | N | wire down | -90.0897 | 29.9427 | 70113 | B | Council District B | Jay Banks
1291254097 | Yes | ALGIERS | FAIR | 2018-06-06 17:17 | 2018-06-06 18:37 | 2018-06-06 18:44 | W0118 | ENOI | DIS | 5015 | 4060746101 | DLIN | 81 | 936 | 82368 | 87 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | Equipment - Fuse Switch a phase switch burning up | -90.0514 | 29.9283 | 70053 | C | Council District C | Jay Banks
1292380772 | Yes | ORLEANS | HEAT | 2018-06-25 18:07 | 2018-06-25 19:00 | 2018-06-25 19:01 | 1926 | ENOI | SBKR | 1926 | 3909945674 | DLIN | 1 | 980 | 52920 | 54 | EQUIPMENT | EARM | Equipment - Crossarm | N | Crossarm broke at 2300 Joseph St. Opened sw. 23137 and closed breaker.: Part of Loop Scheme | -90.0992 | 29.9171 | 70115 | B | Council District B | Jay Banks
1293103923 | Yes | ORLEANS | FAIR | 2018-07-07 17:26 | 2018-07-07 18:14 | 2018-07-07 18:15 | B0527 | ENOI | RCLR | 25151 | 3809746857 | DLIN | 1 | 997 | 48853 | 49 | ANIMAL | ASQL | Animal - Squirrel | N | Animal - Squirrel | -90.1304 | 29.9498 | 70118 | A | Council District A | Jay Banks
1292649450 | Yes | EAST ORLEANS | THDR | 2018-06-30 22:59 | 2018-07-01 02:09 | 2018-07-01 02:01 | 612 | ENOI | DIS | 23414 | 4129547995 | DLIN | 6 | 997 | 181454 | 182 | LIGHTNING | LGHT | Lightning | N |  | -90.0292 | 29.9803 | 70117 | D | Council District D | Jay Banks
1293083180 | NO | EAST ORLEANS | FAIR | 2018-07-07 11:27 | 2018-07-07 11:31 | 2018-07-07 11:31 | 612 | ENOI | SBKR | 612 | 4081648420 | DLIN | 6 | 1026 | 4104 | 4 | OTHER | FOTH | Fire - Other (Describe in Remarks Field) | N | Serviceman found balloons in primary conductors on Rocheblave St | -90.0441 | 29.9921 | 70126 | D | Council District D | Jay Banks
1293506877 | NO | EAST ORLEANS | THDR | 2018-07-15 15:54 | 2018-07-15 16:03 | 2018-07-15 15:56 | 612 | ENOI | SBKR | 612 | 4081648420 | DLIN | 6 | 1026 | 2052 | 2 | LIGHTNING | LGHT | Lightning | N |  | -90.0441 | 29.9921 | 70126 | D | Council District D | Jay Banks
1293182072 | NO | EAST ORLEANS | FAIR | 2018-07-09 08:43 | 2018-07-09 08:48 | 2018-07-09 08:48 | 1610 | ENOI | SBKR | 1610 | 4351549759 | DLIN | 6 | 1032 | 5160 | 5 | OTHER | FOBJ | Foreign Objects - Other | N | bkr op while operating switch27271 of dsr 43799 | -89.9583 | 30.028 | 70127 | E | Council District E | Jay Banks
1292658149 | Yes | EAST ORLEANS | FAIR | 2018-07-01 07:27 | 2018-07-01 09:01 | 2018-07-01 08:41 | 2216 | ENOI | VFI | 37194 | 4282450286 | DLIN | 6 | 1046 | 77404 | 74 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | N/O switch was closed in cub. 224 leaving 2 feeders tied, when cable failed it took out VFI. | -97.0758 | 27.9066 | 70127 | E | Council District E | Jared Brossett
1292642065 | Yes | EAST ORLEANS | THDR | 2018-06-30 22:59 | 2018-07-01 01:52 | 2018-07-01 01:24 | 612 | ENOI | SBKR | 612 | 4081648420 | DLIN | 6 | 1050 | 152250 | 145 | LIGHTNING | LGHT | Lightning | N |  | -90.0441 | 29.9921 | 70126 | D | Council District D | Cyndi Nguyen
1294428381 | NO | EAST ORLEANS | THDR | 2018-07-28 21:54 | 2018-07-28 21:54 | 2018-07-28 21:54 | 2223 | ENOI | SBKR | 2223 | 4334850767 | DLIN | 6 | 1168 | 0 | 0 | OTHER | TFLT | Transient Fault | N | crew operated feeder shooting underground lateral 25974 | -89.9632 | 30.0558 | 70128 | E | Council District E | Jared Brossett
1294477592 | Yes | ORLEANS | FAIR | 2018-07-29 16:04 | 2018-07-29 17:46 | 2018-07-29 17:46 | 1554 | ENOI | SBKR | 1554 | 3950446990 | DLIN | 1 | 1401 | 142902 | 102 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Burnt jump outside of station | -90.086 | 29.9532 | 70113 | B | Council District B | Jay Banks
1292023560 | NO | EAST ORLEANS | THDR | 2018-06-19 13:42 | 2018-06-19 13:42 | 2018-06-19 13:42 | 503 | ENOI | SBKR | 503 | 4075049220 | DLIN | 6 | 1410 | 0 | 0 | OTHER | TFLT | Transient Fault | N | Circuit operated twice earlier, Patroling now.....................PC | -90.0458 | 30.0141 | 70126 | D | Council District D | Jay Banks
1292024851 | NO | EAST ORLEANS | THDR | 2018-06-19 14:13 | 2018-06-19 14:13 | 2018-06-19 14:13 | 503 | ENOI | SBKR | 503 | 4075049220 | DLIN | 6 | 1410 | 0 | 0 | OTHER | TFLT | Transient Fault | N | Circuit operation of a few seconds only................PC | -90.0458 | 30.0141 | 70126 | D | Council District D | Joseph Giarrusso
1291455808 | NO | EAST ORLEANS | THDR | 2018-06-10 12:36 | 2018-06-10 13:17 | 2018-06-10 13:19 | 2347 | ENOI | TRAN | 2347 | 4215247804 | TLIN | 6 | 1420 | 61060 | 43 | OTHER | UNKI | Unknown - Under Investigation | N | Loss of source from Michoud Line to ARABI and Tricou TCCS tried closing DERBNY N9702 but couldnt close substation in route | -90.0021 | 29.9747 | 70117 | E | Council District E | Kristin Palmer
1292689552 | Yes | ORLEANS | FAIR | 2018-07-01 22:44 | 2018-07-01 23:40 | 2018-07-01 23:31 | 1915 | ENOI | SBKR | 1915 | 3909745669 | DLIN | 1 | 1423 | 66881 | 47 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.0993 | 29.9169 | 70115 | B | Council District B | Cyndi Nguyen
1292712397 | Yes | ORLEANS | FAIR | 2018-07-02 12:59 | 2018-07-02 16:03 | 2018-07-02 16:05 | 2013 | ENOI | DIS | 25604 | 3825946639 | DLIN | 1 | 1440 | 266400 | 185 | EQUIPMENT | EABS | Equipment - Air Break / Disconnect Switch | N | disconnected and jumpers burned up on c phase | -90.1255 | 29.9438 | 70118 | A | Council District A | Joseph Giarrusso
1294136339 | NO | ORLEANS CBD | FAIR | 2018-07-22 15:13 | 2018-07-22 16:46 | 2018-07-22 16:46 | 1844 | ENOI | SUBN | NOTRE | 00000000000 | DSUB | 4 | 1505 | 139965 | 93 | OTHER | FOBJ | Foreign Objects - Other | N | Balloons have been found on ground burnt which took out bus on T4 at Notre Dame |  |  | 70130 | B | Council District B | Jared Brossett
1292654961 | NO | EAST ORLEANS | FAIR | 2018-07-01 06:25 | 2018-07-01 06:25 | 2018-07-01 06:26 | 2211 | ENOI | SBKR | 2211 | 4334750769 | DLIN | 6 | 1542 | 1542 | 1 | OTHER | TFLT | Transient Fault | N |  | -89.9632 | 30.0558 | 70128 | E | Council District E | Kristin Palmer
1292776867 | NO | ORLEANS | THDR | 2018-07-03 05:00 | 2018-07-03 07:01 | 2018-07-03 07:03 | 1913 | ENOI | SUBN | 1913 | 3909445669 | DSUB | 1 | 1590 | 195570 | 123 | IMPROPER RELAYING | DEDR | Relay Design Error - Drawing | N | substation was at sub unknow cause; during installation wiring was reversed in A & C phase linear coupler due to incorrect drawings as per P. Cotoya | -90.0994 | 29.9169 | 70115 | B | Council District B | Kristin Palmer
1291135469 | NO | ORLEANS | FAIR | 2018-06-05 05:46 | 2018-06-05 05:51 | 2018-06-05 05:51 | 1712 | ENOI | SBKR | 1712 | 4023848726 | DLIN | 1 | 1592 | 7960 | 5 | OTHER | UNKN | Inspected Unknown | N | notified substation to check relay on 1712 breaker was NOT on nonauto and locked out on ONE trip | -90.0622 | 30.0007 | 70122 | D | Council District D | Kristin Palmer
1292863428 | NO | ORLEANS | FAIR | 2018-07-04 05:48 | 2018-07-04 05:48 | 2018-07-04 05:48 | 1712 | ENOI | SBKR | 1712 | 4023848726 | DLIN | 1 | 1594 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N | Circuit operated one time , serviceman advised | -90.0622 | 30.0007 | 70122 | D | Council District D | Jared Brossett
1292776748 | NO | ORLEANS | THDR | 2018-07-03 05:00 | 2018-07-03 07:02 | 2018-07-03 06:43 | 1914 | ENOI | SUBN | 1914 | 3909545669 | DSUB | 1 | 1619 | 166757 | 103 | IMPROPER RELAYING | DEDR | Relay Design Error - Drawing | N | substation was at sub unknow cause; during installation wiring was reversed in A & C phase linear coupler due to incorrect drawings as per P. Cotoya | -90.0993 | 29.9169 | 70115 | B | Council District B | Joseph Giarrusso
1292657804 | Yes | EAST ORLEANS | FAIR | 2018-07-01 07:25 | 2018-07-01 08:40 | 2018-07-01 08:41 | 2211 | ENOI | SBKR | 2211 | 4334750769 | DLIN | 6 | 1625 | 155660 | 76 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Bad cable between Cub. 213 and Cub. 224 bay #4. Cable iscolated and switched around. | -89.9632 | 30.0558 | 70128 | E | Council District E | Kristin Palmer
1294238140 | NO | ORLEANS | FAIR | 2018-07-24 06:01 | 2018-07-24 06:01 | 2018-07-24 06:01 | 1712 | ENOI | SBKR | 1712 | 4023848726 | DLIN | 1 | 1637 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N |  | -90.0622 | 30.0007 | 70122 | D | Council District D | Kristin Palmer
1294319219 | NO | ORLEANS | FAIR | 2018-07-26 14:36 | 2018-07-26 14:36 | 2018-07-26 14:36 | 1712 | ENOI | SBKR | 1712 | 4023848726 | DLIN | 1 | 1643 | 0 | 0 | ANIMAL | RBRD | Animal - Bird Reportable Incident (Mortality or Injury) | N | Non-reportable black birds contacted primary & stell x-arm on Claiborne, St. Philip to Ursuline (side of off ramp) | -90.0622 | 30.0007 | 70122 | D | Council District D | Cyndi Nguyen
1292776781 | NO | ORLEANS | THDR | 2018-07-03 05:00 | 2018-07-03 06:42 | 2018-07-03 06:40 | 1917 | ENOI | SUBN | 1917 | 3910145669 | DSUB | 1 | 1643 | 164300 | 100 | IMPROPER RELAYING | DEDR | Relay Design Error - Drawing | N | substation was at sub unknow cause; during installation wiring was reversed in A & C phase linear coupler due to incorrect drawings as per P. Cotoya | -90.0992 | 29.917 | 70115 | B | Council District B | Jared Brossett
1292779754 | NO | ORLEANS | FAIR | 2018-07-03 05:44 | 2018-07-03 05:44 | 2018-07-03 05:44 | 1923 | ENOI | SUBN | 1923 | 3909345674 | DSUB | 1 | 1689 | 0 | 0 | OTHER | UNKN | Inspected Unknown | N | Inspected Unknown | -90.0994 | 29.9171 | 70115 | B | Council District B | Jared Brossett
1293166837 | NO | EAST ORLEANS | FAIR | 2018-07-09 07:21 | 2018-07-09 07:21 | 2018-07-09 07:22 | 613 | ENOI | SBKR | 613 | 4081548420 | DLIN | 6 | 1731 | 0 | 0 | EQUIPMENT | EARR | Equipment - Arrestor | N | arrestor flash near sw.71697 | -90.0441 | 29.9921 | 70126 | D | Council District D | Cyndi Nguyen
1292780054 | Yes | ORLEANS | FAIR | 2018-07-03 05:46 | 2018-07-03 07:35 | 2018-07-03 07:36 | 2146 | ENOI | SBKR | 2146 | 4012946121 | DLIN | 1 | 1854 | 202086 | 109 | EQUIPMENT | EARM | Equipment - Crossarm | N | broke crossarm and wire down | -90.0665 | 29.9291 | 70130 | B | Council District B | Cyndi Nguyen
1292776689 | NO | ORLEANS | THDR | 2018-07-03 05:00 | 2018-07-03 07:05 | 2018-07-03 06:55 | 1916 | ENOI | SUBN | 1916 | 3909845669 | DSUB | 1 | 1993 | 229195 | 115 | IMPROPER RELAYING | DEDR | Relay Design Error - Drawing | N | substation was at sub unknow cause; during installation wiring was reversed in A & C phase linear coupler due to incorrect drawings as per P. Cotoya | -90.0993 | 29.9169 | 70115 | B | Council District B | Cyndi Nguyen
1292442339 | NO | ALGIERS | HEAT | 2018-06-27 14:03 | 2018-06-27 14:03 | 2018-06-27 14:03 | W0713 | ENOI | SBKR | W0713 | 4173945845 | DLIN | 81 | 2037 | 0 | 0 | HUMAN FACTORS | VHCL | Vehicle | N | tractor hit guy wire operated breaker | -90.0158 | 29.921 | 70114 | C | Council District C | Jay Banks
1291455763 | NO | EAST ORLEANS | THDR | 2018-06-10 12:36 | 2018-06-10 13:18 | 2018-06-10 13:19 | 2346 | ENOI | TRAN | 2346 | 4215047805 | TLIN | 6 | 2118 | 91074 | 43 | OTHER | UNKI | Unknown - Under Investigation | N | Loss of source from Michoud Line to ARABI and Tricou TCCS tried closing DERBNY N9702 but couldnt close substation in route | -90.0021 | 29.9747 | 70117 | E | Council District E | Cyndi Nguyen
1293185289 | Yes | EAST ORLEANS | FAIR | 2018-07-09 07:29 | 2018-07-09 09:03 | 2018-07-09 09:01 | 615 | ENOI | DIS | 55999 | 4054948382 | DLIN | 6 | 2293 | 210956 | 92 | EQUIPMENT | EARR | Equipment - Arrestor | N | Crew found bad arrestor near switch 71697 | -90.0524 | 29.9912 | 70122 | D | Council District D | Jay Banks
1292549333 | Yes | ORLEANS | FAIR | 2018-06-29 08:18 | 2018-06-29 08:56 | 2018-06-29 08:50 | 1915 | ENOI | SBKR | 1915 | 3909745669 | DLIN | 1 | 2332 | 74624 | 32 | OTHER | FOBJ | Foreign Objects - Other | N | Balloons got into phases burning wire down. Crew is enroute to repair. | -90.0993 | 29.9169 | 70115 | B | Council District B | Cyndi Nguyen
1292776877 | NO | ORLEANS | THDR | 2018-07-03 05:00 | 2018-07-03 07:03 | 2018-07-03 07:02 | 1915 | ENOI | SUBN | 1915 | 3909745669 | DSUB | 1 | 2335 | 284870 | 122 | IMPROPER RELAYING | DEDR | Relay Design Error - Drawing | N | substation was at sub unknow cause; during installation wiring was reversed in A & C phase linear coupler due to incorrect drawings as per P. Cotoya | -90.0993 | 29.9169 | 70115 | B | Council District B | Cyndi Nguyen
1293166887 | NO | EAST ORLEANS | FAIR | 2018-07-09 07:21 | 2018-07-09 07:21 | 2018-07-09 07:22 | 614 | ENOI | SBKR | 614 | 4081448420 | DLIN | 6 | 2344 | 0 | 0 | EQUIPMENT | EARR | Equipment - Arrestor | N | arrestor flash near sw.71697 | -90.0441 | 29.9921 | 70126 | D | Council District D | Cyndi Nguyen
1292447584 | Yes | EAST ORLEANS | FAIR | 2018-06-27 15:36 | 2018-06-27 16:43 | 2018-06-27 16:44 | 2212 | ENOI | SBKR | 2212 | 4334650770 | DLIN | 6 | 2533 | 172244 | 68 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | phase fell, locked feeder out, crew picked back up, back on | -89.9632 | 30.0559 | 70128 | E | Council District E | Cyndi Nguyen
1292587872 | NO | ORLEANS | THDR | 2018-06-29 17:40 | 2018-06-29 17:40 | 2018-06-29 17:41 | 2135 | ENOI | SBKR | 2135 | 4013546137 | DLIN | 1 | 2683 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N |  | -90.0664 | 29.9295 | 70130 | B | Council District B | Jared Brossett
1293467083 | Yes | ORLEANS | FAIR | 2018-07-14 09:31 | 2018-07-14 09:40 | 2018-07-14 09:37 | 2132 | ENOI | SBKR | 2132 | 4013446133 | DLIN | 1 | 2791 | 16746 | 6 | HUMAN FACTORS | HCDC | Contractor - Distribution Line (Describe in remarks) | N | Shield conductor came out of grip while contractors were moving it | -90.0664 | 29.9294 | 70130 | B | Council District B | Jared Brossett
1291594673 | NO | ALGIERS | THDR | 2018-06-12 16:19 | 2018-06-12 16:19 | 2018-06-12 16:20 | W1712 | ENOI | SBKR | W1712 | 4284045926 | DLIN | 81 | 2807 | 0 | 0 | LIGHTNING | LGHT | Lightning | N |  | -89.981 | 29.9228 | 70131 | C | Council District C | Cyndi Nguyen
1291950308 | NO | ORLEANS | THDR | 2018-06-18 13:14 | 2018-06-18 13:18 | 2018-06-18 13:18 | 2013 | ENOI | SBKR | 2013 | 3847347389 | DLIN | 1 | 3276 | 16380 | 5 | VEGETATION | VOHL | Overhanging Limb | N | TREE HAS FALLEN ON FEEDER HAD TO DROP TO REMOVE TREE | -90.1184 | 29.9644 | 70118 | A | Council District A | Jay Banks