## CI Cause Category Details
Row Labels | Sum of CI
Animal | 12961
Animal - Bird Reportable Inc (Mortality or Injury) | 9868
Animal - Other (Describe in Remarks Field) | 1407
Animal - Squirrel | 1686
Equipment Failure | 126160 | 165799 | Distribution CI's (chart 1 of deck)
Breaker - Oil | 14353 | 44565 | Scheduled Interruption & Emergency Switching CI's (chart 4 of deck)
Cable Failure in manhole | 30 | 53868 | Transmission CI's (chart 9 of deck)
Equipment Failure - Air Break / Disconnect Switch | 89 | 264232 | Total CI's reported January - October 2020
Equipment Failure - Arrestor | 3541
Equipment Failure - Automatic Sleeve | 1168
Equipment Failure - Capacitor | 1691
Equipment Failure - Connector / Sleeve | 233
Equipment Failure - Connector Sleeve | 9721
Equipment Failure - Crossarm | 21127
Equipment Failure - Elbow | 1579
Equipment Failure - Fuse Link | 2359
Equipment Failure - Fuse Switch | 1571
Equipment Failure - Insulator | 2132
Equipment Failure - Metering | 21
Equipment Failure - Neutral / Shield Conductor | 18
Equipment Failure - Other (Describe in Remarks Fie | 1138
Equipment Failure - Pole | 3116
Equipment Failure - Primary Conductor | 18879
Equipment Failure - Shield Conductor | 7351
Equipment Failure - Transformer | 3157
Secondary/Service Conductor | 335
Slack Conductor / Loose Connection | 2329
Substation Bushing - Breaker | 7169
Switching Cabinet | 2741
Transformer Splicing chamber failure | 3
Cable Failure in duct | 96
Secondary cable failure | 1
Equipment Failure - Electronic Recloser | 1419
Equipment Failure - Recloser / Sectionalizer | 352
Control Cable Failure | 2787
Equipment Failure - Neutral Conductor | 79
Potential/Voltage Transformer | 13459
Substation Equipment Other (Describe in remarks) | 2116
Foreign Trouble | 3550
Foreign Trouble - Neighboring Utility | 3550
Human Error | 1834
Company - Distribution Business (Describe in remar | 37
Entergy Distribution Contractor (Describe in rema | 134
Human Error - Company (Describe in Remarks Field) | 17
Improper Design (Describe in Remarks Field) | 1574
Mis-Coordination (Describe in remarks) | 72
Lightning | 15032
Lightning | 15032
Other | 62509
Corrosion | 35
Emergency Switching | 30542
Fire - Other (Describe in Remarks Field) | 167
Foreign Objects (Describe in Remarks Field) | 17355
Inspected Unknown | 4267
Meter Exchange | 15
Unknown - Under Investigation | 4376
Storm | 5752
Public Damage | 15067
Human Error - Non-Entergy Workers (Describe in Rem | 3243
Malicious Damage | 754
Vehicle | 11070
Scheduled Interruption | 14023
Scheduled Interruption | 14023
Vegetation | 13096
Overhanging Limb | 2449
Tree On Line Outside R.O.W | 1736
Tree/Limb Growing Inside R.O.W. | 5010
Vine Growing into Line | 3901
Grand Total | 264232

## CI by District & Weather
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
Sum of CI
DISTRICT NAME | WEATHER_CONDITION | Summary Cause Updated | CAUSE_DESC | MONTH | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 36306 | 13.74%
Council District B | [9 empty] | 97445 | 36.88%
Council District C | [9 empty] | 7504 | 2.84%
Council District D | [9 empty] | 77223 | 29.23%
Council District E | [9 empty] | 45754 | 17.32%
Grand Total | [9 empty] | 264232 | 100%

## CI by District & Zip Code
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
Sum of CI
DISTRICT NAME | ZIP | Summary Cause Updated | CAUSE_DESC | MONTH | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 36306 | 13.74%
Council District B | [9 empty] | 97445 | 36.88%
Council District C | [9 empty] | 7504 | 2.84%
Council District D | [9 empty] | 77223 | 29.23%
Council District E | [9 empty] | 45754 | 17.32%
Grand Total | [9 empty] | 264232 | 100%

## data
'Date Table'[Year] | CI | CASE_ID | In_NOCC_Reporting | NETWORK_NAME | WEATHER_CONDITION | TOTAL_DURATION_MINUTES | FIRST_CALL_DATE_TIME | LAST_CALL_DATE_TIME | TROUBLE_CLEAR_TIME | ACTUAL_CUSTOMER_MINUTES | DEVICE_TYPE | DEVICE_ID | DISTRIBUTION_LOCATION_NBR | FEEDER_ID | Fdr_Owner | LOCAL_OFFICE_NBR | TOTAL_CUSTOMERS_AFFECTED | CAUSE | CAUSE_DESC | MAJOR_EVENT | REMARKS | LONGITUDE | LATITUDE | SUMMARY_CAUSE | DEVICE_TYPE_DESC | Summary Cause Updated | FIRST_CALL_DATE | System_ | DISTRICT | DISTRICT NAME | REPNAME | ZIP | MONTH
2020 | 2 | 1321608611 | Yes | ORLEANS CBD | FAIR | 80 | 2020-01-01 05:16 | 2020-01-01 05:31 | 2020-01-01 06:35 | 160 | SBKR | 1822 | 4015446698 | 1822 | ENOI | 4 | 2 | EPRI | Equipment Failure - Primary Conductor | N | failure in manhole 6-1460; bad splice on b phase: The 2 cust. were restored manuelly at 6;35 AM Fder was restored 1/2/20 4:08 AM: The 3rd cust was a mis-match | -90.0656 | 29.9449 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-01-01 | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 224 | 1321627546 | Yes | ORLEANS | FAIR | 355 | 2020-01-01 17:36 | 2020-01-01 23:06 | 2020-01-01 23:31 | 79520 | LFUS | 28059 | 3928646516 | 1915 | ENOI | 1 | 224 | VHCL | Vehicle | N | car hit pole; 5 broke poles and wire down | -90.0929 | 29.9402 | Public Damage | Line Fuse | Public Damage | 2020-01-01 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 14 | 1321631146 | Yes | ORLEANS | FAIR | 904 | 2020-01-01 17:36 | 2020-01-01 21:51 | 2020-01-02 08:40 | 12656 | OPEN | 3917946550 | 3917946550 | 1915 | ENOI | 1 | 14 | VHCL | Vehicle | N | car hit pole; 5 broke poles and wire down, PID chg to NO, related to #1321627546 (DGault) | -90.0964 | 29.9411 | Public Damage | Open | Public Damage | 2020-01-01 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 1 | 1321637104 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-02 07:10 | 2020-01-02 07:10 | 2020-01-02 08:30 | 80 | TFUS | 1223486 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | vines grew into terminal pole toook out a phase cleared vines refused barrrel and got lights cback on and tested voltage lights cam eback on dwillin | -90.0377 | 30.0062 | Vegetation | Transformer Fuse | Vegetation | 2020-01-02 | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 23 | 1321643125 | Yes | ORLEANS | THDR | 89 | 2020-01-02 09:42 | 2020-01-02 09:42 | 2020-01-02 11:11 | 2047 | LFUS | 27621 | 3858046356 | 1926 | ENOI | 1 | 23 | VOHL | Overhanging Limb | N | Crew on site picking up down primary | -90.1153 | 29.936 | Vegetation | Line Fuse | Vegetation | 2020-01-02 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 1
2020 | 8 | 1321649001 | Yes | EAST ORLEANS | THDR | 125 | 2020-01-02 11:15 | 2020-01-02 11:27 | 2020-01-02 13:20 | 1000 | TFUS | 1137669 | 41102491707 | 501 | ENOI | 6 | 8 | EPRI | Equipment Failure - Primary Conductor | N | Crew on the way to repair burned up riser | -90.0348 | 30.0126 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-02 | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 13 | 1321665957 | Yes | EAST ORLEANS | RAIN | 81 | 2020-01-02 19:23 | 2020-01-02 20:40 | 2020-01-02 20:44 | 1053 | TFUS | 1205818 | 40891475703 | 622 | ENOI | 6 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.042 | 29.9687 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-02 | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 6 | 1321686189 | Yes | EAST ORLEANS | FAIR | 97 | 2020-01-03 07:43 | 2020-01-03 07:47 | 2020-01-03 09:20 | 582 | XFMR | 1373368 | 43960512098 | 2217 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N | bad transformer | -89.9437 | 30.0677 | Equipment Failure | Transformer | Equipment Failure | 2020-01-03 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 1 | 1321689819 | Yes | ORLEANS | RAIN | 36 | 2020-01-03 08:21 | 2020-01-03 08:21 | 2020-01-03 08:57 | 36 | SERV | SERVICE | 38483463662 | 2024 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | changed conector at pole voltage check good gkathma | -90.1185 | 29.9362 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-03 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 44 | 1321707115 | Yes | EAST ORLEANS | FAIR | 310 | 2020-01-03 16:41 | 2020-01-03 18:05 | 2020-01-03 21:51 | 13640 | LFUS | 27215 | 4204249890 | 2211 | ENOI | 6 | 44 | EPRI | Equipment Failure - Primary Conductor | N | crew to repair | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-03 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 1 | 1321713956 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-03 21:29 | 2020-01-03 21:29 | 2020-01-03 22:49 | 80 | SERV | SERVICE | 42029493934 | 1607 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed **TFUS 1315127 8 to SERV 1315127 8** --- sec conect..repaired tbrock | -90.0053 | 30.0185 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-03 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 1 | 1321722737 | Yes | ORLEANS | FAIR | 40 | 2020-01-04 12:02 | 2020-01-04 12:02 | 2020-01-04 12:42 | 40 | SERV | SERVICE | 40316487839 | 1701 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Changed **TFUS 58867 5 to SERV 58867 5** --- hot leg burnt at pole dcain2 | -90.0596 | 30.0022 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-04 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 347 | 1321742427 | Yes | EAST ORLEANS | FAIR | 99 | 2020-01-05 10:46 | 2020-01-05 11:56 | 2020-01-05 12:25 | 34353 | VFI | 38268 | 4264649768 | 1602 | ENOI | 6 | 347 | EFLK | Equipment Failure - Fuse Link | N | fault behind lateral 73441 | -89.9934 | 30.0265 | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | 2020-01-05 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 851 | 1321740753 | Yes | EAST ORLEANS | FAIR | 70 | 2020-01-05 10:46 | 2020-01-05 13:26 | 2020-01-05 11:56 | 59570 | SBKR | 1602 | 4351549756 | 1602 | ENOI | 6 | 851 | ESWC | Switching Cabinet | N | opened in vfi 531 opened switch 38268 serviceman to ride remainng customer sout Cub, # 554 flashover Okay Temp | -89.9583 | 30.0279 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-01-05 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 36 | 1321744962 | Yes | EAST ORLEANS | FAIR | 34 | 2020-01-05 14:26 | 2020-01-05 14:39 | 2020-01-05 15:00 | 1224 | LFUS | 62597 | 4159649935 | 2212 | ENOI | 6 | 36 | ASQL | Animal - Squirrel | N | squirrel took out over head portion thata casuse outage for underground dwillin | -90.0189 | 30.0333 | Animal | Line Fuse | Animal | 2020-01-05 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 1 | 1321749621 | Yes | ORLEANS | COLD | 142 | 2020-01-05 21:49 | 2020-01-05 21:49 | 2020-01-06 00:11 | 142 | SERV | SERVICE | 38103461220 | 2013 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed **TFUS 549754 * 10 to SERV 549754 * 10** --- bad connection at weather head abengst | -90.1306 | 29.9298 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 16 | 1321759209 | Yes | EAST ORLEANS | FAIR | 105 | 2020-01-06 09:27 | 2020-01-06 09:27 | 2020-01-06 11:12 | 1680 | TFUS | 569328 | 40728487726 | 1702 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N | Crew On Site Working | -90.0467 | 30.0019 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 77 | 1321760883 | Yes | ORLEANS | FAIR | 47 | 2020-01-06 09:38 | 2020-01-06 09:47 | 2020-01-06 10:25 | 3619 | LFUS | 33980 | 3956946513 | 2132 | ENOI | 1 | 77 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons let go by cust. removed balloons and refused lfus. dsmit36 | -89.9849 | 30.033 | Other | Line Fuse | Other | 2020-01-06 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 841 | 1321761982 | Yes | EAST ORLEANS | FAIR | 19 | 2020-01-06 09:45 | 2020-01-06 10:18 | 2020-01-06 10:04 | 15979 | SBKR | 1602 | 4351549756 | 1602 | ENOI | 6 | 841 | ESWC | Switching Cabinet | N | Fault in CUB 554 caused outage | -89.9583 | 30.0279 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-01-06 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 126 | 1321765323 | Yes | EAST ORLEANS | FAIR | 161 | 2020-01-06 09:45 | 2020-01-06 13:08 | 2020-01-06 12:26 | 14154 | SWIT | 25111 | 4246449716 | 1602 | ENOI | 6 | 126 | ESWC | Switching Cabinet | N | Crew replacing bad switching cabinet | -97.0758 | 27.9066 | Equipment Failure | Switch | Equipment Failure | 2020-01-06 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 25 | 1321769814 | Yes | EAST ORLEANS | FAIR | 128 | 2020-01-06 13:42 | 2020-01-06 15:31 | 2020-01-06 15:50 | 3200 | LFUS | 25370 | 4385351220 | 2217 | ENOI | 6 | 25 | EPRI | Equipment Failure - Primary Conductor | N | Switched out bad cable between V-24 to TP 25370 | -89.9472 | 30.0681 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-06 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 26 | 1321808505 | Yes | ORLEANS | FAIR | 110 | 2020-01-07 15:43 | 2020-01-07 17:34 | 2020-01-07 17:34 | 2860 | LFUS | 37703 | 3947445909 | 2147 | ENOI | 1 | 26 | ASQL | Animal - Squirrel | N | got across lateral and blew 2 phases | -90.0873 | 29.9236 | Animal | Line Fuse | Animal | 2020-01-07 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 75 | 1321820126 | Yes | EAST ORLEANS | FAIR | 211 | 2020-01-07 20:49 | 2020-01-07 23:01 | 2020-01-08 00:20 | 15825 | LFUS | 27348 | 4264949768 | 1602 | ENOI | 6 | 75 | EPRI | Equipment Failure - Primary Conductor | N | bad cable from cubicle 6 to vault 1 | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-07 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 11 | 1321820424 | Yes | ORLEANS | FAIR | 74 | 2020-01-07 21:17 | 2020-01-07 21:17 | 2020-01-07 22:31 | 814 | TFUS | 55653 | 38968480755 | 904 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1024 | 29.9832 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-07 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 16 | 1321829805 | Yes | ORLEANS | FAIR | 211 | 2020-01-08 06:59 | 2020-01-08 07:11 | 2020-01-08 10:30 | 3376 | TFUS | 53182 | 38684487237 | 408 | ENOI | 1 | 16 | FOTH | Fire - Other (Describe in Remarks Field) | N | fire at location burnt wire down, transformer back in | -90.1114 | 30.0011 | Other | Transformer Fuse | Other | 2020-01-08 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 4 | 1321831987 | Yes | EAST ORLEANS | FAIR | 260 | 2020-01-08 08:56 | 2020-01-08 08:59 | 2020-01-08 13:16 | 1040 | TFUS | 79575 | 42517501966 | 2212 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N |  | -89.9896 | 30.0404 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-08 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 276 | 1321835001 | Yes | EAST ORLEANS | FAIR | 247 | 2020-01-08 10:45 | 2020-01-08 13:01 | 2020-01-08 14:52 | 68172 | LFUS | 26252 | 4360850642 | 2214 | ENOI | 6 | 276 | ETRD | Equipment Failure - Transformer | N | crew to replace | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-08 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 48 | 1321847622 | Yes | EAST ORLEANS | FAIR | 58 | 2020-01-08 14:30 | 2020-01-08 15:08 | 2020-01-08 15:28 | 2784 | LFUS | 37416 | 40593476553 | 622 | ENOI | 6 | 48 | SCHD | Scheduled Interruption | N | crew on site | -90.0513 | 29.9711 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-01-08 | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 3 | 1321852054 | Yes | EAST ORLEANS | FAIR | 48 | 2020-01-08 16:13 | 2020-01-08 16:13 | 2020-01-08 17:01 | 144 | XFMR | 665472 | 41954472941 | 2346 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N |  | -90.0084 | 29.9607 | Equipment Failure | Transformer | Equipment Failure | 2020-01-08 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 1 | 1321890202 | Yes | ORLEANS | FAIR | 22 | 2020-01-09 19:02 | 2020-01-09 19:02 | 2020-01-09 19:24 | 22 | SERV | METER | 38903461840 | 1914 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | Changed **TFUS 77590 * 11 to SERV 77590 * 1** --- meter was not all rthe way into meter socket. per 310 treed3 | -90.1052 | 29.9311 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-09 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 1 | 1321900766 | Yes | EAST ORLEANS | FAIR | 78 | 2020-01-10 03:42 | 2020-01-10 03:42 | 2020-01-10 05:00 | 78 | SERV | SERVICE | 42073500359 | 2212 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N | ami meter burned up customer lug pulled meter meter #am10993i155 installed new meter 8154918 sn 92095254 cbowden | -90.0037 | 30.0361 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 17 | 1321917083 | Yes | EAST ORLEANS | FAIR | 136 | 2020-01-10 11:29 | 2020-01-10 11:46 | 2020-01-10 13:45 | 2312 | LFUS | 23780 | 42465497468 | 1602 | ENOI | 6 | 17 | UNKN | Inspected Unknown | N | Changed **TFUS 1298164 * 17 to LFUS 1298164 * 17** --- Refused B phase in cub 167 sw 23780--Inspected unknown jvickna | -89.9915 | 30.0279 | Other | Line Fuse | Other | 2020-01-10 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 5 | 1321924209 | Yes | ALGIERS ELEC ONLY | FAIR | 36 | 2020-01-10 12:09 | 2020-01-10 12:09 | 2020-01-10 12:45 | 180 | LFUS | 5534-F | 4462845638 | W1715 | ENOI | 81 | 5 | EARM | Equipment Failure - Crossarm | N | Crew to replace cross-arm downstream of this device, per Zach Washington...........PC | -89.9246 | 29.9144 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-10 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 137 | 1321931828 | Yes | EAST ORLEANS | FAIR | 39 | 2020-01-10 13:56 | 2020-01-10 14:27 | 2020-01-10 14:35 | 5343 | DIS | 38259 | 4126248306 | 626 | ENOI | 6 | 137 | SCHD | Scheduled Interruption | N | Scheduled Interruption; crew picking up low hanging primary | -90.0301 | 29.9887 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-01-10 | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 76 | 1322200807 | Yes | ORLEANS | THDR | 147 | 2020-01-11 06:34 | 2020-01-11 08:40 | 2020-01-11 09:01 | 11172 | LFUS | 27822 | 3801346713 | B0527 | ENOI | 1 | 76 | VLFL | Tree On Line Outside R.O.W | N | crew repaired shield wire damaged by tree | -90.1331 | 29.946 | Vegetation | Line Fuse | Vegetation | 2020-01-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 5 | 1322147313 | Yes | ORLEANS | WIND | 79 | 2020-01-11 06:38 | 2020-01-11 06:38 | 2020-01-11 07:57 | 395 | TFUS | 1385289 | 39706489324 | 1704 | ENOI | 1 | 5 | VOHL | Overhanging Limb | N | found tree branch on top of transformer resfued ok jcox7 | -90.079 | 30.0065 | Vegetation | Transformer Fuse | Vegetation | 2020-01-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 1 | 1322173499 | Yes | ORLEANS | WIND | 44 | 2020-01-11 07:43 | 2020-01-11 07:43 | 2020-01-11 08:27 | 44 | SECO | SECONDARY COND | 39729483055 | 627 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Changed **TFUS 9 to TFUS 1** --- loose connection at pole repaired and checked voltage jcox7 | -90.0785 | 29.9892 | Equipment Failure | Secondary Conductor | Equipment Failure | 2020-01-11 | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 86 | 1322194593 | Yes | ORLEANS | THDR | 361 | 2020-01-11 08:16 | 2020-01-11 13:15 | 2020-01-11 14:17 | 31046 | LFUS | 27790 | 39932484636 | 1703 | ENOI | 1 | 86 | EARM | Equipment Failure - Crossarm | N | crew replaced crossarm and repaired pole | -90.072 | 29.9935 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 12 | 1322234430 | Yes | ORLEANS | THDR | 54 | 2020-01-11 09:25 | 2020-01-11 09:30 | 2020-01-11 10:19 | 648 | TFUS | 518794 | 38168466520 | 2014 | ENOI | 1 | 12 | LGHT | Lightning | N | out by weather. refused ok dsmit36 | -90.1283 | 29.9443 | Lightning | Transformer Fuse | Lightning | 2020-01-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 61 | 1322256616 | Yes | ORLEANS | THDR | 63 | 2020-01-11 09:26 | 2020-01-11 09:57 | 2020-01-11 10:29 | 3843 | LFUS | 28031 | 3833945903 | 1914 | ENOI | 1 | 61 | LGHT | Lightning | N | lightning tagged an insulator 1 span from the lateral. Crew changed ins. and refused lateral rbiles | -90.1231 | 29.9237 | Lightning | Line Fuse | Lightning | 2020-01-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 11 | 1322240774 | Yes | ORLEANS | THDR | 49 | 2020-01-11 09:33 | 2020-01-11 09:33 | 2020-01-11 10:22 | 539 | LFUS | 33059 | 38974475070 | 903 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | roof blew off building taking out a and b phase and taking down 1 span open wire secondary, picked up wire and refused lateral mrusse8 | -90.1025 | 29.9676 | Other | Line Fuse | Other | 2020-01-11 | DLIN | B | Council District B | Jay Banks | 70119 | 1
2020 | 10 | 1322249652 | Yes | EAST ORLEANS | THDR | 93 | 2020-01-11 09:37 | 2020-01-11 09:41 | 2020-01-11 11:10 | 930 | LFUS | 38536 | 43220496192 | 1611 | ENOI | 6 | 10 | LGHT | Lightning | N | Changed **TFUS 1361822 8 to LFUS 1361822 8** --- refused B and C phase on lateral 38536 due to weather jvickna | -89.9677 | 30.0243 | Lightning | Line Fuse | Lightning | 2020-01-11 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 1 | 1322323741 | Yes | ALGIERS ELEC ONLY | THDR | 330 | 2020-01-11 10:00 | 2020-01-11 10:00 | 2020-01-11 15:30 | 330 | TFUS | 1543046 | 4141646669 | W1725 | ENOI | 81 | 1 | EMER | Emergency Switching | N | Opened in order for crew to make repairs. per B. rissuto............PC | -90.0258 | 29.9437 | Other | Transformer Fuse | Emergency Switching | 2020-01-11 | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 42 | 1322269743 | Yes | ALGIERS ELEC ONLY | RAIN | 113 | 2020-01-11 10:00 | 2020-01-11 10:48 | 2020-01-11 11:53 | 4746 | LFUS | 5002 | 4141446606 | W1725 | ENOI | 81 | 42 | ETRD | Equipment Failure - Transformer | N | back n now bad pot brizzut | -90.0259 | 29.942 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-11 | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 33 | 1322288849 | Yes | EAST ORLEANS | FAIR | 69 | 2020-01-11 10:35 | 2020-01-11 10:57 | 2020-01-11 11:44 | 2277 | LFUS | 34976 | 4152747182 | 2346 | ENOI | 6 | 33 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | ballon got into secondary took out stinger pot which blew lateral fuse refuse lateral and transformer and lights are back on and good voltage dwillin | -90.022 | 29.9578 | Other | Line Fuse | Other | 2020-01-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 1 | 1322322442 | Yes | EAST ORLEANS | THDR | 96 | 2020-01-11 11:48 | 2020-01-11 11:50 | 2020-01-11 13:24 | 96 | LFUS | 83983 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | vines took out b phase on terminal pole-cleared vines and refused b phase ok-voltage ok-cust back on swalsh1 1-11-20 swalsh1 | -90.0377 | 30.0062 | Vegetation | Line Fuse | Vegetation | 2020-01-11 | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 30 | 1322330888 | Yes | ORLEANS | THDR | 109 | 2020-01-11 12:19 | 2020-01-11 12:19 | 2020-01-11 14:08 | 3270 | LFUS | 27906 | 38475463265 | 1926 | ENOI | 1 | 30 | LGHT | Lightning | N | lightning took out c phase of lateral 27906 refused ok rbiles | -90.1186 | 29.9353 | Lightning | Line Fuse | Lightning | 2020-01-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 88 | 1322332691 | Yes | ORLEANS | THDR | 35 | 2020-01-11 12:29 | 2020-01-11 12:53 | 2020-01-11 13:05 | 3080 | LFUS | 37781 | 3988848138 | 1709 | ENOI | 1 | 88 | LGHT | Lightning | N | ispected unknown refused advise jcox7 | -90.0735 | 29.9846 | Lightning | Line Fuse | Lightning | 2020-01-11 | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 2 | 1322340541 | Yes | EAST ORLEANS | THDR | 71 | 2020-01-11 13:04 | 2020-01-11 13:04 | 2020-01-11 14:15 | 142 | PRIM | 4341249109 | 4341249109 | 1612 | ENOI | 6 | 2 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | MOULDING | -89.9618 | 30.0102 | Other | Primary Meter | Other | 2020-01-11 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 41 | 1322465744 | Yes | ORLEANS | FAIR | 434 | 2020-01-12 04:11 | 2020-01-12 10:17 | 2020-01-12 11:25 | 17794 | DIS | 14349 | 3982346566 | 2137 | ENOI | 1 | 41 | EMER | Emergency Switching | N | broke pole, crew on site | -90.0761 | 29.9413 | Other | Disconnect Switch | Emergency Switching | 2020-01-12 | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 2 | 1322467215 | Yes | ALGIERS ELEC ONLY | RAIN | 216 | 2020-01-12 05:55 | 2020-01-12 05:55 | 2020-01-12 09:31 | 432 | TFUS | BY174099 | 4417845173 | W1715 | ENOI | 81 | 2 | EFSW | Equipment Failure - Fuse Switch | N | top riser on switch burnt in the clear made repairs cust back in light jthom15 | -89.9391 | 29.9017 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-12 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 3 | 1322474174 | Yes | ALGIERS ELEC ONLY | RAIN | 133 | 2020-01-12 07:35 | 2020-01-12 07:35 | 2020-01-12 09:48 | 399 | TFUS | BY174123 | 4405545113 | W1715 | ENOI | 81 | 3 | EFSW | Equipment Failure - Fuse Switch | N | top riser on switch burnt in clear made repairs cust back in lights jthom15 | -89.943 | 29.9001 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-12 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 5 | 1322510653 | Yes | ORLEANS | FAIR | 78 | 2020-01-12 12:23 | 2020-01-12 12:23 | 2020-01-12 13:41 | 390 | TFUS | 1183487 | 39789466302 | 2137 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0772 | 29.9432 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-12 | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 65 | 1322523814 | Yes | EAST ORLEANS | FAIR | 139 | 2020-01-12 13:41 | 2020-01-12 13:44 | 2020-01-12 16:01 | 9035 | LFUS | 25724 | 4319150521 | 2214 | ENOI | 6 | 65 | EPRI | Equipment Failure - Primary Conductor | N | bad cable between cub 60 and vault 100 | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 2 | 1322605291 | Yes | EAST ORLEANS | FOGG | 78 | 2020-01-13 07:29 | 2020-01-13 07:29 | 2020-01-13 08:47 | 156 | TFUS | 1106471 | 41320493904 | 1009 | ENOI | 6 | 2 | EFLK | Equipment Failure - Fuse Link | N | refused b phase check customer ok cschexn | -90.0277 | 30.0186 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-13 | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 17 | 1322615999 | Yes | ORLEANS | FAIR | 242 | 2020-01-13 09:40 | 2020-01-13 13:25 | 2020-01-13 13:42 | 4114 | DIS | 27125 | 38503474755 | 2011 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | outage required to safely replace rotten xarms located at the intersection of Olive and Leonidas | -90.1174 | 29.9667 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-01-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 26 | 1322629818 | Yes | ORLEANS | FAIR | 78 | 2020-01-13 12:12 | 2020-01-13 12:12 | 2020-01-13 13:30 | 2028 | DIS | 23138 | 3852247482 | 2012 | ENOI | 1 | 26 | SCHD | Scheduled Interruption | N | Line de-energized to safely replace xarms | -90.1168 | 29.9669 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-01-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 1 | 1322667082 | Yes | ALGIERS ELEC ONLY | FOGG | 311 | 2020-01-13 16:19 | 2020-01-13 16:28 | 2020-01-13 21:30 | 311 | SERV | SERVICE | 4136546563 | W0725 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N | Changed **TFUS BY88464 37 to SERV BY88464 1** --- old service line went bad. changed out line and good voltage checked mtaruc | -90.0274 | 29.9409 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-13 | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 23 | 1322735698 | Yes | EAST ORLEANS | FAIR | 240 | 2020-01-14 10:00 | 2020-01-14 10:00 | 2020-01-14 14:00 | 5520 | TFUS | 67500 | 40484476639 | 623 | ENOI | 6 | 23 | SCHD | Scheduled Interruption | N | ppole transfer | -90.0547 | 29.9714 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-14 | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 6 | 1322735719 | Yes | EAST ORLEANS | FAIR | 12 | 2020-01-14 10:18 | 2020-01-14 10:18 | 2020-01-14 10:30 | 72 | TFUS | 73176 | 41551474793 | 2347 | ENOI | 6 | 6 | ESEC | Secondary/Service Conductor | N | made repairs to trans | -90.0211 | 29.966 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-14 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 2 | 1322818414 | Yes | EAST ORLEANS | FAIR | 36 | 2020-01-15 13:05 | 2020-01-15 13:05 | 2020-01-15 13:41 | 72 | XFMR | 79392 | 49613525017 | 1204 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N |  | -89.7641 | 30.1015 | Equipment Failure | Transformer | Equipment Failure | 2020-01-15 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 4 | 1322854567 | Yes | EAST ORLEANS | FAIR | 66 | 2020-01-16 09:34 | 2020-01-16 09:34 | 2020-01-16 10:40 | 264 | TFUS | 1605537 | 42777504021 | 2215 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | crew onsite | -89.9813 | 30.046 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-16 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 52 | 1322857299 | Yes | EAST ORLEANS | FAIR | 34 | 2020-01-16 10:04 | 2020-01-16 10:15 | 2020-01-16 10:38 | 1768 | LFUS | 24311 | 4173149985 | 2212 | ENOI | 6 | 52 | VINE | Vine Growing into Line | N | vines grew into b phase cleaared as muc as i could but someone needs to coem clear vines road out lateral all lights came back on as i can tell | -90.0146 | 30.0348 | Vegetation | Line Fuse | Vegetation | 2020-01-16 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 5 | 1322933942 | Yes | ALGIERS ELEC ONLY | FAIR | 53 | 2020-01-17 15:55 | 2020-01-17 15:55 | 2020-01-17 16:48 | 265 | TFUS | BY110681 | 4226045412 | W1714 | ENOI | 81 | 5 | SCHD | Scheduled Interruption | N | Nick Carroll will have xfmr out | -89.9995 | 29.9089 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-17 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 1 | 1322951627 | Yes | ALGIERS ELEC ONLY | FAIR | 215 | 2020-01-18 08:39 | 2020-01-18 08:39 | 2020-01-18 12:14 | 215 | SERV | METER | 4164146240 | W0725 | ENOI | 81 | 1 | MTEX | Meter Exchange | N | stolen meter, mtr change ticket to be made, rc | -90.0187 | 29.9319 | Other | Service Conductor | Other | 2020-01-18 | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 7 | 1323000141 | Yes | ALGIERS ELEC ONLY | FAIR | 74 | 2020-01-19 06:21 | 2020-01-19 06:31 | 2020-01-19 07:35 | 518 | TFUS | 1417734 | 4264345881 | W1713 | ENOI | 81 | 7 | VOHL | Overhanging Limb | N | ROBERT COURET W-00 | -89.9873 | 29.9217 | Vegetation | Transformer Fuse | Vegetation | 2020-01-19 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 7 | 1323001850 | Yes | ALGIERS ELEC ONLY | FAIR | 134 | 2020-01-19 07:55 | 2020-01-19 07:55 | 2020-01-19 10:09 | 938 | XFMR | 1417734 | 4264345881 | W1713 | ENOI | 81 | 7 | ETRD | Equipment Failure - Transformer | N | Nick Carroll crew (Ollie Hull, Benjamin Clayborn, Brad Barrios) | -89.9873 | 29.9217 | Equipment Failure | Transformer | Equipment Failure | 2020-01-19 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 1 | 1323003961 | Yes | ORLEANS | FAIR | 140 | 2020-01-19 08:35 | 2020-01-19 08:35 | 2020-01-19 10:55 | 140 | SECO | SECONDARY | 38600465860 | 1554 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | bad jumper on secondary wire | -90.1147 | 29.9424 | Equipment Failure | Secondary Conductor | Equipment Failure | 2020-01-19 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 3 | 1323025386 | Yes | ORLEANS | FAIR | 189 | 2020-01-20 04:51 | 2020-01-20 04:51 | 2020-01-20 08:00 | 567 | TFUS | 32466 | 39602493949 | 509 | ENOI | 1 | 3 | ESEC | Secondary/Service Conductor | N | transformer back in and secondary picked back up | -90.0821 | 30.0192 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 3 | 1323037426 | Yes | EAST ORLEANS | FAIR | 249 | 2020-01-20 14:12 | 2020-01-20 14:17 | 2020-01-20 18:21 | 747 | XFMR | 1193965 | 42845504050 | 2216 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | bad transformer, crew in route | -89.9791 | 30.0459 | Equipment Failure | Transformer | Equipment Failure | 2020-01-20 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 5 | 1323046317 | Yes | EAST ORLEANS | FAIR | 352 | 2020-01-20 21:08 | 2020-01-20 21:08 | 2020-01-21 03:00 | 1760 | TFUS | 1193973 | 40899482518 | 611 | ENOI | 6 | 5 | ESEC | Secondary/Service Conductor | N | repairs at transformer | -90.0415 | 29.9874 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-20 | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 16 | 1323046635 | Yes | ORLEANS | FAIR | 208 | 2020-01-20 21:21 | 2020-01-20 21:21 | 2020-01-21 00:50 | 3328 | TFUS | 729472 | 38920475976 | 903 | ENOI | 1 | 16 | ECON | Equipment Failure - Connector / Sleeve | N | changed out connections at weather head. | -90.1041 | 29.9701 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-20 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 263 | 1323053986 | Yes | EAST ORLEANS | FAIR | 463 | 2020-01-21 02:19 | 2020-01-21 10:02 | 2020-01-21 10:02 | 121769 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 263 | EPRI | Equipment Failure - Primary Conductor | N | primary wire down | -89.8028 | 30.0694 | Equipment Failure | Recloser | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 253 | 1323053914 | Yes | EAST ORLEANS | FAIR | 401 | 2020-01-21 04:54 | 2020-01-21 11:32 | 2020-01-21 11:35 | 101453 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 253 | ETRD | Equipment Failure - Transformer | N | replaced transformer and lateral back in | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 15 | 1323063051 | Yes | ORLEANS | FAIR | 201 | 2020-01-21 08:36 | 2020-01-21 08:44 | 2020-01-21 11:57 | 3015 | SWIT | V10-17 | 38818496158 | 401 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | recable job | -97.0758 | 27.9066 | Scheduled Interruption | Switch | Scheduled Interruption | 2020-01-21 | DLIN | D | Council District D | Jared Brossett | 70124 | 1
2020 | 1 | 1323068509 | Yes | ALGIERS ELEC ONLY | FAIR | 101 | 2020-01-21 12:00 | 2020-01-21 12:00 | 2020-01-21 13:41 | 101 | SERV | SERVICE | 4252245651 | W1714 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N |  | -89.9912 | 29.9154 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-21 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 15 | 1323070035 | Yes | ALGIERS ELEC ONLY | FAIR | 165 | 2020-01-21 12:54 | 2020-01-21 13:02 | 2020-01-21 15:39 | 2475 | TFUS | 1203436 | 4255145618 | W1714 | ENOI | 81 | 15 | UNKN | Inspected Unknown | N |  | -89.9903 | 29.9145 | Other | Transformer Fuse | Other | 2020-01-21 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 9 | 1323073215 | Yes | EAST ORLEANS | FAIR | 121 | 2020-01-21 14:10 | 2020-01-21 14:10 | 2020-01-21 16:11 | 1089 | TFUS | 64100 | 43284495685 | 1611 | ENOI | 6 | 9 | SCHD | Scheduled Interruption | N | crew opened for safety to transfer pole | -89.9656 | 30.0229 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 9 | 1323082060 | Yes | EAST ORLEANS | FAIR | 640 | 2020-01-21 17:59 | 2020-01-21 21:01 | 2020-01-22 04:39 | 5760 | XFMR | 1495749 | 40463475459 | 623 | ENOI | 6 | 9 | ETRD | Equipment Failure - Transformer | N | crew changedtransformer | -90.0556 | 29.9681 | Equipment Failure | Transformer | Equipment Failure | 2020-01-21 | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 716 | 1323082860 | Yes | EAST ORLEANS | FAIR | 75 | 2020-01-21 18:23 | 2020-01-21 19:28 | 2020-01-21 19:38 | 53700 | SBKR | 1204 | 4544050173 | 1204 | ENOI | 6 | 716 | EPRI | Equipment Failure - Primary Conductor | N | poen midpoint breaker in | -89.8973 | 30.0387 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 51 | 1323083919 | Yes | EAST ORLEANS | FAIR | 576 | 2020-01-21 19:02 | 2020-01-22 02:32 | 2020-01-22 04:38 | 29376 | LFUS | 24971 | 4214250165 | 2212 | ENOI | 6 | 51 | ETRD | Equipment Failure - Transformer | N | Failed padmount transformer | -90.0015 | 30.0396 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 234 | 1323084559 | Yes | EAST ORLEANS | FAIR | 27 | 2020-01-21 19:43 | 2020-01-21 19:57 | 2020-01-21 20:10 | 3510 | RCLR | 37793 | 4946452184 | 1204 | ENOI | 6 | 234 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.7693 | 30.0927 | Equipment Failure | Recloser | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 9 | 1323084922 | Yes | EAST ORLEANS | FAIR | 524 | 2020-01-21 19:54 | 2020-01-21 20:01 | 2020-01-22 04:39 | 4716 | TFUS | 1315139 | 43498509515 | 2217 | ENOI | 6 | 9 | EABS | Equipment Failure - Air Break / Disconnect Switch | N |  | -89.9583 | 30.0609 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 3 | 1323085293 | Yes | EAST ORLEANS | FAIR | 55 | 2020-01-21 19:58 | 2020-01-21 19:58 | 2020-01-21 20:53 | 165 | LFUS | F05622 | 4830351192 | 1204 | ENOI | 6 | 3 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.8064 | 30.0658 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 262 | 1323085775 | Yes | EAST ORLEANS | FAIR | 320 | 2020-01-21 19:58 | 2020-01-21 22:25 | 2020-01-22 01:18 | 83840 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 262 | EPRI | Equipment Failure - Primary Conductor | N | wire down in marsh | -89.8028 | 30.0694 | Equipment Failure | Recloser | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 1 | 1323087626 | Yes | EAST ORLEANS | FAIR | 175 | 2020-01-21 21:43 | 2020-01-21 21:43 | 2020-01-22 00:38 | 175 | TFUS | 65841 | 46077507365 | 1204 | ENOI | 6 | 1 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.8769 | 30.054 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 614 | 1323087728 | Yes | EAST ORLEANS | FAIR | 409 | 2020-01-21 22:01 | 2020-01-22 02:53 | 2020-01-22 04:50 | 251126 | RCLR | 85388 | 4373351112 | 2217 | ENOI | 6 | 614 | EPRI | Equipment Failure - Primary Conductor | N | wiredown | -89.951 | 30.0652 | Equipment Failure | Recloser | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 12 | 1323088224 | Yes | EAST ORLEANS | FAIR | 228 | 2020-01-21 22:03 | 2020-01-22 01:21 | 2020-01-22 01:51 | 2736 | TFUS | 1048655 | 43916511664 | 2217 | ENOI | 6 | 12 | EABS | Equipment Failure - Air Break / Disconnect Switch | N | outage is due to crew picking up wire on curran. avon park is inside isolated portion of feeder thats under clearance | -89.945 | 30.0667 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 11 | 1323088737 | Yes | EAST ORLEANS | FAIR | 226 | 2020-01-21 23:27 | 2020-01-22 00:10 | 2020-01-22 03:13 | 2486 | TFUS | 23813 | 40482495074 | 506 | ENOI | 6 | 11 | ECON | Equipment Failure - Connector / Sleeve | N | burnt trans lead ..replaced | -90.0541 | 30.0221 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 1 | 1323096832 | Yes | ORLEANS | FAIR | 90 | 2020-01-22 10:01 | 2020-01-22 10:01 | 2020-01-22 11:31 | 90 | SERV | SERVICE | 39963459713 | 2147 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | bad connection at pole | -90.0718 | 29.9251 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-22 | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 125 | 1323111678 | Yes | ORLEANS | FAIR | 227 | 2020-01-22 15:28 | 2020-01-22 18:40 | 2020-01-22 19:15 | 28375 | LFUS | 21686 | 3971247620 | 907 | ENOI | 1 | 125 | VHCL | Vehicle | N | dump truck hit pole PID IN PROGRESS (Unable to to find info on dump truck that hit the pole) | -90.0791 | 29.9705 | Public Damage | Line Fuse | Public Damage | 2020-01-22 | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 460 | 1323115884 | Yes | ALGIERS ELEC ONLY | FAIR | 213 | 2020-01-22 18:02 | 2020-01-22 21:12 | 2020-01-22 21:35 | 97980 | LFUS | 1105 | 4195645775 | W0712 | ENOI | 81 | 460 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | L1105 was blown as well as subL34242, cause balloons on switch, rc 1-22-20 | -90.009 | 29.919 | Other | Line Fuse | Other | 2020-01-22 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 19 | 1323119085 | Yes | EAST ORLEANS | FAIR | 145 | 2020-01-22 20:36 | 2020-01-22 22:26 | 2020-01-22 23:01 | 2755 | LFUS | 25651 | 4338850670 | 2214 | ENOI | 6 | 19 | EELB | Equipment Failure - Elbow | N | bad ebow crew chad.. | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-22 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 172 | 1323119101 | Yes | EAST ORLEANS | FAIR | 278 | 2020-01-22 20:37 | 2020-01-23 01:17 | 2020-01-23 01:15 | 47816 | LFUS | 25610 | 4335750498 | 2214 | ENOI | 6 | 172 | EELB | Equipment Failure - Elbow | N | bad elbow | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-22 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 13 | 1323133322 | Yes | ORLEANS | FAIR | 67 | 2020-01-23 07:43 | 2020-01-23 08:07 | 2020-01-23 08:50 | 871 | TFUS | 72349 | 38762481819 | 903 | ENOI | 1 | 13 | VHCL | Vehicle | N | truck pulled down service line and tore meters and stem pipe off of house. related to ticket 1323096279 yesterday already sent to minimalclaimskc | -90.1091 | 29.9862 | Public Damage | Transformer Fuse | Public Damage | 2020-01-23 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 167 | 1323138006 | Yes | ALGIERS ELEC ONLY | THDR | 85 | 2020-01-23 09:43 | 2020-01-23 11:07 | 2020-01-23 11:08 | 14195 | RCLR | 5123 | 4150446191 | W0725 | ENOI | 81 | 167 | EMER | Emergency Switching | N | phase down on arm | -90.0231 | 29.9306 | Other | Recloser | Emergency Switching | 2020-01-23 | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 56 | 1323138236 | Yes | ORLEANS | FAIR | 77 | 2020-01-23 09:48 | 2020-01-23 09:57 | 2020-01-23 11:05 | 4312 | LFUS | 27806 | 3884646637 | 1916 | ENOI | 1 | 56 | EARM | Equipment Failure - Crossarm | N | cross arm broke street side phase was cut down temp ok gor now #305 | -90.1068 | 29.9437 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-23 | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 211 | 1323138909 | Yes | ALGIERS ELEC ONLY | THDR | 219 | 2020-01-23 09:59 | 2020-01-23 12:40 | 2020-01-23 13:38 | 46209 | RCLR | 33772 | 4313545406 | W1715 | ENOI | 81 | 211 | EINS | Equipment Failure - Insulator | N | BCLEME1 | -89.9719 | 29.9085 | Equipment Failure | Recloser | Equipment Failure | 2020-01-23 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 47 | 1323159950 | Yes | ORLEANS | FAIR | 153 | 2020-01-23 23:43 | 2020-01-23 23:56 | 2020-01-24 02:16 | 7191 | LFUS | 28009 | 3863545809 | 1913 | ENOI | 1 | 47 | SCHD | Scheduled Interruption | N | crew was out there on a schduled outage | -90.1137 | 29.9209 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-01-23 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 1 | 1323164693 | Yes | ORLEANS | FAIR | 71 | 2020-01-24 08:07 | 2020-01-24 08:07 | 2020-01-24 09:18 | 71 | SERV | SERVICE COND | 38374484905 | 407 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | bad connection at weather head changed out ok #305 | -90.1212 | 29.9948 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-24 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 2 | 1323182720 | Yes | ORLEANS | FAIR | 92 | 2020-01-24 17:00 | 2020-01-24 17:00 | 2020-01-24 18:32 | 184 | LFUS | 37944 | 38356458630 | 1914 | ENOI | 1 | 2 | EFLK | Equipment Failure - Fuse Link | N | Found phase switch blown on lateral to closed delta bank. Inspected primary and found flash mark where wire touched other potential. Refused lateral phase and threw it in. Back in lights. | -90.1226 | 29.9225 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-24 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 3 | 1323198606 | Yes | EAST ORLEANS | FAIR | 203 | 2020-01-25 15:29 | 2020-01-25 15:29 | 2020-01-25 18:52 | 609 | TFUS | 1460718 | 40760480182 | 622 | ENOI | 6 | 3 | EARM | Equipment Failure - Crossarm | N | replaced crossarm arm on dead end pole | -90.046 | 29.9811 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-25 | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 110 | 1323217422 | Yes | EAST ORLEANS | FAIR | 464 | 2020-01-26 09:43 | 2020-01-26 13:21 | 2020-01-26 17:27 | 51040 | LFUS | 27177 | 4351250071 | 1609 | ENOI | 6 | 110 | ETRD | Equipment Failure - Transformer | N | crew changed out bad transformer | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-26 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 1 | 1323217578 | Yes | ORLEANS | FAIR | 140 | 2020-01-26 10:03 | 2020-01-26 10:03 | 2020-01-26 12:23 | 140 | SERV | SERVICE | 39316462677 | 1924 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Repaired neutral at weatherhead | -90.0921 | 29.9333 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-26 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 2 | 1323217943 | Yes | EAST ORLEANS | FAIR | 173 | 2020-01-26 10:23 | 2020-01-26 10:23 | 2020-01-26 13:16 | 346 | TFUS | 32086 | 44464496384 | 1601 | ENOI | 6 | 2 | ASQL | Animal - Squirrel | N | squirrel took out transformer feeding building refused transfomre got great voltage now no one is here its a commercial customer closed today | -89.9283 | 30.0244 | Animal | Transformer Fuse | Animal | 2020-01-26 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 83 | 1323219985 | Yes | ORLEANS | FAIR | 66 | 2020-01-26 12:29 | 2020-01-26 12:43 | 2020-01-26 13:35 | 5478 | LFUS | 27976 | 4035147852 | 1709 | ENOI | 1 | 83 | EPRI | Equipment Failure - Primary Conductor | N |  | -90.0588 | 29.9766 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-26 | DLIN | D | Council District D | Jared Brossett | 70116 | 1
2020 | 25 | 1323220694 | Yes | ORLEANS | FAIR | 125 | 2020-01-26 13:29 | 2020-01-26 13:36 | 2020-01-26 15:34 | 3125 | LFUS | 27940 | 3927945767 | 1922 | ENOI | 1 | 25 | VINE | Vine Growing into Line | N | Vines. Refused ok Veg ticket created Jmulle2 | -90.0935 | 29.9194 | Vegetation | Line Fuse | Vegetation | 2020-01-26 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 12 | 1323222467 | Yes | ORLEANS | RAIN | 131 | 2020-01-26 15:50 | 2020-01-26 17:09 | 2020-01-26 18:01 | 1572 | TFUS | 18346 | 38366491158 | 409 | ENOI | 1 | 12 | AOTH | Animal - Other (Describe in Remarks Field) | N | bird droppings on top tformer cleaned off the droppings tformer refused good everyone back in lights | -90.1211 | 30.0119 | Animal | Transformer Fuse | Animal | 2020-01-26 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 19 | 1323227281 | Yes | ALGIERS ELEC ONLY | FAIR | 78 | 2020-01-26 22:56 | 2020-01-26 23:15 | 2020-01-27 00:14 | 1482 | LFUS | 5699 | 4261545915 | W1713 | ENOI | 81 | 19 | UNKN | Inspected Unknown | N | blown lat fuse refused and held also transformer 3004469 was blown not sure if this is what caused the lat fuse to blow. both lat fuse and transformer had proper size fuses in them also | -89.9882 | 29.9226 | Other | Line Fuse | Other | 2020-01-26 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 12 | 1323232466 | Yes | EAST ORLEANS | FAIR | 1673 | 2020-01-27 08:47 | 2020-01-27 08:48 | 2020-01-28 12:40 | 20076 | TFUS | 1313464 | 41862495089 | 1610 | ENOI | 6 | 12 | ETRD | Equipment Failure - Transformer | N | bad submersible;will be out until tomorrow morning | -90.0107 | 30.0217 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-27 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 7 | 1323232948 | Yes | ORLEANS | FAIR | 211 | 2020-01-27 09:00 | 2020-01-27 09:00 | 2020-01-27 12:31 | 1477 | TFUS | 59936 | 38748467302 | 1916 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1099 | 29.9463 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-27 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 1
2020 | 99 | 1323233258 | Yes | EAST ORLEANS | FAIR | 507 | 2020-01-27 09:14 | 2020-01-27 16:55 | 2020-01-27 17:41 | 50193 | LFUS | 27653 | 4289350637 | 2215 | ENOI | 6 | 99 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9777 | 30.0523 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-01-27 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 1451 | 1323244545 | Yes | ORLEANS | FAIR | 11 | 2020-01-27 13:45 | 2020-01-27 13:57 | 2020-01-27 13:56 | 15961 | SBKR | 1554 | 3950446990 | 1554 | ENOI | 1 | 1451 | UNKN | Inspected Unknown | N | serviceman did not find anything on line; closed bkr in and holding | -90.086 | 29.9532 | Other | Substation Breaker | Other | 2020-01-27 | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 17 | 1323248150 | Yes | ORLEANS | FAIR | 399 | 2020-01-27 15:21 | 2020-01-27 20:21 | 2020-01-27 22:00 | 6783 | XFMR | 62309 | 39410465886 | 1915 | ENOI | 1 | 17 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.089 | 29.9421 | Equipment Failure | Transformer | Equipment Failure | 2020-01-27 | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 1 | 1323248173 | Yes | ORLEANS | FAIR | 147 | 2020-01-27 15:23 | 2020-01-27 15:23 | 2020-01-27 17:51 | 147 | SERV | SERVICE | 39402478092 | 912 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | spliced service and made new connections at weatherhead | -90.0889 | 29.9758 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-27 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 12 | 1323251479 | Yes | ALGIERS ELEC ONLY | FAIR | 317 | 2020-01-27 17:46 | 2020-01-27 20:56 | 2020-01-27 23:03 | 3804 | TFUS | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | EFLK | Equipment Failure - Fuse Link | N | refused blown fuse | -89.9867 | 29.9226 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-27 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 315 | 1323252770 | Yes | EAST ORLEANS | FAIR | 40 | 2020-01-27 19:22 | 2020-01-27 19:53 | 2020-01-27 20:02 | 12600 | SBKR | 625 | 4081248423 | 625 | ENOI | 6 | 315 | VHCL | Vehicle | N | vehicle hit guy wire and flipped into feeder, removed and back on RELAED TO KT# 1323254789 (AKS) | -90.0442 | 29.9922 | Public Damage | Substation Breaker | Public Damage | 2020-01-27 | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 2365 | 1323253767 | Yes | ORLEANS | FAIR | 17 | 2020-01-27 19:25 | 2020-01-27 19:41 | 2020-01-27 19:42 | 40205 | SBKR | 907 | 3897447410 | 907 | ENOI | 1 | 2365 | EMER | Emergency Switching | N | had to drop feeder for transformers on fire | -90.1026 | 29.9648 | Other | Substation Breaker | Emergency Switching | 2020-01-27 | DLIN | B | Council District B | Jay Banks | 70119 | 1
2020 | 52 | 1323254359 | Yes | ORLEANS | FAIR | 481 | 2020-01-27 19:44 | 2020-01-27 23:25 | 2020-01-28 03:45 | 25012 | XFMR | 1413671 | 3986247585 | 907 | ENOI | 1 | 52 | ETRD | Equipment Failure - Transformer | N | bad transformer changed out, good voltager now | -90.0745 | 29.9694 | Equipment Failure | Transformer | Equipment Failure | 2020-01-27 | DLIN | D | Council District D | Jared Brossett | 70116 | 1
2020 | 8 | 1323262374 | Yes | ORLEANS | FAIR | 357 | 2020-01-28 08:03 | 2020-01-28 08:03 | 2020-01-28 14:00 | 2856 | TFUS | 62321 | 39300467704 | 2021 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0925 | 29.9471 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-28 | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 5 | 1323263389 | Yes | EAST ORLEANS | FAIR | 124 | 2020-01-28 08:48 | 2020-01-28 10:15 | 2020-01-28 10:52 | 620 | TFUS | 1087299 | 42802502570 | 2216 | ENOI | 6 | 5 | VHCL | Vehicle | N | someoned bumped cubicle and knocked out c phase | -89.9807 | 30.042 | Public Damage | Transformer Fuse | Public Damage | 2020-01-28 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 24 | 1323267264 | Yes | ORLEANS | FAIR | 692 | 2020-01-28 10:43 | 2020-01-28 20:23 | 2020-01-28 22:15 | 16608 | TFUS | 603506 | 38759464546 | 1554 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1097 | 29.9386 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-28 | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 4 | 1323272107 | Yes | ORLEANS | FAIR | 38 | 2020-01-28 13:44 | 2020-01-28 13:50 | 2020-01-28 14:22 | 152 | TFUS | 3004438 | 38731464304 | 1926 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Planned outage contractors working per#305 | -90.1105 | 29.938 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-28 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 1
2020 | 11 | 1323273155 | Yes | ORLEANS | FAIR | 98 | 2020-01-28 14:23 | 2020-01-28 14:23 | 2020-01-28 16:01 | 1078 | TFUS | 61598 | 39294467195 | 2021 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0927 | 29.9459 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-28 | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 1 | 1323284518 | Yes | EAST ORLEANS | FAIR | 303 | 2020-01-28 20:06 | 2020-01-28 21:25 | 2020-01-29 01:09 | 303 | SERV | SERVICE | 42166494030 | 1607 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | picked up wire, good voltage | -90.001 | 30.0187 | Equipment Failure | Service Conductor | Equipment Failure | 2020-01-28 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 12 | 1323289932 | Yes | ALGIERS ELEC ONLY | FAIR | 124 | 2020-01-29 02:45 | 2020-01-29 08:49 | 2020-01-29 04:49 | 1488 | XFMR | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | ETRD | Equipment Failure - Transformer | N | bad 100by in rear of 6315 brighton pl, rc 1-29-20 | -89.9867 | 29.9226 | Equipment Failure | Transformer | Equipment Failure | 2020-01-29 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 51 | 1323295246 | Yes | EAST ORLEANS | RAIN | 159 | 2020-01-29 05:36 | 2020-01-29 06:46 | 2020-01-29 08:15 | 8262 | DIS | 23316 | 4124747804 | 621 | ENOI | 6 | 51 | EARM | Equipment Failure - Crossarm | N | broke arm at disc. 25291 | -90.0308 | 29.975 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-01-29 | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 162 | 1323291398 | Yes | EAST ORLEANS | RAIN | 162 | 2020-01-29 05:36 | 2020-01-29 07:43 | 2020-01-29 08:18 | 26244 | RCLR | 23282 | 4122747950 | 621 | ENOI | 6 | 162 | EARM | Equipment Failure - Crossarm | N | broke crossarm at disc. 25291 | -90.0313 | 29.979 | Equipment Failure | Recloser | Equipment Failure | 2020-01-29 | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 144 | 1323293386 | Yes | EAST ORLEANS | RAIN | 321 | 2020-01-29 05:36 | 2020-01-29 10:53 | 2020-01-29 10:57 | 46224 | DIS | 23061 | 4122747782 | 621 | ENOI | 6 | 144 | EARM | Equipment Failure - Crossarm | N | broke crossarm at disc. 25291 | -90.0313 | 29.9745 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-01-29 | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 6 | 1323291673 | Yes | ORLEANS | FAIR | 112 | 2020-01-29 06:11 | 2020-01-29 06:52 | 2020-01-29 08:03 | 672 | TFUS | 16216 | 3989349266 | 510 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | refused transformer ( Dloc. # 39896492416 ) taken out by weather, lateral was still in | -90.073 | 30.0155 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 7 | 1323295995 | Yes | ORLEANS | RAIN | 393 | 2020-01-29 08:27 | 2020-01-29 08:27 | 2020-01-29 15:00 | 2751 | TFUS | 1590194 | 39330467050 | 2021 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0917 | 29.9454 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-29 | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 12 | 1323298113 | Yes | ALGIERS ELEC ONLY | FAIR | 199 | 2020-01-29 09:08 | 2020-01-29 09:09 | 2020-01-29 12:27 | 2388 | TFUS | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | SCHD | Scheduled Interruption | N | CREW OUTAGE | -89.9867 | 29.9226 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-29 | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 234 | 1323299416 | Yes | ORLEANS | FAIR | 384 | 2020-01-29 09:17 | 2020-01-29 14:51 | 2020-01-29 15:41 | 89856 | LFUS | 37908 | 3865747472 | 2017 | ENOI | 1 | 234 | ECNS | Equipment Failure - Connector Sleeve | N | SHIELD WIRE DOWN | -90.1124 | 29.9666 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 313 | 1323305072 | Yes | ORLEANS | FAIR | 21 | 2020-01-29 10:05 | 2020-01-29 10:05 | 2020-01-29 10:26 | 6573 | DIS | 25494 | 3882647318 | 2011 | ENOI | 1 | 313 | EMER | Emergency Switching | N | SHIELD WIRE DOWN | -90.1072 | 29.9624 | Other | Disconnect Switch | Emergency Switching | 2020-01-29 | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 11 | 1323304450 | Yes | ORLEANS | FAIR | 220 | 2020-01-29 10:05 | 2020-01-29 12:39 | 2020-01-29 13:45 | 2420 | DIS | 25476 | 3861947481 | 2011 | ENOI | 1 | 11 | EMER | Emergency Switching | N | SHIELD WIRE DOWN | -90.1137 | 29.9669 | Other | Disconnect Switch | Emergency Switching | 2020-01-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 9 | 1323304403 | Yes | ORLEANS | FAIR | 110 | 2020-01-29 10:05 | 2020-01-29 10:05 | 2020-01-29 11:55 | 990 | TFUS | 1361517 | 38447493598 | 409 | ENOI | 1 | 9 | EFSW | Equipment Failure - Fuse Switch | N | no comments | -90.1185 | 30.0186 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-29 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 6 | 1323312030 | Yes | ORLEANS | FAIR | 110 | 2020-01-29 12:43 | 2020-01-29 12:43 | 2020-01-29 14:33 | 660 | TFUS | 1417271 | 39826488565 | 1704 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | fuse link corroded and broke. replaced and reenergized ok. | -90.0752 | 30.0044 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-01-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 9 | 1323314478 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-29 13:40 | 2020-01-29 13:40 | 2020-01-29 15:00 | 720 | TFUS | 64100 | 43284495685 | 1611 | ENOI | 6 | 9 | SCHD | Scheduled Interruption | N |  | -89.9656 | 30.0229 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-01-29 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 24 | 1323314806 | Yes | ORLEANS | FAIR | 182 | 2020-01-29 13:44 | 2020-01-29 13:46 | 2020-01-29 16:46 | 4368 | TFUS | 1533023 | 39840459058 | 2147 | ENOI | 1 | 24 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | no comments | -90.0758 | 29.9232 | Other | Transformer Fuse | Other | 2020-01-29 | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 28 | 1323337190 | Yes | ORLEANS | FAIR | 241 | 2020-01-30 08:43 | 2020-01-30 08:43 | 2020-01-30 12:44 | 6748 | SWIT | 7 | 38833494311 | 401 | ENOI | 1 | 28 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -97.0758 | 27.9066 | Scheduled Interruption | Switch | Scheduled Interruption | 2020-01-30 | DLIN | D | Council District D | Jared Brossett | 70124 | 1
2020 | 90 | 1323344448 | Yes | EAST ORLEANS | FAIR | 303 | 2020-01-30 10:33 | 2020-01-30 14:15 | 2020-01-30 15:36 | 27270 | LFUS | 27340-F | 4482350242 | 1205 | ENOI | 6 | 90 | ETRD | Equipment Failure - Transformer | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-01-30 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 16 | 1323357585 | Yes | ORLEANS | FAIR | 343 | 2020-01-30 22:18 | 2020-01-31 00:16 | 2020-01-31 04:01 | 5488 | LFUS | 17679 | 38333485489 | 400 | ENOI | 1 | 16 | VHCL | Vehicle | N | SENT TO CLAIMS AS MINIMAL CLAIM. NO CAR AT SCENE | -90.1224 | 29.9964 | Public Damage | Line Fuse | Public Damage | 2020-01-30 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 42 | 1323384290 | Yes | EAST ORLEANS | FAIR | 579 | 2020-02-01 07:31 | 2020-02-01 16:49 | 2020-02-01 17:10 | 24318 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 42 | ETRD | Equipment Failure - Transformer | N | crew replaced | -89.9562 | 30.0596 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-01 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 1 | 1323384382 | Yes | EAST ORLEANS | FAIR | 393 | 2020-02-01 07:44 | 2020-02-01 09:13 | 2020-02-01 14:17 | 393 | SERV | SERVICE | 4386451333 | 2217 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | manhole burnt | -89.9466 | 30.0712 | Equipment Failure | Service Conductor | Equipment Failure | 2020-02-01 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 16 | 1323384421 | Yes | EAST ORLEANS | FAIR | 390 | 2020-02-01 07:52 | 2020-02-01 09:42 | 2020-02-01 14:22 | 6240 | TFUS | 617753 | 43842513577 | 2217 | ENOI | 6 | 16 | ESEC | Secondary/Service Conductor | N | manhole burnt up repaired | -89.9472 | 30.0719 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-01 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 68 | 1323384442 | Yes | ORLEANS | FAIR | 280 | 2020-02-01 08:01 | 2020-02-01 11:43 | 2020-02-01 12:41 | 19040 | LFUS | 17674 | 4020349326 | 503 | ENOI | 1 | 68 | EARM | Equipment Failure - Crossarm | N | Broken crossarm caused lateral outage also caused 1 span of lateral to burn down at sleeve. | -90.0632 | 30.0171 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-01 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 28 | 1323400798 | Yes | EAST ORLEANS | FOGG | 137 | 2020-02-01 23:54 | 2020-02-02 00:20 | 2020-02-02 02:11 | 3836 | LFUS | 27891 | 4156747196 | 2346 | ENOI | 6 | 28 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons on line; refused a phase | -90.0208 | 29.9582 | Other | Line Fuse | Other | 2020-02-01 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 26 | 1323427511 | Yes | ORLEANS | FAIR | 283 | 2020-02-02 19:37 | 2020-02-02 19:37 | 2020-02-03 00:21 | 7358 | LFUS | 21189 | 3800546584 | B0527 | ENOI | 1 | 26 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1335 | 29.9423 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-02 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 1 | 1323436744 | Yes | EAST ORLEANS | FAIR | 307 | 2020-02-03 08:24 | 2020-02-03 08:24 | 2020-02-03 13:31 | 307 | TFUS | 28497 | 41836500134 | 2212 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | replaced jumper connection | -90.0113 | 30.0356 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-03 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 134 | 1323441474 | Yes | EAST ORLEANS | FAIR | 108 | 2020-02-03 10:12 | 2020-02-03 10:57 | 2020-02-03 12:01 | 14472 | LFUS | 21152 | 4051147776 | 623 | ENOI | 6 | 134 | SCHD | Scheduled Interruption | N | crew onsite making repairs | -90.0538 | 29.9744 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-03 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 1 | 1323479576 | Yes | EAST ORLEANS | FAIR | 131 | 2020-02-03 17:25 | 2020-02-03 17:25 | 2020-02-03 19:36 | 131 | TFUS | 1177611 | 4066949720 | 508 | ENOI | 6 | 1 | UNKN | Inspected Unknown | N | fuse blown on a phase | -90.0482 | 30.0279 | Other | Transformer Fuse | Other | 2020-02-03 | DLIN | D | Council District D | Jared Brossett | 70148 | 2
2020 | 1 | 1323491980 | Yes | ORLEANS | FAIR | 80 | 2020-02-04 08:51 | 2020-02-04 08:51 | 2020-02-04 10:11 | 80 | SERV | METER | 38614466197 | 1554 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | ami meter open internally | -90.1143 | 29.9433 | Other | Service Conductor | Other | 2020-02-04 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 1 | 1323520258 | Yes | EAST ORLEANS | FAIR | 142 | 2020-02-04 20:52 | 2020-02-04 23:34 | 2020-02-04 23:14 | 142 | SERV | SERVICE | 43572495525 | 1601 | ENOI | 6 | 1 | VHCL | Vehicle | N | truck hit service line..hold meter#AM11175406 removed service ..meter pan pulled off wall. RELATED TO TKT# 1323511838, 1323512749 (AKS) | -89.9566 | 30.0223 | Public Damage | Service Conductor | Public Damage | 2020-02-04 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 735 | 1323525567 | Yes | ORLEANS | FAIR | 56 | 2020-02-05 01:00 | 2020-02-05 01:43 | 2020-02-05 01:56 | 47040 | DIS | 23899 | 3851646958 | 2016 | ENOI | 1 | 735 | VHCL | Vehicle | N | car broke pole; shield wire down PID IN PROGRESS- WAITING ON CONTRACTORS | -90.1171 | 29.9525 | Public Damage | Disconnect Switch | Public Damage | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 44 | 1323525769 | Yes | ORLEANS | FAIR | 68 | 2020-02-05 01:00 | 2020-02-05 01:00 | 2020-02-05 02:08 | 3212 | DIS | 23892 | 3854246996 | 2016 | ENOI | 1 | 44 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1163 | 29.9536 | Public Damage | Disconnect Switch | Public Damage | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 2
2020 | 82 | 1323525729 | Yes | ORLEANS | FAIR | 93 | 2020-02-05 01:00 | 2020-02-05 01:00 | 2020-02-05 02:33 | 7954 | DIS | 24330 | 3852446954 | 2016 | ENOI | 1 | 82 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1168 | 29.9525 | Public Damage | Disconnect Switch | Public Damage | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 11 | 1323525368 | Yes | ORLEANS | FAIR | 1140 | 2020-02-05 01:00 | 2020-02-05 17:49 | 2020-02-05 20:00 | 12540 | DIS | 23886 | 3851346971 | 2016 | ENOI | 1 | 11 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1172 | 29.9529 | Public Damage | Disconnect Switch | Public Damage | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 1288 | 1323526756 | Yes | ORLEANS | FAIR | 36 | 2020-02-05 02:25 | 2020-02-05 02:56 | 2020-02-05 03:01 | 46368 | DIS | 21967 | 3862946737 | 2024 | ENOI | 1 | 1288 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1138 | 29.9464 | Public Damage | Disconnect Switch | Public Damage | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 2
2020 | 1 | 1323526696 | Yes | ORLEANS | FAIR | 1055 | 2020-02-05 02:25 | 2020-02-05 02:56 | 2020-02-05 20:00 | 1055 | DIS | 23962 | 3843647209 | 2024 | ENOI | 1 | 1 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1197 | 29.9594 | Public Damage | Disconnect Switch | Public Damage | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 6 | 1323534021 | Yes | EAST ORLEANS | RAIN | 87 | 2020-02-05 06:25 | 2020-02-05 07:09 | 2020-02-05 07:52 | 522 | TFUS | 66110 | 43572495525 | 1601 | ENOI | 6 | 6 | LGHT | Lightning | N | weather | -89.9566 | 30.0223 | Lightning | Transformer Fuse | Lightning | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 7 | 1323543759 | Yes | ORLEANS | FAIR | 84 | 2020-02-05 10:24 | 2020-02-05 10:24 | 2020-02-05 11:49 | 588 | TFUS | 79233 | 38298464075 | 2013 | ENOI | 1 | 7 | VLGL | Tree/Limb Growing Inside R.O.W. | N | palm tree branches hitting power lines in rear, trimmed what could get need vegetation to clear lines vege ticket created jmulle2 | -90.1242 | 29.9374 | Vegetation | Transformer Fuse | Vegetation | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 1 | 1323546098 | Yes | EAST ORLEANS | RAIN | 107 | 2020-02-05 11:46 | 2020-02-05 11:46 | 2020-02-05 13:33 | 107 | LFUS | 83983 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | John Domangue cleared vines on pole and refused lateral per OC | -90.0377 | 30.0062 | Vegetation | Line Fuse | Vegetation | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1 | 1323548792 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 12:49 | 2020-02-05 12:49 | 2020-02-05 15:03 | 134 | TFUS | 1483809 | 40334487975 | 1702 | ENOI | 6 | 1 | LGHT | Lightning | N | refused transformer taken out by molding falling across switch | -90.0592 | 30.0025 | Lightning | Transformer Fuse | Lightning | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 198 | 1323558838 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 13:23 | 2020-02-05 15:29 | 2020-02-05 15:37 | 26928 | DIS | 25301 | 4100148012 | 621 | ENOI | 6 | 198 | ECNS | Equipment Failure - Connector Sleeve | N | crew onsite making repairs: Wire burned down due to a failed kearney connection | -90.0384 | 29.9808 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 745 | 1323559097 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 13:23 | 2020-02-05 13:23 | 2020-02-05 15:37 | 73010 | DIS | 25215 | 4103247998 | 621 | ENOI | 6 | 745 | ECNS | Equipment Failure - Connector Sleeve | N | crew picking up wire due to a failed kearney connection | -90.0374 | 29.9803 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 93 | 1323549802 | Yes | EAST ORLEANS | THDR | 95 | 2020-02-05 13:23 | 2020-02-05 14:57 | 2020-02-05 14:58 | 8835 | SBKR | 621 | 4081848423 | 621 | ENOI | 6 | 93 | ECNS | Equipment Failure - Connector Sleeve | N | crew tripped due to down wire due to failed kearney coonection | -90.044 | 29.9922 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1166 | 1323550211 | Yes | EAST ORLEANS | THDR | 73 | 2020-02-05 13:25 | 2020-02-05 14:35 | 2020-02-05 14:37 | 85118 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 1166 | EPRI | Equipment Failure - Primary Conductor | N | crew onsiyte picking up lateral | -90.0021 | 29.9747 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 30 | 1323555868 | Yes | EAST ORLEANS | THDR | 231 | 2020-02-05 13:25 | 2020-02-05 16:31 | 2020-02-05 17:16 | 6930 | LFUS | 82569 | 4192847736 | 2347 | ENOI | 6 | 30 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up wire | -90.0091 | 29.9728 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 119 | 1323549856 | Yes | EAST ORLEANS | THDR | 25 | 2020-02-05 13:25 | 2020-02-05 13:49 | 2020-02-05 13:50 | 2975 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 119 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Crews found balloons on feeder on Florida & Egania | -90.0441 | 29.9921 | Other | Substation Breaker | Other | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 2 | 1323550570 | Yes | ORLEANS | THDR | 168 | 2020-02-05 13:31 | 2020-02-05 13:42 | 2020-02-05 16:19 | 336 | TFUS | 29325 | 39377470287 | 1553 | ENOI | 1 | 2 | LGHT | Lightning | N | weather | -90.0899 | 29.9543 | Lightning | Transformer Fuse | Lightning | 2020-02-05 | DLIN | B | Council District B | Jay Banks | 70113 | 2
2020 | 41 | 1323557039 | Yes | EAST ORLEANS | THDR | 315 | 2020-02-05 13:33 | 2020-02-05 18:38 | 2020-02-05 18:48 | 12915 | LFUS | 31818 | 4164547152 | 2346 | ENOI | 6 | 41 | EPOL | Equipment Failure - Pole | N | refuse latteral | -90.0182 | 29.957 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 25 | 1323557034 | Yes | EAST ORLEANS | THDR | 266 | 2020-02-05 13:33 | 2020-02-05 17:21 | 2020-02-05 17:59 | 6650 | LFUS | 34975 | 4151047208 | 2346 | ENOI | 6 | 25 | LGHT | Lightning | N | refuse b phase | -90.0226 | 29.9585 | Lightning | Line Fuse | Lightning | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 7 | 1323551125 | Yes | ORLEANS | WIND | 45 | 2020-02-05 13:39 | 2020-02-05 13:42 | 2020-02-05 14:24 | 315 | TFUS | 1099405 | 39552488027 | 1703 | ENOI | 1 | 7 | LGHT | Lightning | N | weather | -90.0838 | 30.0031 | Lightning | Transformer Fuse | Lightning | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 3 | 1323551129 | Yes | ORLEANS | WIND | 44 | 2020-02-05 13:40 | 2020-02-05 13:40 | 2020-02-05 14:24 | 132 | TFUS | 76190 | 38463461461 | 1917 | ENOI | 1 | 3 | LGHT | Lightning | N | weather | -90.1191 | 29.9303 | Lightning | Transformer Fuse | Lightning | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 66 | 1323551306 | Yes | EAST ORLEANS | THDR | 297 | 2020-02-05 13:41 | 2020-02-05 17:41 | 2020-02-05 18:38 | 19602 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 66 | LGHT | Lightning | N |  | -89.959 | 30.0234 | Lightning | Line Fuse | Lightning | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 75 | 1323552613 | Yes | ORLEANS | WIND | 112 | 2020-02-05 14:00 | 2020-02-05 14:00 | 2020-02-05 15:52 | 8400 | DIS | 25426 | 3895046772 | 1553 | ENOI | 1 | 75 | EMER | Emergency Switching | N | Taken out for safety to replace burnt cross-arm & repair damaged phase | -90.1036 | 29.9474 | Other | Disconnect Switch | Emergency Switching | 2020-02-05 | DLIN | B | Council District B | Jay Banks | 70125 | 2
2020 | 198 | 1323563948 | Yes | EAST ORLEANS | THDR | 166 | 2020-02-05 14:47 | 2020-02-05 17:14 | 2020-02-05 17:33 | 32868 | DIS | 25215 | 4103247998 | 611 | ENOI | 6 | 198 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up wire | -90.0374 | 29.9803 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-02-05 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 18 | 1323561267 | Yes | EAST ORLEANS | THDR | 200 | 2020-02-05 14:54 | 2020-02-05 15:53 | 2020-02-05 18:14 | 3600 | LFUS | 62285 | 4180447921 | 612 | ENOI | 6 | 18 | LGHT | Lightning | N |  | -90.0131 | 29.9781 | Lightning | Line Fuse | Lightning | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 9 | 1323561274 | Yes | EAST ORLEANS | THDR | 162 | 2020-02-05 15:16 | 2020-02-05 15:16 | 2020-02-05 17:58 | 1458 | TFUS | 73957 | 41821479083 | 612 | ENOI | 6 | 9 | LGHT | Lightning | N | weather | -90.0125 | 29.9777 | Lightning | Transformer Fuse | Lightning | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 10 | 1323571541 | Yes | EAST ORLEANS | THDR | 243 | 2020-02-05 16:24 | 2020-02-05 20:15 | 2020-02-05 20:27 | 2430 | TFUS | 1358844 | 44417501345 | 1205 | ENOI | 6 | 10 | AOTH | Animal - Other (Describe in Remarks Field) | N | rat took out b phase lateral in cubicle 82- refused ok-cust back on | -89.9296 | 30.0381 | Animal | Transformer Fuse | Animal | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 5 | 1323574976 | Yes | EAST ORLEANS | THDR | 389 | 2020-02-05 16:39 | 2020-02-05 17:34 | 2020-02-05 23:08 | 1945 | TFUS | 1543254 | 43598495566 | 1601 | ENOI | 6 | 5 | EPOL | Equipment Failure - Pole | N | crew replacing pole | -89.9557 | 30.0224 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 75 | 1323576846 | Yes | ORLEANS | THDR | 212 | 2020-02-05 17:03 | 2020-02-05 17:13 | 2020-02-05 20:35 | 15900 | LFUS | 27869 | 3847346112 | 1917 | ENOI | 1 | 75 | LGHT | Lightning | N | weather | -90.1188 | 29.9292 | Lightning | Line Fuse | Lightning | 2020-02-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 4 | 1323577065 | Yes | EAST ORLEANS | THDR | 70 | 2020-02-05 17:07 | 2020-02-05 17:10 | 2020-02-05 18:17 | 280 | TFUS | 73153 | 41749477220 | 2325 | ENOI | 6 | 4 | LGHT | Lightning | N | refused B and C phase taken out by bad weather | -90.0149 | 29.9726 | Lightning | Transformer Fuse | Lightning | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 306 | 1323587389 | Yes | EAST ORLEANS | THDR | 156 | 2020-02-05 20:29 | 2020-02-05 22:04 | 2020-02-05 23:05 | 47736 | DIS | D01643 | 4356849760 | 1601 | ENOI | 6 | 306 | EMER | Emergency Switching | N | taken out for safety to replace burnt pole | -89.9557 | 30.0225 | Other | Disconnect Switch | Emergency Switching | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 50 | 1323588929 | Yes | EAST ORLEANS | THDR | 140 | 2020-02-05 20:45 | 2020-02-05 20:45 | 2020-02-05 23:05 | 7000 | DIS | 23818 | 4352749766 | 1608 | ENOI | 6 | 50 | EMER | Emergency Switching | N | crew to replace pole | -89.9557 | 30.0225 | Other | Disconnect Switch | Emergency Switching | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 32 | 1323593781 | Yes | EAST ORLEANS | FAIR | 100 | 2020-02-05 23:06 | 2020-02-05 23:59 | 2020-02-06 00:46 | 3200 | LFUS | 27190 | 4450051090 | 2213 | ENOI | 6 | 32 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-05 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 11 | 1323610473 | Yes | ORLEANS | WIND | 114 | 2020-02-06 07:06 | 2020-02-06 07:06 | 2020-02-06 09:00 | 1254 | TFUS | 74399 | 40386478720 | 1709 | ENOI | 1 | 11 | LGHT | Lightning | N | refused transformer taken out by weather | -90.0577 | 29.9772 | Lightning | Transformer Fuse | Lightning | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70116 | 2
2020 | 55 | 1323610634 | Yes | EAST ORLEANS | THDR | 232 | 2020-02-06 07:15 | 2020-02-06 10:20 | 2020-02-06 11:07 | 12760 | LFUS | 23476 | 4333250949 | 2223 | ENOI | 6 | 55 | LGHT | Lightning | N | weasther | -89.9637 | 30.0609 | Lightning | Line Fuse | Lightning | 2020-02-06 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 8 | 1323613484 | Yes | ORLEANS | RAIN | 89 | 2020-02-06 08:19 | 2020-02-06 09:08 | 2020-02-06 09:48 | 712 | TFUS | 60606 | 39493474594 | 907 | ENOI | 1 | 8 | ESEC | Secondary/Service Conductor | N | service wire failure caused transformer to fault. | -90.0861 | 29.9661 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-06 | DLIN | B | Council District B | Jay Banks | 70119 | 2
2020 | 16 | 1323614486 | Yes | EAST ORLEANS | RAIN | 123 | 2020-02-06 08:43 | 2020-02-06 08:43 | 2020-02-06 10:46 | 1968 | TFUS | 1155554 | 40524474979 | 2347 | ENOI | 6 | 16 | VOHL | Overhanging Limb | N | removed palm limbs off of transformer reuse ok customer back in lights | -90.0536 | 29.9667 | Vegetation | Transformer Fuse | Vegetation | 2020-02-06 | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 14 | 1323616190 | Yes | ORLEANS | RAIN | 53 | 2020-02-06 09:21 | 2020-02-06 09:30 | 2020-02-06 10:14 | 742 | TFUS | 641930 | 40302484935 | 1708 | ENOI | 1 | 14 | VOHL | Overhanging Limb | N | limb fell across bushing and riser on transformer. per 310 | -90.0602 | 29.9942 | Vegetation | Transformer Fuse | Vegetation | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 50 | 1323623756 | Yes | EAST ORLEANS | FAIR | 219 | 2020-02-06 11:12 | 2020-02-06 13:34 | 2020-02-06 14:51 | 10950 | LFUS | 21126 | 4120947834 | 621 | ENOI | 6 | 50 | ECNS | Equipment Failure - Connector Sleeve | N | riser on switch broke, repaired, customers back on | -90.0319 | 29.9758 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 122 | 1323630435 | Yes | EAST ORLEANS | THDR | 121 | 2020-02-06 13:50 | 2020-02-06 15:06 | 2020-02-06 15:51 | 14762 | LFUS | 21152 | 4051147776 | 623 | ENOI | 6 | 122 | SCHD | Scheduled Interruption | N |  | -90.0538 | 29.9744 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 20 | 1323636140 | Yes | EAST ORLEANS | WIND | 253 | 2020-02-06 16:42 | 2020-02-06 19:53 | 2020-02-06 20:55 | 5060 | LFUS | 75618 | 4081847779 | 622 | ENOI | 6 | 20 | VINE | Vine Growing into Line | N | vine pole..clear..refused lateral.. | -90.0441 | 29.9744 | Vegetation | Line Fuse | Vegetation | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 48 | 1323636868 | Yes | EAST ORLEANS | WIND | 451 | 2020-02-06 17:20 | 2020-02-06 23:15 | 2020-02-07 00:51 | 21648 | LFUS | 23476 | 4333250949 | 2223 | ENOI | 6 | 48 | EFSW | Equipment Failure - Fuse Switch | N | fuse switch repaired | -89.9637 | 30.0609 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-06 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 1 | 1323640712 | Yes | EAST ORLEANS | WIND | 148 | 2020-02-06 19:32 | 2020-02-06 19:40 | 2020-02-06 22:00 | 148 | SERV | SERVICE | 41140473283 | 2347 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Had to replace bad hot leg on the pole. Back in lights. Will need a crew to cut limbs off of a palm tree. The branches are brushing against the primary. 2068575 | -90.0342 | 29.9619 | Equipment Failure | Service Conductor | Equipment Failure | 2020-02-06 | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 8 | 1323642003 | Yes | EAST ORLEANS | WIND | 433 | 2020-02-06 20:33 | 2020-02-06 20:37 | 2020-02-07 03:46 | 3464 | TFUS | 3010148 | 43306495734 | 1611 | ENOI | 6 | 8 | EFLK | Equipment Failure - Fuse Link | N | changed fuse barrel on trans.. | -89.9649 | 30.023 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-06 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 66 | 1323642921 | Yes | EAST ORLEANS | WIND | 578 | 2020-02-06 20:52 | 2020-02-07 03:02 | 2020-02-07 06:30 | 38148 | LFUS | 36787 | 4369551079 | 2217 | ENOI | 6 | 66 | ETRD | Equipment Failure - Transformer | N | Crew on site replacing transformer | -89.9522 | 30.0643 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-06 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 241 | 1323644227 | Yes | EAST ORLEANS | WIND | 47 | 2020-02-06 21:29 | 2020-02-06 21:50 | 2020-02-06 22:16 | 11327 | RCLR | 10123 | 4137849331 | 1001 | ENOI | 6 | 241 | UNKN | Inspected Unknown | N | high winds moved through area at time of lockout | -90.026 | 30.0169 | Other | Recloser | Other | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 64 | 1323649733 | Yes | ORLEANS | WIND | 80 | 2020-02-06 21:48 | 2020-02-06 22:24 | 2020-02-06 23:08 | 5120 | LFUS | 28068 | 3960648669 | 1703 | ENOI | 1 | 64 | EPRI | Equipment Failure - Primary Conductor | N | high wind refused okay | -90.0821 | 29.9993 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1 | 1323653145 | Yes | EAST ORLEANS | WIND | 210 | 2020-02-06 23:58 | 2020-02-06 23:58 | 2020-02-07 03:28 | 210 | LFUS | 61838 | 4107349839 | 1001 | ENOI | 6 | 1 | EFSW | Equipment Failure - Fuse Switch | N | refused lateral 61838 b/c phases only customer back on | -90.0354 | 30.031 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-06 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 974 | 1323655936 | Yes | EAST ORLEANS | WIND | 154 | 2020-02-07 00:01 | 2020-02-07 02:14 | 2020-02-07 02:35 | 149996 | RCLR | 38677 | 4119947436 | 2347 | ENOI | 6 | 974 | EARM | Equipment Failure - Crossarm | N | insulator off arm at location | -90.034 | 29.9673 | Equipment Failure | Recloser | Equipment Failure | 2020-02-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 45 | 1323657975 | Yes | EAST ORLEANS | WIND | 558 | 2020-02-07 00:01 | 2020-02-07 09:34 | 2020-02-07 09:19 | 25110 | DIS | D01653 | 4116547515 | 2347 | ENOI | 6 | 45 | EARM | Equipment Failure - Crossarm | N | crew to replace insulator and crossarm | -90.0333 | 29.9672 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-02-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 427 | 1323653581 | Yes | EAST ORLEANS | WIND | 91 | 2020-02-07 00:02 | 2020-02-07 01:31 | 2020-02-07 01:33 | 38857 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 427 | EARM | Equipment Failure - Crossarm | N | Recloser was locked out; See recloser case | -90.0021 | 29.9747 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-02-07 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 48 | 1323655644 | Yes | EAST ORLEANS | WIND | 114 | 2020-02-07 00:51 | 2020-02-07 01:40 | 2020-02-07 02:45 | 5472 | LFUS | 52377 | 4268250430 | 2215 | ENOI | 6 | 48 | ESEC | Secondary/Service Conductor | N |  | -89.9844 | 30.0466 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-07 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 222 | 1323655478 | Yes | EAST ORLEANS | WIND | 21 | 2020-02-07 01:34 | 2020-02-07 01:52 | 2020-02-07 01:55 | 4662 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 222 | EARM | Equipment Failure - Crossarm | N |  | -90.0021 | 29.9747 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-02-07 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 26 | 1323662339 | Yes | EAST ORLEANS | THDR | 115 | 2020-02-07 05:49 | 2020-02-07 05:56 | 2020-02-07 07:44 | 2990 | LFUS | 37094 | 4106547707 | 611 | ENOI | 6 | 26 | EARR | Equipment Failure - Arrestor | N | failed lightning arrestor on lateral/cleared/refused lateral | -90.0364 | 29.9723 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 279 | 1323663056 | Yes | EAST ORLEANS | THDR | 78 | 2020-02-07 06:33 | 2020-02-07 07:44 | 2020-02-07 07:51 | 21762 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 279 | EARR | Equipment Failure - Arrestor | N | blown arrestor | -90.0337 | 29.9718 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 10 | 1323664900 | Yes | ORLEANS | FAIR | 73 | 2020-02-07 07:41 | 2020-02-07 07:41 | 2020-02-07 08:55 | 730 | TFUS | 1585375 | 39461462505 | 1924 | ENOI | 1 | 10 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | no comments | -90.0875 | 29.9329 | Other | Transformer Fuse | Other | 2020-02-07 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 124 | 1323665502 | Yes | EAST ORLEANS | FAIR | 116 | 2020-02-07 07:55 | 2020-02-07 09:17 | 2020-02-07 09:51 | 14384 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 124 | EFLK | Equipment Failure - Fuse Link | N | crew restored lateral | -90.0337 | 29.9718 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 57 | 1323673353 | Yes | EAST ORLEANS | FAIR | 124 | 2020-02-07 11:46 | 2020-02-07 12:37 | 2020-02-07 13:50 | 7068 | LFUS | 37150 | 40855477822 | 622 | ENOI | 6 | 57 | ECNS | Equipment Failure - Connector Sleeve | N | made new kearney connection repair at trans. | -90.0431 | 29.9745 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 12 | 1323710068 | Yes | ORLEANS | FAIR | 163 | 2020-02-08 09:52 | 2020-02-08 09:52 | 2020-02-08 12:35 | 1956 | TFUS | 59131 | 39328458518 | 1923 | ENOI | 1 | 12 | ECON | Equipment Failure - Connector / Sleeve | N | there is a lead on the transformer heating up will return after hours to replace lead. per 310 | -90.092 | 29.9219 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-08 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 140 | 1323713292 | Yes | ORLEANS | FAIR | 106 | 2020-02-08 12:03 | 2020-02-08 13:40 | 2020-02-08 13:49 | 14840 | LFUS | 37734 | 4029548586 | 1708 | ENOI | 1 | 140 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | b phase only | -90.0603 | 29.9969 | Other | Line Fuse | Other | 2020-02-08 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 11 | 1323716666 | Yes | EAST ORLEANS | FAIR | 214 | 2020-02-08 14:04 | 2020-02-08 14:04 | 2020-02-08 17:38 | 2354 | TFUS | 1417733 | 40381486047 | 1708 | ENOI | 6 | 11 | EARR | Equipment Failure - Arrestor | N | refuse b phase ..cleared arrester | -90.0577 | 29.9973 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-08 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 3 | 1323734811 | Yes | ORLEANS | FAIR | 124 | 2020-02-09 15:14 | 2020-02-09 15:14 | 2020-02-09 17:18 | 372 | TFUS | 32116 | 39340459980 | 2147 | ENOI | 1 | 3 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons. refused ok RELATED TO TKT# 1323734811 (AKS) | -90.0915 | 29.9259 | Other | Transformer Fuse | Other | 2020-02-09 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 1 | 1323764163 | Yes | EAST ORLEANS | WIND | 79 | 2020-02-10 08:14 | 2020-02-10 08:14 | 2020-02-10 09:33 | 79 | LFUS | 27269 | 41375485531 | 616 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | B and C Phase fuse were blown at the lateral switch. Inspected line and determined that #6 copper phases blew together with wind. Made cust contact. Back in lights. | -90.0263 | 29.9955 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-10 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 97 | 1323767376 | Yes | EAST ORLEANS | FAIR | 112 | 2020-02-10 09:48 | 2020-02-10 11:29 | 2020-02-10 11:41 | 10864 | LFUS | 26127 | 4386451333 | 2223 | ENOI | 6 | 97 | SCHD | Scheduled Interruption | N | Contractor had outage for reliability work | -89.9466 | 30.0712 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-10 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 42 | 1323799758 | Yes | EAST ORLEANS | FAIR | 86 | 2020-02-10 20:14 | 2020-02-10 20:29 | 2020-02-10 21:40 | 3612 | LFUS | 17586 | 4099049317 | 508 | ENOI | 6 | 42 | EMER | Emergency Switching | N | crew straighting a pole | -90.0383 | 30.0167 | Other | Line Fuse | Emergency Switching | 2020-02-10 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 115 | 1323805002 | Yes | ORLEANS | FAIR | 52 | 2020-02-11 00:20 | 2020-02-11 01:06 | 2020-02-11 01:12 | 5980 | LFUS | F05219 | 3960746184 | 2146 | ENOI | 1 | 115 | SCHD | Scheduled Interruption | N | crew onsite transferring pole | -90.083 | 29.9309 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-11 | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 1917 | 1323805621 | Yes | ORLEANS | FAIR | 26 | 2020-02-11 00:47 | 2020-02-11 01:10 | 2020-02-11 01:13 | 49842 | SBKR | 2146 | 4012946121 | 2146 | ENOI | 1 | 1917 | EMER | Emergency Switching | N | dropped out for the crew , whencrew was in the process of closing in a laterial the switch came off of the arm and was being supported by the switch stick. | -90.0665 | 29.9291 | Other | Substation Breaker | Emergency Switching | 2020-02-11 | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 17 | 1323822707 | Yes | ORLEANS | FAIR | 19 | 2020-02-11 12:12 | 2020-02-11 12:12 | 2020-02-11 12:31 | 323 | TFUS | 642509 | 39383459492 | 2147 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | scheduled outage | -90.0902 | 29.9247 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-11 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 5 | 1323823115 | Yes | EAST ORLEANS | FAIR | 242 | 2020-02-11 12:19 | 2020-02-11 14:52 | 2020-02-11 16:21 | 1694 | XFMR | 1049527 | 4184247070 | 2346 | ENOI | 6 | 5 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.0122 | 29.9546 | Equipment Failure | Transformer | Equipment Failure | 2020-02-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 107 | 1323849876 | Yes | EAST ORLEANS | FAIR | 120 | 2020-02-12 08:30 | 2020-02-12 09:22 | 2020-02-12 10:30 | 12840 | LFUS | 21798 | 4382851374 | 2223 | ENOI | 6 | 107 | SCHD | Scheduled Interruption | N |  | -89.9477 | 30.0724 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 127 | 1323889600 | Yes | EAST ORLEANS | FAIR | 89 | 2020-02-12 15:05 | 2020-02-12 16:02 | 2020-02-12 16:35 | 11303 | LFUS | 27886 | 4082247647 | 622 | ENOI | 6 | 127 | UNKN | Inspected Unknown | N | Refused C phase at sw# 27886--Inspect unknown | -90.0441 | 29.9707 | Other | Line Fuse | Other | 2020-02-12 | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 14 | 1323899529 | Yes | ORLEANS | FAIR | 203 | 2020-02-12 17:49 | 2020-02-12 21:10 | 2020-02-12 21:12 | 2842 | TFUS | 72350 | 38822482342 | 903 | ENOI | 1 | 14 | ECNS | Equipment Failure - Connector Sleeve | N | picked up span of primary that fell due to the hot tap connection | -90.107 | 29.9875 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-12 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 26 | 1323911490 | Yes | ALGIERS ELEC ONLY | FAIR | 277 | 2020-02-13 00:46 | 2020-02-13 02:05 | 2020-02-13 05:23 | 7202 | TFUS | BY78432 | 4057647060 | W0715 | ENOI | 81 | 26 | VINE | Vine Growing into Line | N | serviceman removed vines from transformer (pwd) | -90.0521 | 29.9548 | Vegetation | Transformer Fuse | Vegetation | 2020-02-13 | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 23 | 1323924228 | Yes | EAST ORLEANS | FAIR | 55 | 2020-02-13 10:05 | 2020-02-13 10:50 | 2020-02-13 11:00 | 1265 | LFUS | 21736 | 4186649358 | 1612 | ENOI | 6 | 23 | SCHD | Scheduled Interruption | N | crew got lateral back in | -90.0105 | 30.0175 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-13 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 31 | 1323930361 | Yes | EAST ORLEANS | FAIR | 550 | 2020-02-13 12:51 | 2020-02-13 20:32 | 2020-02-13 22:01 | 17050 | LFUS | 25289 | 4290350439 | 2216 | ENOI | 6 | 31 | ETRD | Equipment Failure - Transformer | N | crew to replace underground pot | -89.9774 | 30.0469 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-13 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 4 | 1323938290 | Yes | EAST ORLEANS | FAIR | 89 | 2020-02-13 16:31 | 2020-02-13 16:31 | 2020-02-13 18:00 | 356 | TFUS | 32883 | 41762479118 | 612 | ENOI | 6 | 4 | VINE | Vine Growing into Line | N | dead vines..clear | -90.0144 | 29.9778 | Vegetation | Transformer Fuse | Vegetation | 2020-02-13 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 7 | 1323939896 | Yes | ORLEANS | FAIR | 117 | 2020-02-13 17:34 | 2020-02-13 17:35 | 2020-02-13 19:31 | 819 | XFMR | 1349264 | 38517477512 | 2026 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N | crew to change transformer | -90.1169 | 29.9743 | Equipment Failure | Transformer | Equipment Failure | 2020-02-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 114 | 1323981833 | Yes | ORLEANS | FAIR | 105 | 2020-02-14 22:09 | 2020-02-14 22:13 | 2020-02-14 23:54 | 11970 | LFUS | 21458 | 3906145893 | 1923 | ENOI | 1 | 114 | UNKN | Inspected Unknown | N | refused okk | -90.1004 | 29.9231 | Other | Line Fuse | Other | 2020-02-14 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 269 | 1323986713 | Yes | EAST ORLEANS | FAIR | 215 | 2020-02-15 05:12 | 2020-02-15 06:51 | 2020-02-15 08:47 | 57835 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 269 | EELB | Equipment Failure - Elbow | N | crew replaced bad elbow, customers back on now | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-15 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1 | 1323988573 | Yes | ORLEANS | FAIR | 193 | 2020-02-15 07:58 | 2020-02-15 07:58 | 2020-02-15 11:11 | 193 | SECO | METER | 39437478935 | 912 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | cust AMI mtr was opened AMOC doesnt work weekends and DOC doesnt have control to close mtr so changed mtr to mtr#8180313 sn-34644421 r-00000 KC | -90.0878 | 29.978 | Other | Secondary Conductor | Other | 2020-02-15 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 2
2020 | 23 | 1323990854 | Yes | EAST ORLEANS | FAIR | 492 | 2020-02-15 09:08 | 2020-02-15 16:19 | 2020-02-15 17:20 | 11316 | LFUS | 21120 | 4107947975 | 621 | ENOI | 6 | 23 | CORR | Corrosion | N | repaired broke jumper | -90.0358 | 29.9798 | Other | Line Fuse | Other | 2020-02-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 1 | 1324005232 | Yes | ORLEANS | FAIR | 23 | 2020-02-15 13:02 | 2020-02-15 13:07 | 2020-02-15 13:25 | 23 | SECO | METER | 39473478021 | 912 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | 3128 dumaine AMI mtr had open indication AMOC doesnt work weekends and DOC doesnt have control to close mtrs changed to mtr#8180311 sn-57104979 r-00000 | -90.0866 | 29.9755 | Other | Secondary Conductor | Other | 2020-02-15 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 2
2020 | 16 | 1324017985 | Yes | ORLEANS | FAIR | 154 | 2020-02-15 18:35 | 2020-02-15 20:11 | 2020-02-15 21:09 | 2464 | XFMR | 1375593 | 3988249289 | 510 | ENOI | 1 | 16 | HECO | Human Error - Company (Describe in Remarks Field) | N | trans. 1375593 was out taken out by bell contractor ont on scene rclr was in | -90.0733 | 30.0162 | Human Error | Transformer | Human Error | 2020-02-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 4 | 1324041039 | Yes | ORLEANS | FAIR | 264 | 2020-02-16 17:23 | 2020-02-16 17:53 | 2020-02-16 21:47 | 1056 | XFMR | 549347 | 38505459883 | 1914 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | bad xfmr, changed xfmr | -90.1178 | 29.9259 | Equipment Failure | Transformer | Equipment Failure | 2020-02-16 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 2
2020 | 238 | 1324044207 | Yes | ORLEANS | FAIR | 320 | 2020-02-16 20:03 | 2020-02-17 00:56 | 2020-02-17 01:23 | 76160 | DIS | 23320 | 38432474479 | 2022 | ENOI | 1 | 238 | VHCL | Vehicle | N | Crew on site replacing broken pole PID IN PROGRESS RELATED TO TKT# 1324040006 (AKS) | -90.1197 | 29.966 | Public Damage | Disconnect Switch | Public Damage | 2020-02-16 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 3 | 1324059083 | Yes | EAST ORLEANS | FAIR | 336 | 2020-02-17 11:24 | 2020-02-17 11:24 | 2020-02-17 17:00 | 1008 | TFUS | 62400 | 42950505451 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | Crew opened in order to safely do required work............. | -89.9759 | 30.0498 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-17 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 10 | 1324063576 | Yes | EAST ORLEANS | FAIR | 50 | 2020-02-17 14:10 | 2020-02-17 14:10 | 2020-02-17 15:00 | 500 | TFUS | 61817 | 40999477699 | 611 | ENOI | 6 | 10 | SCHD | Scheduled Interruption | N | contractor are transfering pole they have pot out | -90.0384 | 29.9742 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 12 | 1324081149 | Yes | EAST ORLEANS | FAIR | 53 | 2020-02-18 08:08 | 2020-02-18 08:08 | 2020-02-18 09:01 | 636 | XFMR | 633552 | 40981476969 | 611 | ENOI | 6 | 12 | SCHD | Scheduled Interruption | N | crew onsite removing old transformer | -90.0389 | 29.9722 | Scheduled Interruption | Transformer | Scheduled Interruption | 2020-02-18 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 1 | 1324109171 | Yes | ALGIERS ELEC ONLY | FAIR | 86 | 2020-02-18 14:34 | 2020-02-18 14:40 | 2020-02-18 16:00 | 86 | SERV | SERVICE COND | 4212046002 | W1726 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N | Replaced connection on service line............PC | -90.0036 | 29.9252 | Equipment Failure | Service Conductor | Equipment Failure | 2020-02-18 | DLIN | C | Council District C | Kristin Palmer | 70131 | 2
2020 | 1 | 1324132625 | Yes | EAST ORLEANS | FAIR | 352 | 2020-02-18 17:33 | 2020-02-18 17:33 | 2020-02-18 23:25 | 352 | SERV | SERVICE | 42512499834 | 2216 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | repaired | -89.99 | 30.0345 | Equipment Failure | Service Conductor | Equipment Failure | 2020-02-18 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 21 | 1324132510 | Yes | ALGIERS ELEC ONLY | FAIR | 41 | 2020-02-18 20:35 | 2020-02-18 20:35 | 2020-02-18 21:16 | 861 | TFUS | BY149697 | 4115346444 | W1725 | ENOI | 81 | 21 | SCHD | Scheduled Interruption | N | opened transforemr to replace cut out (pwd) | -90.0342 | 29.9376 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-18 | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 8 | 1324142737 | Yes | ORLEANS | FAIR | 133 | 2020-02-19 02:44 | 2020-02-19 04:34 | 2020-02-19 04:58 | 1064 | TFUS | 21729 | 38502489222 | 410 | ENOI | 1 | 8 | EMER | Emergency Switching | N | Out for safety of crew to replace pole | -90.117 | 30.0065 | Other | Transformer Fuse | Emergency Switching | 2020-02-19 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 11 | 1324158085 | Yes | EAST ORLEANS | FAIR | 402 | 2020-02-19 10:44 | 2020-02-19 10:44 | 2020-02-19 17:26 | 4422 | DIS | 36981 | 4542049869 | 1202 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Taken out for safety of Transmission crews to repair damaged shield wire from the night before. All customers were notified | -89.8981 | 30.0303 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-02-19 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 3 | 1324170082 | Yes | EAST ORLEANS | FAIR | 15 | 2020-02-19 14:15 | 2020-02-19 14:15 | 2020-02-19 14:30 | 45 | TFUS | 62400 | 42950505451 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | crew is onsite | -89.976 | 30.0498 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-19 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 9 | 1324187155 | Yes | ALGIERS ELEC ONLY | FAIR | 311 | 2020-02-20 00:19 | 2020-02-20 03:16 | 2020-02-20 05:30 | 2799 | XFMR | BY98542 | 4159646652 | W0723 | ENOI | 81 | 9 | ETRD | Equipment Failure - Transformer | N | bad transformer at location. | -90.02 | 29.9432 | Equipment Failure | Transformer | Equipment Failure | 2020-02-20 | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 14 | 1324202736 | Yes | EAST ORLEANS | RAIN | 103 | 2020-02-20 09:15 | 2020-02-20 09:15 | 2020-02-20 10:58 | 1442 | LFUS | 21695 | 4038148637 | 1708 | ENOI | 6 | 14 | EFLK | Equipment Failure - Fuse Link | N | blown fuse on transformer and lateral taken out by bad weather | -90.0579 | 29.9982 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1462 | 1324238968 | Yes | ORLEANS | RAIN | 32 | 2020-02-20 13:17 | 2020-02-20 13:46 | 2020-02-20 13:49 | 46784 | SBKR | 1702 | 4024148726 | 1702 | ENOI | 1 | 1462 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Serviceman found a piece of molding fell onto primary, cleared object & feeder restored okay | -90.0621 | 30.0007 | Other | Substation Breaker | Other | 2020-02-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 94 | 1324247481 | Yes | ALGIERS ELEC ONLY | THDR | 103 | 2020-02-20 13:57 | 2020-02-20 14:51 | 2020-02-20 15:40 | 9682 | RCLR | 1136 | 4182146253 | W0722 | ENOI | 81 | 94 | LGHT | Lightning | N | lighting took out center phase recloser | -90.0129 | 29.9323 | Lightning | Recloser | Lightning | 2020-02-20 | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 7 | 1324294885 | Yes | EAST ORLEANS | WIND | 72 | 2020-02-20 19:11 | 2020-02-20 19:11 | 2020-02-20 20:23 | 504 | TFUS | 57875 | 40375486483 | 1708 | ENOI | 6 | 7 | EFSW | Equipment Failure - Fuse Switch | N | c phase fuse burnt in half..refused | -90.058 | 29.9985 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 116 | 1324305126 | Yes | ALGIERS ELEC ONLY | WIND | 133 | 2020-02-20 21:00 | 2020-02-20 22:33 | 2020-02-20 23:13 | 15428 | LFUS | 34312 | 4265245351 | W1712 | ENOI | 81 | 116 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | hot line clamp burnt off stirrup, replaced and repaired, cust lights restored | -89.9868 | 29.9072 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-20 | DLIN | C | Council District C | Kristin Palmer | 70131 | 2
2020 | 50 | 1324308301 | Yes | ORLEANS | WIND | 104 | 2020-02-20 21:46 | 2020-02-20 21:57 | 2020-02-20 23:30 | 5200 | LFUS | 44646 | 3853148813 | 410 | ENOI | 1 | 50 | EFLK | Equipment Failure - Fuse Link | N | Refused latteral | -90.116 | 30.0036 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-20 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 10 | 1324327115 | Yes | ORLEANS | FAIR | 94 | 2020-02-21 06:37 | 2020-02-21 07:32 | 2020-02-21 08:11 | 940 | TFUS | 51666 | 39674493122 | 509 | ENOI | 1 | 10 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0799 | 30.017 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-02-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 16 | 1324336355 | Yes | EAST ORLEANS | FAIR | 37 | 2020-02-21 11:44 | 2020-02-21 11:44 | 2020-02-21 12:21 | 592 | TFUS | 54971 | 40370486325 | 1708 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0581 | 29.9981 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 268 | 1324358592 | Yes | EAST ORLEANS | FAIR | 329 | 2020-02-21 23:46 | 2020-02-22 05:14 | 2020-02-22 05:15 | 88172 | DIS | 24625 | 4063748581 | 1710 | ENOI | 6 | 268 | EARM | Equipment Failure - Crossarm | N | broken cross arm crew is enroute to replace arm | -90.0497 | 29.9965 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-02-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 84 | 1324375554 | Yes | ORLEANS | FAIR | 126 | 2020-02-22 16:51 | 2020-02-22 17:12 | 2020-02-22 18:57 | 10584 | LFUS | 21671 | 3979148836 | 1704 | ENOI | 1 | 84 | ETRD | Equipment Failure - Transformer | N | crew replaced xfmr | -90.0762 | 30.0038 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-22 | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 7 | 1324387775 | Yes | EAST ORLEANS | FAIR | 242 | 2020-02-23 07:01 | 2020-02-23 09:14 | 2020-02-23 11:03 | 1694 | TFUS | 527839 | 42532504275 | 2215 | ENOI | 6 | 7 | ASQL | Animal - Squirrel | N | refused pot; lights back on | -89.989 | 30.0469 | Animal | Transformer Fuse | Animal | 2020-02-23 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 12 | 1324391305 | Yes | EAST ORLEANS | FAIR | 639 | 2020-02-23 09:46 | 2020-02-23 09:49 | 2020-02-23 20:25 | 7668 | XFMR | 1373043 | 44468499346 | 1601 | ENOI | 6 | 12 | ETRD | Equipment Failure - Transformer | N |  | -89.9282 | 30.0326 | Equipment Failure | Transformer | Equipment Failure | 2020-02-23 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 6 | 1324396947 | Yes | EAST ORLEANS | FAIR | 15 | 2020-02-23 14:30 | 2020-02-23 14:30 | 2020-02-23 14:45 | 90 | TFUS | 73309 | 41856476262 | 2325 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0114 | 29.97 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-23 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 28 | 1324398683 | Yes | ORLEANS | FAIR | 78 | 2020-02-23 15:27 | 2020-02-23 15:42 | 2020-02-23 16:45 | 2184 | LFUS | 21435 | 3883945809 | 1921 | ENOI | 1 | 28 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | removed balloons off of line; a phase blown KC | -90.1073 | 29.9209 | Other | Line Fuse | Other | 2020-02-23 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 123 | 1324415315 | Yes | ORLEANS | FAIR | 38 | 2020-02-24 06:15 | 2020-02-24 06:40 | 2020-02-24 06:53 | 4674 | LFUS | 27615 | 3972747795 | 615 | ENOI | 1 | 123 | SCHD | Scheduled Interruption | N | crew changing out pole | -90.0786 | 29.9753 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-24 | DLIN | D | Council District D | Jared Brossett | 70119 | 2
2020 | 9 | 1324416282 | Yes | ORLEANS | FAIR | 199 | 2020-02-24 07:42 | 2020-02-24 07:42 | 2020-02-24 11:01 | 1791 | TFUS | 1000615 | 39768462508 | 2135 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | repairs to secondary | -90.078 | 29.9328 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-24 | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 11 | 1324416799 | Yes | EAST ORLEANS | FAIR | 78 | 2020-02-24 08:16 | 2020-02-24 08:19 | 2020-02-24 09:34 | 858 | TFUS | 71154 | 40600474196 | 623 | ENOI | 6 | 11 | ASQL | Animal - Squirrel | N | animal took out transformer re fused transformer and lights back on squirrel got into secondary | -90.0511 | 29.9648 | Animal | Transformer Fuse | Animal | 2020-02-24 | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 98 | 1324448213 | Yes | ORLEANS | FAIR | 274 | 2020-02-24 15:26 | 2020-02-24 19:25 | 2020-02-24 20:00 | 26852 | LFUS | F05614 | 39978464632 | 2137 | ENOI | 1 | 98 | EARM | Equipment Failure - Crossarm | N | crossarms replaced | -90.0713 | 29.9386 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-24 | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 118 | 1324456985 | Yes | EAST ORLEANS | FAIR | 28 | 2020-02-24 18:53 | 2020-02-24 19:15 | 2020-02-24 19:21 | 3304 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 118 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Serviceman patrolled feeder the next morning & found balloons on line at Florida & Gorden Sts. Removed okay | -90.0441 | 29.9921 | Other | Substation Breaker | Other | 2020-02-24 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 14 | 1324463884 | Yes | ORLEANS | FAIR | 17 | 2020-02-24 23:34 | 2020-02-24 23:35 | 2020-02-24 23:51 | 238 | LFUS | 21578 | 3886948465 | 904 | ENOI | 1 | 14 | EARM | Equipment Failure - Crossarm | N |  | -90.1055 | 29.9938 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-24 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 58 | 1324464499 | Yes | EAST ORLEANS | FAIR | 195 | 2020-02-25 00:26 | 2020-02-25 03:14 | 2020-02-25 03:41 | 11310 | LFUS | 24738 | 4346351051 | 2223 | ENOI | 6 | 58 | VHCL | Vehicle | N | car hit pole RELATED TO AMFM 1324463382 | -89.9595 | 30.0636 | Public Damage | Line Fuse | Public Damage | 2020-02-25 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 17 | 1324472835 | Yes | ORLEANS | FAIR | 1511 | 2020-02-25 07:19 | 2020-02-26 04:05 | 2020-02-26 08:30 | 25687 | XFMR | 75060 | 40339473868 | 614 | ENOI | 1 | 17 | ETRD | Equipment Failure - Transformer | N | crew to replace transformer | -90.0595 | 29.9638 | Equipment Failure | Transformer | Equipment Failure | 2020-02-25 | DLIN | C | Council District C | Kristin Palmer | 70116 | 2
2020 | 102 | 1324519542 | Yes | ALGIERS ELEC ONLY | FAIR | 50 | 2020-02-26 06:25 | 2020-02-26 07:10 | 2020-02-26 07:15 | 5100 | RCLR | 5070 | 4119546688 | W1725 | ENOI | 81 | 102 | LGHT | Lightning | N | closed back in per I. Caruthers..........PC | -90.0326 | 29.9444 | Lightning | Recloser | Lightning | 2020-02-26 | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 55 | 1324520081 | Yes | EAST ORLEANS | FAIR | 165 | 2020-02-26 06:40 | 2020-02-26 08:48 | 2020-02-26 09:26 | 9075 | LFUS | 21423 | 4262649350 | 1604 | ENOI | 6 | 55 | EFSW | Equipment Failure - Fuse Switch | N | repared riser and switch, customer back in | -89.9863 | 30.0172 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-26 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 96 | 1324527282 | Yes | ORLEANS | FAIR | 184 | 2020-02-26 10:26 | 2020-02-26 11:58 | 2020-02-26 13:30 | 17664 | OPEN | 3908445887 | 3908445887 | 1917 | ENOI | 1 | 96 | SCHD | Scheduled Interruption | N | Contract crew replacing rotten pole | -90.0996 | 29.9229 | Scheduled Interruption | Open | Scheduled Interruption | 2020-02-26 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 142 | 1324538266 | Yes | ORLEANS | FAIR | 197 | 2020-02-26 13:36 | 2020-02-26 16:43 | 2020-02-26 16:53 | 27974 | LFUS | 27985 | 3909645896 | 1917 | ENOI | 1 | 142 | SCHD | Scheduled Interruption | N | Contract crew replacing pole at the intersection of Chestnut and Milan | -90.0993 | 29.9232 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-26 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 70 | 1324538399 | Yes | ORLEANS | FAIR | 197 | 2020-02-26 13:36 | 2020-02-26 16:15 | 2020-02-26 16:53 | 13790 | LFUS | 27759 | 3909745885 | 1917 | ENOI | 1 | 70 | SCHD | Scheduled Interruption | N | Contract crew replacing pole at the intersection of Chestnut and Milan | -90.0993 | 29.9229 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-26 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 68 | 1324566317 | Yes | ORLEANS | FAIR | 21 | 2020-02-26 22:45 | 2020-02-26 22:51 | 2020-02-26 23:06 | 1428 | LFUS | 33137 | 3866247573 | 2026 | ENOI | 1 | 68 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1125 | 29.9694 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-02-26 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 8 | 1324616546 | Yes | ORLEANS | FAIR | 56 | 2020-02-27 09:05 | 2020-02-27 09:05 | 2020-02-27 10:01 | 448 | TFUS | 60601 | 39064458650 | 1923 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | scheduled outage | -90.1004 | 29.9224 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-27 | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 6 | 1324616559 | Yes | EAST ORLEANS | FAIR | 184 | 2020-02-27 09:05 | 2020-02-27 09:05 | 2020-02-27 12:09 | 1104 | TFUS | 1417774 | 41010475194 | 611 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0382 | 29.9672 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-27 | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 11 | 1324618796 | Yes | EAST ORLEANS | FAIR | 152 | 2020-02-27 09:48 | 2020-02-27 09:48 | 2020-02-27 12:20 | 1672 | TFUS | 60528 | 41062476942 | 611 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0363 | 29.972 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-27 | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 1 | 1324635782 | Yes | ORLEANS | FAIR | 274 | 2020-02-27 17:46 | 2020-02-27 17:46 | 2020-02-27 22:21 | 274 | XFMR | 1087045 | 3914247399 | 912 | ENOI | 1 | 1 | ETRD | Equipment Failure - Transformer | N | crew changed out xfmr | -90.0972 | 29.9645 | Equipment Failure | Transformer | Equipment Failure | 2020-02-27 | DLIN | B | Council District B | Jay Banks | 70119 | 2
2020 | 78 | 1324642076 | Yes | EAST ORLEANS | FAIR | 104 | 2020-02-28 01:56 | 2020-02-28 02:30 | 2020-02-28 03:40 | 8112 | LFUS | 27321-F | 4235149906 | 2211 | ENOI | 6 | 78 | UNKN | Inspected Unknown | N | c phase blown; refused and held | -97.0758 | 27.9066 | Other | Line Fuse | Other | 2020-02-28 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 581 | 1324644436 | Yes | EAST ORLEANS | FAIR | 345 | 2020-02-28 03:10 | 2020-02-28 08:35 | 2020-02-28 08:55 | 200445 | SWIT | 25680 | 4211049707 | 1610 | ENOI | 6 | 581 | EPRI | Equipment Failure - Primary Conductor | N | Bad cable bet sw. # 25680 & # 86561. Picked up cust. from sw. # 25185 | -97.0758 | 27.9066 | Equipment Failure | Switch | Equipment Failure | 2020-02-28 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 11 | 1324654003 | Yes | EAST ORLEANS | FAIR | 1757 | 2020-02-28 03:10 | 2020-02-28 03:10 | 2020-02-29 08:27 | 19327 | SWIT | 27120 | 4230549755 | 1610 | ENOI | 6 | 11 | EPRI | Equipment Failure - Primary Conductor | N | Isolated bad cable bet sw, # 25680 & 86561 | -97.0758 | 27.9066 | Equipment Failure | Switch | Equipment Failure | 2020-02-28 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 144 | 1324656883 | Yes | ORLEANS | FAIR | 140 | 2020-02-28 13:09 | 2020-02-28 14:43 | 2020-02-28 15:29 | 20160 | LFUS | 86144 | 3898146691 | 1925 | ENOI | 1 | 144 | EARM | Equipment Failure - Crossarm | N | broken cross arm replaced | -90.1027 | 29.9451 | Equipment Failure | Line Fuse | Equipment Failure | 2020-02-28 | DLIN | B | Council District B | Jay Banks | 70125 | 2
2020 | 4 | 1324676386 | Yes | EAST ORLEANS | FAIR | 21 | 2020-02-28 21:04 | 2020-02-28 21:04 | 2020-02-28 21:25 | 84 | TFUS | 60105 | 42939493496 | 1604 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9765 | 30.0171 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-02-28 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1 | 1324683772 | Yes | EAST ORLEANS | FAIR | 289 | 2020-02-29 05:28 | 2020-02-29 07:06 | 2020-02-29 10:17 | 289 | SECO | SERVICE | 40861490898 | 501 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.0422 | 30.0105 | Equipment Failure | Secondary Conductor | Equipment Failure | 2020-02-29 | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 3 | 1324727607 | Yes | ORLEANS | FAIR | 184 | 2020-03-01 08:15 | 2020-03-01 08:15 | 2020-03-01 11:19 | 552 | LFUS | 22199 | 4008346242 | 2142 | ENOI | 1 | 3 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.068 | 29.9324 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-01 | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 9 | 1324727347 | Yes | ORLEANS | FAIR | 144 | 2020-03-01 08:36 | 2020-03-01 08:40 | 2020-03-01 11:00 | 1296 | TFUS | 1546252 | 38696482632 | 903 | ENOI | 1 | 9 | EARR | Equipment Failure - Arrestor | N | changed arrestor | -90.1112 | 29.9884 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-01 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 60 | 1324759313 | Yes | ORLEANS | FAIR | 61 | 2020-03-02 04:29 | 2020-03-02 04:53 | 2020-03-02 05:30 | 3660 | LFUS | 37635 | 3979848210 | 1705 | ENOI | 1 | 60 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0763 | 29.9865 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-02 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 121 | 1324763424 | Yes | ORLEANS | FAIR | 64 | 2020-03-02 08:57 | 2020-03-02 09:40 | 2020-03-02 10:01 | 7744 | LFUS | 17521 | 3845449177 | 411 | ENOI | 1 | 121 | SCHD | Scheduled Interruption | N | back on | -90.1183 | 30.0136 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-02 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 28 | 1324786656 | Yes | ORLEANS | FAIR | 91 | 2020-03-02 14:48 | 2020-03-02 15:13 | 2020-03-02 16:19 | 2548 | LFUS | 37635 | 3979848210 | 1705 | ENOI | 1 | 28 | EFLK | Equipment Failure - Fuse Link | N | latera fuse blown, refused. everything ok. | -90.0763 | 29.9865 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-02 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 77 | 1324812511 | Yes | EAST ORLEANS | FAIR | 125 | 2020-03-03 09:15 | 2020-03-03 09:47 | 2020-03-03 11:20 | 9625 | LFUS | 37101 | 4159049958 | 1010 | ENOI | 6 | 77 | SCHD | Scheduled Interruption | N | crew completed work | -90.0193 | 30.0341 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-03 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 25 | 1324838882 | Yes | EAST ORLEANS | FAIR | 66 | 2020-03-03 21:18 | 2020-03-03 21:33 | 2020-03-03 22:24 | 1650 | LFUS | 31765 | 4178547304 | 2346 | ENOI | 6 | 25 | EARM | Equipment Failure - Crossarm | N | crew to change | -90.0138 | 29.9611 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-03 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 67 | 1324839571 | Yes | ORLEANS | FAIR | 191 | 2020-03-03 22:19 | 2020-03-04 00:04 | 2020-03-04 01:30 | 12797 | LFUS | 28115 | 3865446377 | 1927 | ENOI | 1 | 67 | EARM | Equipment Failure - Crossarm | N | changed x arms | -90.1129 | 29.9365 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-03 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 7 | 1324840355 | Yes | EAST ORLEANS | FAIR | 322 | 2020-03-03 23:38 | 2020-03-04 03:48 | 2020-03-04 05:00 | 2254 | XFMR | 77496 | 42469500417 | 1605 | ENOI | 6 | 7 | ETRD | Equipment Failure - Transformer | N | CREW CHANGED | -89.9911 | 30.0362 | Equipment Failure | Transformer | Equipment Failure | 2020-03-03 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 2835 | 1324909780 | Yes | ORLEANS | FAIR | 6 | 2020-03-04 11:10 | 2020-03-04 11:16 | 2020-03-04 11:16 | 17010 | SBKR | 2147 | 4012946119 | 2147 | ENOI | 1 | 2835 | VINE | Vine Growing into Line | N | cause has been confirmed that "Root Cause" was vines on bayonet & primary x-arm | -90.0851 | 29.9198 | Vegetation | Substation Breaker | Vegetation | 2020-03-04 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 25 | 1324949281 | Yes | EAST ORLEANS | FAIR | 104 | 2020-03-04 11:53 | 2020-03-04 12:44 | 2020-03-04 13:37 | 2600 | LFUS | 50003 | 4068547762 | 622 | ENOI | 6 | 25 | EFLK | Equipment Failure - Fuse Link | N | when refused a phase lateral 50003 lights came back on at this location | -90.0485 | 29.974 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-04 | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 2835 | 1324968746 | Yes | ORLEANS | FAIR | 6 | 2020-03-04 12:20 | 2020-03-04 12:25 | 2020-03-04 12:26 | 17010 | SBKR | 2147 | 4012946119 | 2147 | ENOI | 1 | 2835 | EMER | Emergency Switching | N | crossarm at location on fire de-energized to put fire out Chippewa at Pleasant | -90.0851 | 29.9198 | Other | Substation Breaker | Emergency Switching | 2020-03-04 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 69 | 1324974438 | Yes | EAST ORLEANS | FAIR | 36 | 2020-03-04 13:00 | 2020-03-04 13:19 | 2020-03-04 13:36 | 2484 | LFUS | 27936 | 4357949598 | 1601 | ENOI | 6 | 69 | EARM | Equipment Failure - Crossarm | N |  | -89.9565 | 30.0236 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-04 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 8 | 1324984786 | Yes | EAST ORLEANS | FAIR | 194 | 2020-03-04 13:20 | 2020-03-04 15:33 | 2020-03-04 16:34 | 1552 | LFUS | 27757 | 4126947853 | 621 | ENOI | 6 | 8 | EPRI | Equipment Failure - Primary Conductor | N | wire down | -90.0297 | 29.9764 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-04 | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 37 | 1324999233 | Yes | ORLEANS | RAIN | 157 | 2020-03-04 15:13 | 2020-03-04 16:02 | 2020-03-04 17:51 | 5809 | TFUS | 62327 | 39423465450 | 1925 | ENOI | 1 | 37 | EFSW | Equipment Failure - Fuse Switch | N | refused lfus at magnolia and first | -90.0887 | 29.9409 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-04 | DLIN | B | Council District B | Jay Banks | 70113 | 3
2020 | 4 | 1325037811 | Yes | EAST ORLEANS | RAIN | 77 | 2020-03-04 18:38 | 2020-03-04 18:38 | 2020-03-04 19:55 | 308 | LFUS | 36617 | 41796477686 | 2325 | ENOI | 6 | 4 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused single phase lat..wether | -90.0133 | 29.9738 | Other | Line Fuse | Other | 2020-03-04 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 18 | 1325039518 | Yes | EAST ORLEANS | RAIN | 86 | 2020-03-04 18:55 | 2020-03-04 18:55 | 2020-03-04 20:21 | 1548 | LFUS | 62285 | 41776478254 | 612 | ENOI | 6 | 18 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused lat..same as choctaw..wether | -90.014 | 29.9755 | Other | Line Fuse | Other | 2020-03-04 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 425 | 1325077072 | Yes | ORLEANS | FAIR | 368 | 2020-03-05 01:07 | 2020-03-05 07:13 | 2020-03-05 07:15 | 156400 | DIS | 14963 | 3844849081 | 410 | ENOI | 1 | 425 | VHCL | Vehicle | N | VehicleHit a Pole Crew Replaced AT&T Pole | -90.1185 | 30.011 | Public Damage | Disconnect Switch | Public Damage | 2020-03-05 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 1 | 1325083907 | Yes | ALGIERS ELEC ONLY | THDR | 149 | 2020-03-05 06:21 | 2020-03-05 06:21 | 2020-03-05 08:50 | 149 | TFUS | C29425 | 4380545475 | W1715 | ENOI | 81 | 1 | LGHT | Lightning | N | bad weather took out svc talk with cust svc is back on | -89.9503 | 29.9102 | Lightning | Transformer Fuse | Lightning | 2020-03-05 | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 17 | 1325088970 | Yes | ORLEANS | FAIR | 508 | 2020-03-05 07:55 | 2020-03-05 07:55 | 2020-03-05 16:23 | 8653 | DIS | 25353 | 3937145945 | 2147 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | crew on site installing new conductors | -90.0906 | 29.9245 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-03-05 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 46 | 1325089224 | Yes | ORLEANS | FAIR | 513 | 2020-03-05 07:55 | 2020-03-05 11:53 | 2020-03-05 16:28 | 23598 | DIS | 24025 | 3942345968 | 2147 | ENOI | 1 | 46 | SCHD | Scheduled Interruption | N | crew on site installing new conductors | -90.0889 | 29.9251 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-03-05 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 13 | 1325095835 | Yes | EAST ORLEANS | FAIR | 133 | 2020-03-05 09:37 | 2020-03-05 09:54 | 2020-03-05 11:50 | 1729 | TFUS | 26061 | 40975490857 | 501 | ENOI | 6 | 13 | EARM | Equipment Failure - Crossarm | N | RELI WORK | -90.0388 | 30.0103 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-05 | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 27 | 1325104705 | Yes | ORLEANS | FAIR | 71 | 2020-03-05 11:15 | 2020-03-05 11:25 | 2020-03-05 12:26 | 1917 | LFUS | 37993 | 3945647879 | 912 | ENOI | 1 | 27 | SCHD | Scheduled Interruption | N | RELI WORK COMPLETE | -90.0873 | 29.9776 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-05 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 23 | 1325120864 | Yes | EAST ORLEANS | FAIR | 95 | 2020-03-05 15:48 | 2020-03-05 17:02 | 2020-03-05 17:23 | 2185 | LFUS | LFUS | 00000000000 | 2211 | ENOI | 6 | 23 | UNKN | Inspected Unknown | N | refused u/g lat..checked trans ..holding |  |  | Other | Line Fuse | Other | 2020-03-05 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 26 | 1325141261 | Yes | EAST ORLEANS | FAIR | 163 | 2020-03-06 09:02 | 2020-03-06 09:28 | 2020-03-06 11:45 | 4238 | LFUS | 17532 | 4097349099 | 501 | ENOI | 6 | 26 | SCHD | Scheduled Interruption | N | Crew On Site Working | -90.0389 | 30.0107 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-06 | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 10 | 1325141994 | Yes | ORLEANS | FAIR | 74 | 2020-03-06 09:27 | 2020-03-06 09:27 | 2020-03-06 10:41 | 740 | TFUS | 1060584 | 39925462472 | 2137 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.073 | 29.9326 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-06 | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 2 | 1325150169 | Yes | ALGIERS ELEC ONLY | FAIR | 363 | 2020-03-06 13:02 | 2020-03-06 13:02 | 2020-03-06 19:05 | 726 | TFUS | 1016 | 4197946327 | W0726 | ENOI | 81 | 2 | VHCL | Vehicle | N | Crew to pick up wire in which was snagged down stream of this dedvice,...............................PC | -90.008 | 29.9343 | Public Damage | Transformer Fuse | Public Damage | 2020-03-06 | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 12 | 1325174086 | Yes | EAST ORLEANS | FAIR | 143 | 2020-03-07 08:07 | 2020-03-07 08:07 | 2020-03-07 10:30 | 1716 | TFUS | 55984 | 41031480720 | 621 | ENOI | 6 | 12 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | talked to chris boweers need to get transformer at location they have a 50 kv two blocks away feeding this house and voltage is dropping a little so gonna get a job drawn up to hang new pot and cut epoxilators in secondary | -90.0372 | 29.9826 | Other | Transformer Fuse | Other | 2020-03-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 7 | 1325174097 | Yes | ALGIERS ELEC ONLY | FAIR | 150 | 2020-03-07 08:08 | 2020-03-07 09:05 | 2020-03-07 10:38 | 1050 | TFUS | BY88991 | 4215745928 | W1726 | ENOI | 81 | 7 | ASQL | Animal - Squirrel | N | squirrel took out transformer refuse customer back in lights | -90.0023 | 29.9231 | Animal | Transformer Fuse | Animal | 2020-03-07 | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 172 | 1325175370 | Yes | ORLEANS | FAIR | 53 | 2020-03-07 08:47 | 2020-03-07 08:58 | 2020-03-07 09:40 | 9460 | OPEN | 3863645932 | 3863645932 | 1917 | ENOI | 1 | 172 | EMER | Emergency Switching | N | opened for safety of crew to epair broke x am for clearance | -90.1137 | 29.9243 | Other | Open | Emergency Switching | 2020-03-07 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 222 | 1325175289 | Yes | ORLEANS | FAIR | 205 | 2020-03-07 08:47 | 2020-03-07 10:40 | 2020-03-07 12:12 | 45510 | DIS | 23482 | 3876045869 | 1917 | ENOI | 1 | 222 | EMER | Emergency Switching | N | opened for safety of crew to epair broke x am for clearance | -90.1099 | 29.9226 | Other | Disconnect Switch | Emergency Switching | 2020-03-07 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 42 | 1325194517 | Yes | EAST ORLEANS | FAIR | 119 | 2020-03-08 10:22 | 2020-03-08 10:44 | 2020-03-08 12:21 | 4998 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 42 | ASQL | Animal - Squirrel | N | squrriel took out overhead lateral switch refused lateral road out underground lights back on and holdin n good voltage | -89.9561 | 30.0595 | Animal | Line Fuse | Animal | 2020-03-08 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 37 | 1325195154 | Yes | ORLEANS | FAIR | 347 | 2020-03-08 11:26 | 2020-03-08 16:27 | 2020-03-08 17:13 | 12839 | DIS | 24830 | 4009147967 | 615 | ENOI | 1 | 37 | VHCL | Vehicle | N | Crew on site working PID IN PROGRESS KC RELATED TO TKT# 1325193683 (AKS) | -90.0672 | 29.9799 | Public Damage | Disconnect Switch | Public Damage | 2020-03-08 | DLIN | D | Council District D | Jared Brossett | 70119 | 3
2020 | 20 | 1325196222 | Yes | ALGIERS ELEC ONLY | FAIR | 141 | 2020-03-08 12:32 | 2020-03-08 14:08 | 2020-03-08 14:53 | 2820 | LFUS | 5587 | 4283245716 | W1714 | ENOI | 81 | 20 | ASQL | Animal - Squirrel | N | squirrel took out lateral customers are back in lights | -89.9812 | 29.9172 | Animal | Line Fuse | Animal | 2020-03-08 | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 237 | 1325210218 | Yes | EAST ORLEANS | FAIR | 361 | 2020-03-09 08:10 | 2020-03-09 13:23 | 2020-03-09 14:11 | 85557 | LFUS | 17998 | 4158049987 | 1010 | ENOI | 6 | 237 | SCHD | Scheduled Interruption | N | Scheduled Interruption; 267-683-0737 | -90.0195 | 30.0348 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-09 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 1398 | 1325215886 | Yes | EAST ORLEANS | FAIR | 21 | 2020-03-09 11:21 | 2020-03-09 11:42 | 2020-03-09 11:42 | 29358 | SBKR | 2217 | 4334250776 | 2217 | ENOI | 6 | 1398 | VHCL | Vehicle | N | pole hit at morrison and gannon RELATED TO TKT# 1325216450 (AKS0 | -89.9634 | 30.056 | Public Damage | Substation Breaker | Public Damage | 2020-03-09 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 1 | 1325216450 | Yes | EAST ORLEANS | FAIR | 698 | 2020-03-09 11:21 | 2020-03-09 18:18 | 2020-03-09 22:59 | 698 | DIS | 27384 | 4359850869 | 2217 | ENOI | 6 | 1 | VHCL | Vehicle | N | pole hit at gannon and morrison by vehicle RELATED TO TKT# 1325215886 (AKS) | -89.955 | 30.0581 | Public Damage | Disconnect Switch | Public Damage | 2020-03-09 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 6 | 1325216942 | Yes | ORLEANS | FAIR | 141 | 2020-03-09 11:40 | 2020-03-09 11:40 | 2020-03-09 14:01 | 846 | TFUS | 77907 | 38636459349 | 1927 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Outage for crane to lift generator at 1311 Jefferson Ave | -90.1138 | 29.9243 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-09 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 74 | 1325244985 | Yes | EAST ORLEANS | FAIR | 378 | 2020-03-10 07:32 | 2020-03-10 07:53 | 2020-03-10 13:50 | 27972 | LFUS | 27692 | 4373349583 | 1601 | ENOI | 6 | 74 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | contractor dug into line and knocked out later; crew replaced xfmr | -89.9517 | 30.023 | Public Damage | Line Fuse | Public Damage | 2020-03-10 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 24 | 1325246985 | Yes | ORLEANS | FAIR | 120 | 2020-03-10 09:00 | 2020-03-10 09:00 | 2020-03-10 11:00 | 2880 | TFUS | 1002541 | 39724459733 | 2147 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | Scheduled Interruption; 601-910-1304 | -90.0794 | 29.9251 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-10 | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 81 | 1325251365 | Yes | EAST ORLEANS | FAIR | 369 | 2020-03-10 10:22 | 2020-03-10 15:29 | 2020-03-10 16:31 | 29889 | LFUS | 32305 | 4164647339 | 2346 | ENOI | 6 | 81 | VHCL | Vehicle | N | car broke pole | -90.0184 | 29.9622 | Public Damage | Line Fuse | Public Damage | 2020-03-10 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 19 | 1325273476 | Yes | EAST ORLEANS | FAIR | 334 | 2020-03-10 17:26 | 2020-03-10 22:30 | 2020-03-10 23:00 | 6346 | TFUS | 619075 | 4212449674 | 1610 | ENOI | 6 | 19 | EPRI | Equipment Failure - Primary Conductor | N | bad cable, switched out | -97.0758 | 27.9066 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 53 | 1325275264 | Yes | EAST ORLEANS | FAIR | 202 | 2020-03-10 18:25 | 2020-03-10 21:20 | 2020-03-10 21:47 | 10706 | LFUS | 27864 | 4079547423 | 623 | ENOI | 6 | 53 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused c phase..moulding on phase..clear | -90.0451 | 29.9648 | Other | Line Fuse | Other | 2020-03-10 | DLIN | C | Council District C | Kristin Palmer | 70117 | 3
2020 | 5 | 1325277031 | Yes | EAST ORLEANS | FAIR | 184 | 2020-03-10 19:10 | 2020-03-10 19:11 | 2020-03-10 22:14 | 920 | TFUS | 75064 | 41670475701 | 2325 | ENOI | 6 | 5 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused trans..installed animal guard | -90.0175 | 29.9685 | Other | Transformer Fuse | Other | 2020-03-10 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 41 | 1325282371 | Yes | ALGIERS ELEC ONLY | FAIR | 272 | 2020-03-11 01:43 | 2020-03-11 06:20 | 2020-03-11 06:15 | 11152 | LFUS | 5916 | 4177346429 | W0726 | ENOI | 81 | 41 | ECNS | Equipment Failure - Connector Sleeve | N |  | -90.0146 | 29.9372 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-11 | DLIN | C | Council District C | Kristin Palmer | 70114 | 3
2020 | 66 | 1325285495 | Yes | ORLEANS | FAIR | 190 | 2020-03-11 07:00 | 2020-03-11 07:05 | 2020-03-11 10:10 | 12540 | OPEN | 3971445987 | 3971445987 | 2147 | ENOI | 1 | 66 | SCHD | Scheduled Interruption | N | back to normal | -90.0797 | 29.9255 | Scheduled Interruption | Open | Scheduled Interruption | 2020-03-11 | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 45 | 1325284832 | Yes | ORLEANS | FAIR | 20 | 2020-03-11 07:10 | 2020-03-11 10:08 | 2020-03-11 07:30 | 900 | LFUS | 33186 | 3975145935 | 2147 | ENOI | 1 | 45 | SCHD | Scheduled Interruption | N | crew has an ouitage setup until 10:00 am | -90.0787 | 29.924 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-11 | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 123 | 1325285548 | Yes | ORLEANS | FAIR | 108 | 2020-03-11 07:58 | 2020-03-11 08:47 | 2020-03-11 09:47 | 13284 | LFUS | 38033 | 3893046944 | 2015 | ENOI | 1 | 123 | EARM | Equipment Failure - Crossarm | N | changed crossarm. refused lateral. per 310 | -90.1043 | 29.9522 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-11 | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 237 | 1325285714 | Yes | EAST ORLEANS | FAIR | 344 | 2020-03-11 08:07 | 2020-03-11 13:22 | 2020-03-11 13:51 | 81528 | LFUS | 17998 | 4158049987 | 1010 | ENOI | 6 | 237 | SCHD | Scheduled Interruption | N | crew onsite | -90.0195 | 30.0348 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-11 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 3 | 1325286019 | Yes | EAST ORLEANS | FAIR | 211 | 2020-03-11 08:15 | 2020-03-11 08:15 | 2020-03-11 11:46 | 633 | TFUS | 1242332 | 42902506464 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | crew has an outage set up for today | -89.9774 | 30.0527 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-11 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 15 | 1325285990 | Yes | EAST ORLEANS | FAIR | 420 | 2020-03-11 08:15 | 2020-03-11 08:15 | 2020-03-11 15:15 | 6300 | LFUS | 27847 | 4291250653 | 2215 | ENOI | 6 | 15 | SCHD | Scheduled Interruption | N | crew has an outage set for today | -89.977 | 30.0529 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-11 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 4 | 1325286004 | Yes | EAST ORLEANS | FAIR | 421 | 2020-03-11 08:15 | 2020-03-11 08:54 | 2020-03-11 15:16 | 1684 | TFUS | 1499229 | 42923506630 | 2215 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | crew has an outage setup for today | -89.9767 | 30.0531 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-11 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 7 | 1325289126 | Yes | EAST ORLEANS | FAIR | 188 | 2020-03-11 09:33 | 2020-03-11 10:30 | 2020-03-11 12:41 | 1316 | XFMR | 20698 | 40362493030 | 506 | ENOI | 6 | 7 | ETRD | Equipment Failure - Transformer | N | crew to change | -90.0582 | 30.0164 | Equipment Failure | Transformer | Equipment Failure | 2020-03-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 1 | 1325292073 | Yes | EAST ORLEANS | FAIR | 103 | 2020-03-11 10:17 | 2020-03-11 10:17 | 2020-03-11 12:00 | 103 | TFUS | 1213434 | 41139478965 | 621 | ENOI | 6 | 1 | SCHD | Scheduled Interruption | N | Schedule outage. Contractors notified Sewage and Waterboard. | -90.0338 | 29.9775 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-11 | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 8 | 1325298095 | Yes | ORLEANS | FAIR | 111 | 2020-03-11 13:10 | 2020-03-11 13:14 | 2020-03-11 15:01 | 888 | TFUS | 73749 | 39960488721 | 1704 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | crew has trans. out for repairs | -90.0709 | 30.0047 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 7 | 1325298558 | Yes | ORLEANS | FAIR | 105 | 2020-03-11 13:21 | 2020-03-11 13:25 | 2020-03-11 15:06 | 735 | TFUS | 56899 | 39535483021 | 627 | ENOI | 1 | 7 | EARR | Equipment Failure - Arrestor | N | blown arrestor cleared and refused. per 310 | -90.0845 | 29.9892 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-11 | DLIN | D | Council District D | Jared Brossett | 70119 | 3
2020 | 414 | 1325315642 | Yes | EAST ORLEANS | FAIR | 142 | 2020-03-12 06:23 | 2020-03-12 09:24 | 2020-03-12 08:45 | 58788 | VFI | 27422 | 4366350629 | 2213 | ENOI | 6 | 414 | VHCL | Vehicle | N | Vehicle damaged cub. #504 at I-10 service rd & paris rd | -97.0758 | 27.9066 | Public Damage | Vacuum Fault Interrupter | Public Damage | 2020-03-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 9 | 1325319467 | Yes | EAST ORLEANS | FAIR | 457 | 2020-03-12 07:45 | 2020-03-12 07:45 | 2020-03-12 15:22 | 4113 | TFUS | 1490486 | 46388537189 | 1202 | ENOI | 6 | 9 | ECON | Equipment Failure - Connector / Sleeve | N | bad connections on transformer leads/changed out connections good voltage | -89.8658 | 30.136 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-12 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 15 | 1325319637 | Yes | EAST ORLEANS | FAIR | 294 | 2020-03-12 07:52 | 2020-03-12 07:52 | 2020-03-12 12:46 | 4410 | LFUS | 27847 | 4291250653 | 2215 | ENOI | 6 | 15 | SCHD | Scheduled Interruption | N | work completed | -89.977 | 30.0529 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-03-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 63 | 1325327742 | Yes | ORLEANS | FAIR | 130 | 2020-03-12 11:49 | 2020-03-12 13:19 | 2020-03-12 13:59 | 8190 | LFUS | 21302 | 3972447286 | 1511 | ENOI | 1 | 63 | EARR | Equipment Failure - Arrestor | N | refused lateral 21302 b and c phase | -90.0788 | 29.9612 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-12 | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 18 | 1325327776 | Yes | ORLEANS | FAIR | 183 | 2020-03-12 11:53 | 2020-03-12 12:44 | 2020-03-12 14:56 | 3294 | TFUS | 1001093 | 39848461464 | 2132 | ENOI | 1 | 18 | VLGL | Tree/Limb Growing Inside R.O.W. | N | need vegetation ticket made for tree under transformer bank, tested, refused ok KC | -90.0755 | 29.9298 | Vegetation | Transformer Fuse | Vegetation | 2020-03-12 | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 6 | 1325363398 | Yes | ORLEANS | FAIR | 36 | 2020-03-13 12:14 | 2020-03-13 12:17 | 2020-03-13 12:50 | 216 | TFUS | 73716 | 38972467670 | 1553 | ENOI | 1 | 6 | AOTH | Animal - Other (Describe in Remarks Field) | N | refused tf squirel got across tf fuse | -90.1029 | 29.9472 | Animal | Transformer Fuse | Animal | 2020-03-13 | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 2 | 1325378067 | Yes | ORLEANS | FAIR | 666 | 2020-03-14 04:27 | 2020-03-14 14:24 | 2020-03-14 15:33 | 1332 | TFUS | 73662 | 40283491759 | 1701 | ENOI | 1 | 2 | VHCL | Vehicle | N | KC | -90.0605 | 30.013 | Public Damage | Transformer Fuse | Public Damage | 2020-03-14 | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 1 | 1325381288 | Yes | EAST ORLEANS | FAIR | 110 | 2020-03-14 10:03 | 2020-03-14 10:03 | 2020-03-14 11:53 | 110 | LFUS | 17169 | 41375485531 | 616 | ENOI | 6 | 1 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused lateral | -90.025 | 29.997 | Other | Line Fuse | Other | 2020-03-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 1450 | 1325389344 | Yes | ORLEANS | FAIR | 137 | 2020-03-14 20:06 | 2020-03-14 20:06 | 2020-03-14 22:23 | 198650 | SBKR | 1914 | 3909545669 | 1914 | ENOI | 1 | 1450 | ECNS | Equipment Failure - Connector Sleeve | N | Fdr trip/closed & A phase was single phasing due to blown jumper that burned pri dn. @ Arrabella & Camp Sts | -90.0993 | 29.9169 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-03-14 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 4 | 1325394235 | Yes | ORLEANS | FAIR | 252 | 2020-03-14 20:46 | 2020-03-14 22:55 | 2020-03-15 00:58 | 1008 | DIS | 23922 | 3846845651 | 1927 | ENOI | 1 | 4 | ECNS | Equipment Failure - Connector Sleeve | N | primary down and jumper burned @ Arrabella & Camp Sts | -90.1192 | 29.9167 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-03-14 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 188 | 1325394639 | Yes | ORLEANS | FAIR | 34 | 2020-03-14 22:24 | 2020-03-14 22:57 | 2020-03-14 22:58 | 11656 | DIS | 23640 | 3850345854 | 1914 | ENOI | 1 | 188 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up and phase on ground | -90.118 | 29.9223 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-03-14 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 82 | 1325394070 | Yes | ORLEANS | FAIR | 149 | 2020-03-14 22:24 | 2020-03-14 22:48 | 2020-03-15 00:53 | 12218 | DIS | 23638 | 3852145850 | 1914 | ENOI | 1 | 82 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up and phase on ground | -90.1174 | 29.9222 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-03-14 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 64 | 1325394344 | Yes | ORLEANS | FAIR | 151 | 2020-03-14 22:27 | 2020-03-14 22:52 | 2020-03-15 00:58 | 9664 | LFUS | 55660 | 3855645645 | 1927 | ENOI | 1 | 64 | EPRI | Equipment Failure - Primary Conductor | N | phase down and jumper burned | -90.1162 | 29.9165 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-14 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 3 | 1325402050 | Yes | ORLEANS | FAIR | 398 | 2020-03-15 06:45 | 2020-03-15 06:45 | 2020-03-15 13:23 | 1194 | XFMR | 510962 | 38488459675 | 1914 | ENOI | 1 | 3 | ETRD | Equipment Failure - Transformer | N |  | -90.1184 | 29.9253 | Equipment Failure | Transformer | Equipment Failure | 2020-03-15 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 22 | 1325406620 | Yes | ALGIERS ELEC ONLY | FAIR | 76 | 2020-03-15 11:02 | 2020-03-15 12:09 | 2020-03-15 12:18 | 1672 | SBKR | W1725 | 4284345924 | W1725 | ENOI | 81 | 22 | VHCL | Vehicle | N | vehicle broke pole, Chgd PID to No, related to #1325409607 (DGault) | -89.981 | 29.9228 | Public Damage | Substation Breaker | Public Damage | 2020-03-15 | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 852 | 1325409607 | Yes | ALGIERS ELEC ONLY | FAIR | 571 | 2020-03-15 11:02 | 2020-03-15 19:50 | 2020-03-15 20:33 | 152002 | DIS | 5135 | 4249246144 | W1725 | ENOI | 81 | 852 | VHCL | Vehicle | N | vehicle hi pole | -89.9919 | 29.929 | Public Damage | Disconnect Switch | Public Damage | 2020-03-15 | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 19 | 1325408219 | Yes | EAST ORLEANS | FAIR | 104 | 2020-03-15 12:00 | 2020-03-15 12:00 | 2020-03-15 13:44 | 1976 | TFUS | 60581 | 40900477062 | 622 | ENOI | 6 | 19 | VHCL | Vehicle | N | car hit pole | -90.0416 | 29.9724 | Public Damage | Transformer Fuse | Public Damage | 2020-03-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 5 | 1325457267 | Yes | ORLEANS | FAIR | 70 | 2020-03-17 07:03 | 2020-03-17 07:29 | 2020-03-17 08:13 | 350 | TFUS | 595357 | 3977848904 | 1704 | ENOI | 1 | 5 | EFSW | Equipment Failure - Fuse Switch | N | Just a transformer | -90.0768 | 30.0058 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-17 | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 5 | 1325459780 | Yes | ORLEANS | FAIR | 55 | 2020-03-17 09:05 | 2020-03-17 09:05 | 2020-03-17 10:01 | 275 | TFUS | 64925 | 40233479668 | 627 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | crew replacing cross arm | -90.0625 | 29.9798 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-17 | DLIN | D | Council District D | Jared Brossett | 70119 | 3
2020 | 5 | 1325467795 | Yes | EAST ORLEANS | FAIR | 86 | 2020-03-17 13:10 | 2020-03-17 13:54 | 2020-03-17 14:36 | 430 | TFUS | 1048649 | 44560510150 | 2213 | ENOI | 6 | 5 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | Contractors changing meters left breaker off NO PID | -89.9248 | 30.0623 | Public Damage | Transformer Fuse | Public Damage | 2020-03-17 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 70 | 1325512369 | Yes | ORLEANS | FAIR | 114 | 2020-03-18 13:44 | 2020-03-18 15:06 | 2020-03-18 15:38 | 7980 | LFUS | 92823 | 3906745843 | 1923 | ENOI | 1 | 70 | ASQL | Animal - Squirrel | N | CLEARED BIRD INSTALLED BIRD GUARD | -90.1003 | 29.9218 | Animal | Line Fuse | Animal | 2020-03-18 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 21 | 1325526619 | Yes | ORLEANS | FAIR | 18 | 2020-03-18 23:10 | 2020-03-18 23:10 | 2020-03-18 23:28 | 378 | TFUS | 729628 | 39681459752 | 2146 | ENOI | 1 | 21 | ECNS | Equipment Failure - Connector Sleeve | N | jumper repaired on xfmr | -90.0807 | 29.9253 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-18 | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 24 | 1325530057 | Yes | EAST ORLEANS | FAIR | 260 | 2020-03-19 04:16 | 2020-03-19 06:36 | 2020-03-19 08:36 | 6240 | TFUS | 3005286 | 42615493129 | 1604 | ENOI | 6 | 24 | VINE | Vine Growing into Line | N | cleared vines and refused transformer 300528 | -89.9867 | 30.0162 | Vegetation | Transformer Fuse | Vegetation | 2020-03-19 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 55 | 1325562835 | Yes | EAST ORLEANS | FAIR | 367 | 2020-03-19 22:20 | 2020-03-20 01:00 | 2020-03-20 04:28 | 20185 | LFUS | 25217 | 4240450217 | 2211 | ENOI | 6 | 55 | EELB | Equipment Failure - Elbow | N | repaired | -89.9932 | 30.0411 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-19 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 31 | 1325563182 | NO | ORLEANS | FAIR | 164 | 2020-03-19 22:22 | 2020-03-20 00:29 | 2020-03-20 01:06 | 5084 | SUBN | 1543 | 3950646993 | 1543 | ENOI | 1 | 31 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0859 | 29.9532 | Equipment Failure | Substation | Equipment Failure | 2020-03-19 | DSUB | B | Council District B | Jay Banks | 70113 | 3
2020 | 1 | 1325563310 | NO | ORLEANS | FAIR | 164 | 2020-03-19 22:22 | 2020-03-19 22:22 | 2020-03-20 01:06 | 164 | SUBN | 1515 | 3952146981 | 1515 | ENOI | 1 | 1 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0855 | 29.9529 | Equipment Failure | Substation | Equipment Failure | 2020-03-19 | DSUB | B | Council District B | Jay Banks | 70113 | 3
2020 | 2 | 1325563358 | NO | ORLEANS | FAIR | 164 | 2020-03-19 22:22 | 2020-03-19 22:22 | 2020-03-20 01:06 | 328 | SUBN | 1509 | 3951846983 | 1509 | ENOI | 1 | 2 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0855 | 29.953 | Equipment Failure | Substation | Equipment Failure | 2020-03-19 | DSUB | B | Council District B | Jay Banks | 70113 | 3
2020 | 9 | 1325564822 | NO | ORLEANS | FAIR | 164 | 2020-03-19 22:22 | 2020-03-19 22:22 | 2020-03-20 01:06 | 1476 | SUBN | 1542 | 3950746992 | 1542 | ENOI | 1 | 9 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0859 | 29.9532 | Equipment Failure | Substation | Equipment Failure | 2020-03-19 | DSUB | B | Council District B | Jay Banks | 70113 | 3
2020 | 15 | 1325563441 | Yes | ORLEANS | FAIR | 164 | 2020-03-19 22:22 | 2020-03-19 23:07 | 2020-03-20 01:07 | 2460 | SUBN | 1510 | 3951746984 | 1510 | ENOI | 1 | 15 | EPRI | Equipment Failure - Primary Conductor | N | primary cable faiure on 1510 breaker didnt relay out causing master to open up | -90.0856 | 29.953 | Equipment Failure | Substation | Equipment Failure | 2020-03-19 | DLIN | B | Council District B | Jay Banks | 70113 | 3
2020 | 661 | 1325566005 | Yes | EAST ORLEANS | FAIR | 167 | 2020-03-19 22:58 | 2020-03-20 01:40 | 2020-03-20 01:45 | 110387 | VFI | 27120 | 4243049745 | 1610 | ENOI | 6 | 661 | EPRI | Equipment Failure - Primary Conductor | N | primary ug cable fail | -97.0758 | 27.9066 | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | 2020-03-19 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 24 | 1325602730 | Yes | ORLEANS | FAIR | 355 | 2020-03-20 15:35 | 2020-03-20 19:34 | 2020-03-20 21:30 | 8520 | LFUS | 17692 | 3887448776 | 405 | ENOI | 1 | 24 | ETRD | Equipment Failure - Transformer | N | Parrellel Transformers bad and took out lateral troubleshooter got lateral in crew changed out transformers | -90.1053 | 30.0025 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-20 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 136 | 1325615894 | Yes | ORLEANS | FAIR | 356 | 2020-03-21 00:09 | 2020-03-21 05:48 | 2020-03-21 06:05 | 48416 | LFUS | 17747 | 3852449417 | 409 | ENOI | 1 | 136 | EARM | Equipment Failure - Crossarm | N | changed out x arm | -90.1161 | 30.0203 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-21 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 243 | 1325616344 | Yes | ORLEANS | FAIR | 188 | 2020-03-21 00:52 | 2020-03-21 02:12 | 2020-03-21 04:00 | 45684 | DIS | 23445 | 3898647498 | 903 | ENOI | 1 | 243 | EINS | Equipment Failure - Insulator | N | Open for safety to pickup phase that burned down from failed oinsulator at D"hemecourt & Cortez | -90.1022 | 29.9673 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-03-21 | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 176 | 1325661916 | Yes | ORLEANS | FAIR | 376 | 2020-03-22 12:44 | 2020-03-22 18:58 | 2020-03-22 19:00 | 66176 | LFUS | 27949 | 3986347312 | 1511 | ENOI | 1 | 176 | VHCL | Vehicle | N | car broke pole PID IN PROGRESS KC RELATED TO TKT# 1325661916 (AKS0 | -90.0745 | 29.962 | Public Damage | Line Fuse | Public Damage | 2020-03-22 | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 1 | 1325687193 | Yes | EAST ORLEANS | FAIR | 50 | 2020-03-23 08:55 | 2020-03-23 08:55 | 2020-03-23 09:45 | 50 | SERV | SERVICE | 4286350315 | 2216 | ENOI | 6 | 1 | MALD | Malicious Damage | N | Someone pulled meter broke into business check voltage ok plugged in meter and sealed customer back on, CHg PID to NO, criminal mischief - security dept issue | -89.9788 | 30.0435 | Public Damage | Service Conductor | Public Damage | 2020-03-23 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 134 | 1325707249 | Yes | ORLEANS | FAIR | 80 | 2020-03-23 18:10 | 2020-03-23 19:22 | 2020-03-23 19:31 | 10720 | LFUS | 27650 | 3977248967 | 1704 | ENOI | 1 | 134 | VLFL | Tree On Line Outside R.O.W | N | crew onsite making repairs | -90.0769 | 30.0073 | Vegetation | Line Fuse | Vegetation | 2020-03-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 74 | 1325731096 | Yes | EAST ORLEANS | FAIR | 315 | 2020-03-24 09:15 | 2020-03-24 13:50 | 2020-03-24 14:30 | 23310 | DIS | 22751 | 4654451526 | 1202 | ENOI | 6 | 74 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.862 | 30.0753 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-03-24 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 1 | 1325740262 | Yes | ORLEANS | FAIR | 165 | 2020-03-24 12:27 | 2020-03-24 12:27 | 2020-03-24 15:12 | 165 | TFUS | 1413402 | 39529481986 | 1705 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | tops side riser on lateral switch brokerepaired riser and changed c phase switch | -90.0848 | 29.9864 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-24 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 250 | 1325740722 | Yes | ORLEANS | FAIR | 73 | 2020-03-24 12:37 | 2020-03-24 13:40 | 2020-03-24 13:50 | 18250 | LFUS | 27910 | 4001447600 | 1712 | ENOI | 1 | 250 | EARM | Equipment Failure - Crossarm | N | end of arm broke and insulator came out of arm. reinstalled insulator | -90.0697 | 29.9698 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-24 | DLIN | D | Council District D | Jared Brossett | 70116 | 3
2020 | 4 | 1325755199 | Yes | ORLEANS | FAIR | 63 | 2020-03-24 16:07 | 2020-03-24 16:07 | 2020-03-24 17:10 | 252 | TFUS | 66080 | 38427472556 | 2016 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1198 | 29.9608 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-03-24 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 3
2020 | 97 | 1325778061 | Yes | ORLEANS | FAIR | 286 | 2020-03-25 03:30 | 2020-03-25 08:10 | 2020-03-25 08:16 | 27742 | LFUS | 38032 | 3893546975 | 2015 | ENOI | 1 | 97 | FOTH | Fire - Other (Describe in Remarks Field) | N | lateral is out due to a fire | -90.1038 | 29.953 | Other | Line Fuse | Other | 2020-03-25 | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 1 | 1325783682 | Yes | EAST ORLEANS | FAIR | 164 | 2020-03-25 07:08 | 2020-03-25 07:08 | 2020-03-25 09:52 | 164 | XFMR | 1239193 | 4142249180 | 1010 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | crew changed out bad pot | -90.0245 | 30.0128 | Equipment Failure | Transformer | Equipment Failure | 2020-03-25 | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 25 | 1325826194 | Yes | EAST ORLEANS | FAIR | 59 | 2020-03-25 20:05 | 2020-03-25 20:15 | 2020-03-25 21:04 | 1475 | LFUS | 58763 | 4259449242 | 1607 | ENOI | 6 | 25 | EARR | Equipment Failure - Arrestor | N | refused lat..blown arestor | -89.9874 | 30.0142 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-25 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 64 | 1325827386 | Yes | EAST ORLEANS | FAIR | 85 | 2020-03-25 20:41 | 2020-03-25 21:17 | 2020-03-25 22:06 | 5440 | LFUS | 21147 | 4069347881 | 623 | ENOI | 6 | 64 | EARR | Equipment Failure - Arrestor | N | refused a phase..cleared arestor.. | -90.0481 | 29.9772 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-25 | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 72 | 1325830344 | Yes | EAST ORLEANS | FAIR | 204 | 2020-03-25 23:06 | 2020-03-25 23:44 | 2020-03-26 02:30 | 14688 | LFUS | 24766 | 4440350119 | 1608 | ENOI | 6 | 72 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | "B" phase Indoor pothead in walk-in vault on Granville Dr. failed & burnt other 2 phases Isolated vlt, & restored lateral | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-25 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 4 | 1325850439 | Yes | EAST ORLEANS | FAIR | 289 | 2020-03-26 09:11 | 2020-03-26 10:57 | 2020-03-26 14:00 | 1156 | ELBO | 43284504925 | 43284504925 | 2214 | ENOI | 6 | 4 | ETRD | Equipment Failure - Transformer | N | burnt transformer replaced | -97.0758 | 27.9066 | Equipment Failure | Elbow | Equipment Failure | 2020-03-26 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 20 | 1325845296 | Yes | EAST ORLEANS | FAIR | 118 | 2020-03-26 09:17 | 2020-03-26 09:30 | 2020-03-26 11:15 | 2360 | LFUS | 25602 | 4319850532 | 2214 | ENOI | 6 | 20 | FOTH | Fire - Other (Describe in Remarks Field) | N | transformer caught firer, crew on site to repair | -97.0758 | 27.9066 | Other | Line Fuse | Other | 2020-03-26 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 63 | 1325868359 | Yes | EAST ORLEANS | FAIR | 339 | 2020-03-26 12:22 | 2020-03-26 13:54 | 2020-03-26 18:01 | 21357 | LFUS | 25848 | 4438450346 | 1608 | ENOI | 6 | 63 | EPRI | Equipment Failure - Primary Conductor | N | BAD CABLE | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-26 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 3 | 1325880626 | Yes | EAST ORLEANS | FAIR | 265 | 2020-03-26 21:41 | 2020-03-26 23:54 | 2020-03-27 02:06 | 795 | XFMR | 1149816 | 42899504160 | 2216 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | changed out transf. | -89.9775 | 30.0462 | Equipment Failure | Transformer | Equipment Failure | 2020-03-26 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 2 | 1325891147 | Yes | EAST ORLEANS | FAIR | 35 | 2020-03-27 01:32 | 2020-03-27 01:44 | 2020-03-27 02:07 | 70 | XFMR | 79978 | 4290350439 | 2216 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N | crew changing out transformer. | -89.9774 | 30.0469 | Equipment Failure | Transformer | Equipment Failure | 2020-03-27 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 27 | 1325908514 | Yes | ORLEANS | FAIR | 60 | 2020-03-27 12:46 | 2020-03-27 12:51 | 2020-03-27 13:46 | 1620 | TFUS | 76114 | 39176475866 | 911 | ENOI | 1 | 27 | ECNS | Equipment Failure - Connector Sleeve | N |  | -90.0962 | 29.9697 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-27 | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 30 | 1325942615 | Yes | EAST ORLEANS | FAIR | 224 | 2020-03-28 04:41 | 2020-03-28 08:03 | 2020-03-28 08:25 | 6720 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 30 | CFIM | Cable Failure in manhole | N | isolated b phase from V-15 to cub-22. identified hole in cable in submersible vault-15. | -89.9561 | 30.0595 | Equipment Failure | Line Fuse | Equipment Failure | 2020-03-28 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 75 | 1325948510 | Yes | ORLEANS | FAIR | 130 | 2020-03-28 07:51 | 2020-03-28 09:42 | 2020-03-28 10:01 | 9750 | LFUS | 27715 | 3916545880 | 1922 | ENOI | 1 | 75 | VLFL | Tree On Line Outside R.O.W | N | removed and refused | -90.097 | 29.9228 | Vegetation | Line Fuse | Vegetation | 2020-03-28 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 7 | 1325957496 | Yes | ORLEANS | FAIR | 132 | 2020-03-28 11:07 | 2020-03-28 11:07 | 2020-03-28 13:19 | 924 | TFUS | 617927 | 39144457916 | 1922 | ENOI | 1 | 7 | ASQL | Animal - Squirrel | N | refused due to squirel | -90.0978 | 29.9203 | Animal | Transformer Fuse | Animal | 2020-03-28 | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 13 | 1326013533 | Yes | ORLEANS | FAIR | 121 | 2020-03-29 07:40 | 2020-03-29 07:43 | 2020-03-29 09:41 | 1573 | TFUS | 1531175 | 38472473660 | 2016 | ENOI | 1 | 13 | VINE | Vine Growing into Line | N | removed and refused | -90.1185 | 29.9639 | Vegetation | Transformer Fuse | Vegetation | 2020-03-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 3
2020 | 1 | 1326047719 | Yes | EAST ORLEANS | FAIR | 617 | 2020-03-30 03:46 | 2020-03-30 03:46 | 2020-03-30 14:03 | 617 | TFUS | 30067 | 43767504790 | 2214 | ENOI | 6 | 1 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | replaced tie bar in underground transformer | -89.9501 | 30.0479 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-30 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 5 | 1326080529 | Yes | ORLEANS | FAIR | 23 | 2020-03-30 17:50 | 2020-03-30 17:50 | 2020-03-30 18:13 | 115 | DIS | 42102 | 3953347149 | 1506 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N |  | -90.085 | 29.9575 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-03-30 | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 1 | 1326080547 | Yes | ORLEANS | FAIR | 448 | 2020-03-30 17:50 | 2020-03-30 17:50 | 2020-03-31 01:18 | 448 | SWIT | 27253 | 39597471266 | 1506 | ENOI | 1 | 1 | SCHD | Scheduled Interruption | N | crew replacing cable in Vault # 211 Planned outage | -97.0758 | 27.9066 | Scheduled Interruption | Switch | Scheduled Interruption | 2020-03-30 | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 6 | 1326098448 | Yes | ORLEANS | FAIR | 313 | 2020-03-30 23:47 | 2020-03-30 23:52 | 2020-03-31 05:00 | 0 | TFUS | 54894 | 3878546969 | 2015 | ENOI | 1 | 6 | VINE | Vine Growing into Line | N | Cleared vines refused transformer HW | -90.1086 | 29.9528 | Vegetation | Transformer Fuse | Vegetation | 2020-03-30 | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 67 | 1326108189 | Yes | ORLEANS | FAIR | 135 | 2020-03-31 05:45 | 2020-03-31 07:26 | 2020-03-31 08:00 | 9045 | LFUS | 27675 | 3910546720 | 1922 | ENOI | 1 | 67 | VINE | Vine Growing into Line | N | rermoved vines, refused lateral | -90.0987 | 29.9458 | Vegetation | Line Fuse | Vegetation | 2020-03-31 | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 4 | 1326113204 | Yes | EAST ORLEANS | FAIR | 147 | 2020-03-31 07:33 | 2020-03-31 07:59 | 2020-03-31 10:00 | 588 | TFUS | 72871 | 42018475443 | 2346 | ENOI | 6 | 4 | EFSW | Equipment Failure - Fuse Switch | N | replaced transformer switch, customer back on: Flashover caused feeder to trip/close | -90.0062 | 29.9676 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-31 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 2088 | 1326128164 | Yes | ORLEANS | WIND | 41 | 2020-03-31 11:51 | 2020-03-31 12:24 | 2020-03-31 12:32 | 85608 | SBKR | 912 | 3898147404 | 912 | ENOI | 1 | 2088 | SLAK | Slack Conductor / Loose Connection | N | gravier and s clark, high wind, possible slack spans on dog leg of lateral | -90.1023 | 29.9647 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-03-31 | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 2 | 1326130727 | Yes | ORLEANS | FAIR | 114 | 2020-03-31 12:36 | 2020-03-31 12:36 | 2020-03-31 14:30 | 228 | TFUS | 57149 | 39014474170 | 912 | ENOI | 1 | 2 | SLAK | Slack Conductor / Loose Connection | N | slack span at gravier and s clark | -90.1013 | 29.9651 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-03-31 | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 82 | 1326137283 | Yes | ORLEANS | WIND | 152 | 2020-03-31 13:14 | 2020-03-31 14:37 | 2020-03-31 15:46 | 12464 | LFUS | 27672 | 3968747354 | 1511 | ENOI | 1 | 82 | VLFL | Tree On Line Outside R.O.W | N | top of tree broke and fell across latrerial burning down a phase and blowing fuse on b and c phase. crew cut tree away and picked up a phase | -90.08 | 29.9631 | Vegetation | Line Fuse | Vegetation | 2020-03-31 | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 6 | 1326148987 | Yes | EAST ORLEANS | FAIR | 256 | 2020-03-31 16:54 | 2020-03-31 16:55 | 2020-03-31 21:10 | 1536 | XFMR | 569607 | 43481509717 | 2217 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N | Crew on the way to repair submersible | -89.9588 | 30.0614 | Equipment Failure | Transformer | Equipment Failure | 2020-03-31 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 4 | 1326149381 | Yes | EAST ORLEANS | FAIR | 152 | 2020-03-31 17:04 | 2020-03-31 17:10 | 2020-03-31 19:36 | 608 | TFUS | 696585 | 41858470225 | 2346 | ENOI | 6 | 4 | VOHL | Overhanging Limb | N | Cut tree limbs. Need follow up | -90.0116 | 29.9534 | Vegetation | Transformer Fuse | Vegetation | 2020-03-31 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 27 | 1326179860 | Yes | ORLEANS | FAIR | 108 | 2020-04-01 07:38 | 2020-04-01 08:24 | 2020-04-01 09:26 | 2916 | LFUS | 177730 | 3854948315 | 408 | ENOI | 1 | 27 | ECNS | Equipment Failure - Connector Sleeve | N | RISER CAME OUT OF SWITCH PUT RISER BACK IN SWITCH | -90.1157 | 29.9899 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-01 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 1 | 1326182998 | Yes | EAST ORLEANS | FAIR | 172 | 2020-04-01 09:04 | 2020-04-01 09:04 | 2020-04-01 11:56 | 172 | SERV | METER | 40674486532 | 1710 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N | AMI meter has a defect, installed new meter 8197302 sn89900430 reading 00000 | -90.0484 | 29.9986 | Equipment Failure | Service Conductor | Equipment Failure | 2020-04-01 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 3 | 1326228392 | Yes | EAST ORLEANS | FAIR | 95 | 2020-04-02 08:43 | 2020-04-02 08:43 | 2020-04-02 10:18 | 285 | TFUS | 1307146 | 4073147859 | 622 | ENOI | 6 | 3 | AOTH | Animal - Other (Describe in Remarks Field) | N | Animal caused transformer fuse to blow. Cust back in lights. | -90.0467 | 29.9767 | Animal | Transformer Fuse | Animal | 2020-04-02 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 1 | 1326232086 | Yes | ORLEANS | FAIR | 109 | 2020-04-02 09:45 | 2020-04-02 09:45 | 2020-04-02 11:34 | 109 | SERV | SERVICE COND | 3986147400 | 907 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | repaired bad UG block | -90.0746 | 29.9643 | Equipment Failure | Service Conductor | Equipment Failure | 2020-04-02 | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 9 | 1326232294 | Yes | ORLEANS | FAIR | 11 | 2020-04-02 09:49 | 2020-04-02 09:49 | 2020-04-02 10:00 | 99 | TFUS | 25627 | 40043493837 | 503 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0681 | 30.0188 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-02 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 1 | 1326262368 | Yes | ORLEANS | FAIR | 100 | 2020-04-03 07:07 | 2020-04-03 07:07 | 2020-04-03 08:47 | 100 | SERV | SERVICE COND | 38160462631 | 2013 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad connection at weatherhead | -90.1286 | 29.9335 | Equipment Failure | Service Conductor | Equipment Failure | 2020-04-03 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 9 | 1326262782 | Yes | ORLEANS | FAIR | 323 | 2020-04-03 07:20 | 2020-04-03 08:29 | 2020-04-03 12:43 | 2907 | TFUS | 21205 | 38725488458 | 408 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | transferred bell pole and changed xfmr | -90.1099 | 30.0044 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-03 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 7 | 1326310714 | Yes | ORLEANS | FAIR | 237 | 2020-04-04 07:53 | 2020-04-04 07:53 | 2020-04-04 11:50 | 1659 | TFUS | 55743 | 40138487847 | 1704 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0654 | 30.0023 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-04 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 6 | 1326310722 | Yes | ORLEANS | FAIR | 238 | 2020-04-04 07:53 | 2020-04-04 08:16 | 2020-04-04 11:51 | 1428 | TFUS | 71373 | 40139487707 | 1704 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0654 | 30.0019 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-04 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 214 | 1326339586 | Yes | EAST ORLEANS | FAIR | 59 | 2020-04-04 23:34 | 2020-04-05 00:30 | 2020-04-05 00:33 | 12626 | LFUS | 27890 | 4104247687 | 611 | ENOI | 6 | 214 | EARM | Equipment Failure - Crossarm | N |  | -90.0372 | 29.972 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-04 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 130 | 1326339990 | Yes | EAST ORLEANS | FAIR | 35 | 2020-04-05 | 2020-04-05 00:04 | 2020-04-05 00:35 | 4550 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 130 | EINS | Equipment Failure - Insulator | N |  | -90.044 | 29.9708 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-05 | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 203 | 1326341850 | Yes | ORLEANS | FAIR | 120 | 2020-04-05 01:34 | 2020-04-05 02:27 | 2020-04-05 03:34 | 24360 | LFUS | 97107 | 4016948726 | 1704 | ENOI | 1 | 203 | EARM | Equipment Failure - Crossarm | N |  | -90.0642 | 30.0006 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-05 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 16 | 1326349496 | Yes | ORLEANS | FAIR | 32 | 2020-04-05 09:08 | 2020-04-05 09:08 | 2020-04-05 09:40 | 512 | LFUS | 28046 | 3913346967 | 1553 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0978 | 29.9527 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-04-05 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 4 | 1326353195 | Yes | ORLEANS | FAIR | 44 | 2020-04-05 10:22 | 2020-04-05 10:22 | 2020-04-05 11:06 | 176 | LFUS | 36687 | 3982147304 | 1511 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0758 | 29.9617 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-04-05 | DLIN | B | Council District B | Jay Banks | 70112 | 4
2020 | 351 | 1326453968 | Yes | EAST ORLEANS | FAIR | 18 | 2020-04-07 12:26 | 2020-04-07 12:41 | 2020-04-07 12:44 | 6318 | SWIT | 26183 | 4438750548 | 1609 | ENOI | 6 | 351 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -97.0758 | 27.9066 | Scheduled Interruption | Switch | Scheduled Interruption | 2020-04-07 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 1 | 1326457737 | Yes | ORLEANS | FAIR | 206 | 2020-04-07 13:52 | 2020-04-07 14:04 | 2020-04-07 17:18 | 206 | SERV | SERVICE | 39383458105 | 1922 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | trimmed tree, changed connections at the pole per 310 | -90.0902 | 29.9208 | Equipment Failure | Service Conductor | Equipment Failure | 2020-04-07 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 11 | 1326459620 | Yes | ORLEANS | FAIR | 190 | 2020-04-07 14:39 | 2020-04-07 14:39 | 2020-04-07 17:49 | 2090 | TFUS | 62936 | 39103468355 | 2021 | ENOI | 1 | 11 | EONE | Equipment Failure - Neutral / Shield Conductor | N | bad neutral connection on the transformer. per 310 | -90.0986 | 29.949 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-07 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 1 | 1326497490 | Yes | ORLEANS | FAIR | 29 | 2020-04-08 09:51 | 2020-04-08 09:51 | 2020-04-08 10:20 | 29 | TFUS | 30704 | 38166472777 | 2022 | ENOI | 1 | 1 | HECD | Company - Distribution Business (Describe in remar | N | Switched out for scheduled outage. Outage had been cancelled previously. | -90.1283 | 29.9614 | Human Error | Transformer Fuse | Human Error | 2020-04-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 77 | 1326526483 | Yes | ORLEANS | FAIR | 124 | 2020-04-08 17:29 | 2020-04-08 19:19 | 2020-04-08 19:33 | 9548 | LFUS | 21478 | 3908246060 | 1924 | ENOI | 1 | 77 | ECON | Equipment Failure - Connector / Sleeve | N | replaced hot line clamp and stirrup for lateral b phase. per 310 | -90.0997 | 29.9276 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-08 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 8 | 1326568665 | Yes | EAST ORLEANS | FAIR | 145 | 2020-04-09 10:00 | 2020-04-09 10:14 | 2020-04-09 12:25 | 1160 | LFUS | 38442 | 4205447637 | 2346 | ENOI | 6 | 8 | EPOL | Equipment Failure - Pole | N | customers back on | -90.005 | 29.9702 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-09 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 86 | 1326578592 | Yes | EAST ORLEANS | FAIR | 232 | 2020-04-09 12:54 | 2020-04-09 15:11 | 2020-04-09 16:46 | 19952 | LFUS | 21116 | 4094548019 | 621 | ENOI | 6 | 86 | VHCL | Vehicle | N | vehicle hit and broke pole, wires down, crew repaired | -90.0402 | 29.981 | Public Damage | Line Fuse | Public Damage | 2020-04-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 172 | 1326658765 | Yes | EAST ORLEANS | THDR | 300 | 2020-04-09 20:50 | 2020-04-10 01:00 | 2020-04-10 01:50 | 51600 | LFUS | 25610 | 4335750498 | 2214 | ENOI | 6 | 172 | EELB | Equipment Failure - Elbow | N | replaced elbow in submersible xfmr | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-09 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 5 | 1326732805 | Yes | EAST ORLEANS | THDR | 927 | 2020-04-09 23:13 | 2020-04-10 06:57 | 2020-04-10 14:40 | 4635 | OPEN | 5036554805 | 5036554805 | 1204 | ENOI | 6 | 5 | EPOL | Equipment Failure - Pole | N | 2 poles and primary down, repaired and replaced | -89.7396 | 30.1643 | Equipment Failure | Open | Equipment Failure | 2020-04-09 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 243 | 1326698180 | Yes | EAST ORLEANS | THDR | 348 | 2020-04-09 23:13 | 2020-04-10 05:23 | 2020-04-10 05:01 | 84564 | RCLR | 22184 | 4946452184 | 1204 | ENOI | 6 | 243 | EPRI | Equipment Failure - Primary Conductor | N | Wire down 22173 Chef 1/0 primary | -89.7692 | 30.0928 | Equipment Failure | Recloser | Equipment Failure | 2020-04-09 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 100 | 1326691444 | Yes | ORLEANS | THDR | 167 | 2020-04-09 23:21 | 2020-04-10 00:53 | 2020-04-10 02:08 | 16700 | LFUS | 17525 | 3836348870 | 410 | ENOI | 1 | 100 | LGHT | Lightning | N | refused ok taken out by weather | -90.1214 | 30.0051 | Lightning | Line Fuse | Lightning | 2020-04-09 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 879 | 1326691569 | Yes | ORLEANS | THDR | 139 | 2020-04-09 23:23 | 2020-04-10 01:30 | 2020-04-10 01:42 | 122181 | LFUS | F24069 | 3887447985 | 903 | ENOI | 1 | 879 | LGHT | Lightning | N | refused lateral 27794 all three phases,refused lateral at voisin and general diaz sidewalk phase,lateral 27962 refused b phase. | -90.1057 | 29.9807 | Lightning | Line Fuse | Lightning | 2020-04-09 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 66 | 1326691664 | Yes | ORLEANS | THDR | 193 | 2020-04-09 23:26 | 2020-04-10 02:00 | 2020-04-10 02:39 | 12738 | LFUS | 28068 | 3960648669 | 1703 | ENOI | 1 | 66 | LGHT | Lightning | N | taken out by weather refused ok | -90.0821 | 29.9993 | Lightning | Line Fuse | Lightning | 2020-04-09 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 6 | 1326691838 | Yes | ORLEANS | THDR | 243 | 2020-04-09 23:27 | 2020-04-09 23:27 | 2020-04-10 03:30 | 1458 | TFUS | 1187 | 38678484927 | 408 | ENOI | 1 | 6 | LGHT | Lightning | N | taken out by weather refused ok | -90.1115 | 29.9947 | Lightning | Transformer Fuse | Lightning | 2020-04-09 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 9 | 1326691934 | Yes | EAST ORLEANS | THDR | 282 | 2020-04-09 23:28 | 2020-04-10 03:27 | 2020-04-10 04:10 | 2538 | TFUS | 54886 | 42273502070 | 2211 | ENOI | 6 | 9 | EFSW | Equipment Failure - Fuse Switch | N | Wire broke on top of switch repaired | -89.9974 | 30.0409 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-09 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 165 | 1326691948 | Yes | ORLEANS | THDR | 152 | 2020-04-09 23:28 | 2020-04-09 23:37 | 2020-04-10 02:00 | 25080 | LFUS | 27704 | 3847746872 | 2016 | ENOI | 1 | 165 | LGHT | Lightning | N | taken out by weather refused ok | -90.1188 | 29.9503 | Lightning | Line Fuse | Lightning | 2020-04-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 83 | 1326693094 | Yes | ORLEANS | THDR | 270 | 2020-04-09 23:30 | 2020-04-10 03:59 | 2020-04-10 04:00 | 22410 | LFUS | 27672 | 3968747354 | 1511 | ENOI | 1 | 83 | LGHT | Lightning | N | taken out by weather refused ok | -90.08 | 29.9631 | Lightning | Line Fuse | Lightning | 2020-04-09 | DLIN | B | Council District B | Jay Banks | 70112 | 4
2020 | 40 | 1326693224 | Yes | EAST ORLEANS | THDR | 272 | 2020-04-09 23:32 | 2020-04-10 02:47 | 2020-04-10 04:05 | 10880 | LFUS | 21769 | 4296949346 | 1611 | ENOI | 6 | 40 | EFLK | Equipment Failure - Fuse Link | N | Refuse lateral 21769 b&amp;amp;c phases customer back in | -89.9756 | 30.0169 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-09 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 10 | 1326692771 | Yes | ORLEANS | THDR | 266 | 2020-04-09 23:34 | 2020-04-10 02:04 | 2020-04-10 04:00 | 2660 | TFUS | 1205965 | 38703472254 | 2011 | ENOI | 1 | 10 | LGHT | Lightning | N | taken out by weather refused ok | -90.1113 | 29.9599 | Lightning | Transformer Fuse | Lightning | 2020-04-09 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 103 | 1326693120 | Yes | ORLEANS | THDR | 204 | 2020-04-09 23:36 | 2020-04-10 02:09 | 2020-04-10 03:00 | 21012 | LFUS | 21813 | 3928146648 | 2021 | ENOI | 1 | 103 | LGHT | Lightning | N | taken out by weather refused ok | -90.0932 | 29.9438 | Lightning | Line Fuse | Lightning | 2020-04-09 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 58 | 1326693036 | Yes | EAST ORLEANS | THDR | 853 | 2020-04-09 23:37 | 2020-04-10 13:14 | 2020-04-10 13:51 | 49474 | LFUS | 27992 | 4264649381 | 1604 | ENOI | 6 | 58 | EPOL | Equipment Failure - Pole | N | Two rotted off SCBT poles need to transfer poles already set | -89.9857 | 30.0179 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-09 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 30 | 1326693406 | Yes | ORLEANS | THDR | 171 | 2020-04-09 23:39 | 2020-04-09 23:39 | 2020-04-10 02:30 | 5130 | TFUS | 1401920 | 3975245866 | 2146 | ENOI | 1 | 30 | EFSW | Equipment Failure - Fuse Switch | N | repaired jumper on trans refused ok | -90.0785 | 29.9222 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-09 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 96 | 1326694368 | Yes | ORLEANS | THDR | 132 | 2020-04-09 23:48 | 2020-04-09 23:48 | 2020-04-10 02:00 | 12672 | LFUS | F05614 | 39978464632 | 2137 | ENOI | 1 | 96 | LGHT | Lightning | N | teken out by weather refused ok | -90.0713 | 29.9386 | Lightning | Line Fuse | Lightning | 2020-04-09 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 74 | 1326694904 | Yes | EAST ORLEANS | THDR | 39 | 2020-04-09 23:51 | 2020-04-09 23:55 | 2020-04-10 00:30 | 2886 | LFUS | 27758 | 4093547749 | 622 | ENOI | 6 | 74 | EARM | Equipment Failure - Crossarm | N | arm broke on north johnson | -90.0405 | 29.9737 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 34 | 1326708697 | Yes | EAST ORLEANS | THDR | 219 | 2020-04-09 23:51 | 2020-04-10 02:07 | 2020-04-10 03:30 | 7446 | LFUS | 37119 | 4089647831 | 622 | ENOI | 6 | 34 | EARM | Equipment Failure - Crossarm | N | Broken crossarm on Clouet and N. Johnson | -90.0417 | 29.9759 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 45 | 1326701220 | Yes | ORLEANS | THDR | 340 | 2020-04-10 00:01 | 2020-04-10 04:51 | 2020-04-10 05:41 | 15300 | LFUS | 27910 | 4001447600 | 1712 | ENOI | 1 | 45 | LGHT | Lightning | N | taken out by weather refused ok | -90.0697 | 29.9698 | Lightning | Line Fuse | Lightning | 2020-04-10 | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 3 | 1326696357 | Yes | EAST ORLEANS | THDR | 282 | 2020-04-10 00:18 | 2020-04-10 00:18 | 2020-04-10 05:00 | 846 | XFMR | 1324626 | 40667491561 | 502 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | Bad transformer 50 Kva | -90.0485 | 30.0125 | Equipment Failure | Transformer | Equipment Failure | 2020-04-10 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 11 | 1326701516 | Yes | EAST ORLEANS | THDR | 176 | 2020-04-10 00:49 | 2020-04-10 03:28 | 2020-04-10 03:45 | 1936 | TFUS | 68407 | 42375493507 | 1607 | ENOI | 6 | 11 | EFSW | Equipment Failure - Fuse Switch | N | Wire broke on top of switch repaired | -89.9943 | 30.0172 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 9 | 1326703115 | Yes | ORLEANS | THDR | 58 | 2020-04-10 01:02 | 2020-04-10 01:02 | 2020-04-10 02:00 | 522 | TFUS | 67458 | 38417468094 | 2016 | ENOI | 1 | 9 | LGHT | Lightning | N | taken out by weather refused ok | -90.1203 | 29.9485 | Lightning | Transformer Fuse | Lightning | 2020-04-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 22 | 1326709672 | Yes | EAST ORLEANS | THDR | 139 | 2020-04-10 01:41 | 2020-04-10 01:41 | 2020-04-10 04:00 | 3058 | LFUS | 27716 | 43330494366 | 1611 | ENOI | 6 | 22 | EFLK | Equipment Failure - Fuse Link | N | Refused lateral sw 27716 B&C phase | -89.9643 | 30.0193 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-10 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 134 | 1326718187 | Yes | ORLEANS | THDR | 600 | 2020-04-10 03:35 | 2020-04-10 13:00 | 2020-04-10 13:35 | 80400 | LFUS | 21813 | 3928146648 | 2021 | ENOI | 1 | 134 | EPOL | Equipment Failure - Pole | N | broken pole AT S. MIRO AND 3RD ST | -90.0932 | 29.9438 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-10 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 14 | 1326717859 | Yes | ORLEANS | THDR | 24 | 2020-04-10 03:36 | 2020-04-10 03:52 | 2020-04-10 04:00 | 336 | TFUS | 1002285 | 39996464841 | 2137 | ENOI | 1 | 14 | LGHT | Lightning | N | taken out by weather refused ok | -90.0706 | 29.9392 | Lightning | Transformer Fuse | Lightning | 2020-04-10 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 9 | 1326721350 | Yes | EAST ORLEANS | THDR | 58 | 2020-04-10 05:03 | 2020-04-10 05:03 | 2020-04-10 06:01 | 522 | XFMR | 54886 | 42273502070 | 2211 | ENOI | 6 | 9 | ETRD | Equipment Failure - Transformer | N | Bad 50 KVA, leads and switch | -89.9974 | 30.0409 | Equipment Failure | Transformer | Equipment Failure | 2020-04-10 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 8 | 1326723023 | Yes | ORLEANS | THDR | 80 | 2020-04-10 05:31 | 2020-04-10 05:31 | 2020-04-10 06:51 | 640 | TFUS | 66889 | 38498468689 | 2016 | ENOI | 1 | 8 | VINE | Vine Growing into Line | N | Vines on transformer jumper refused ok | -90.1178 | 29.9501 | Vegetation | Transformer Fuse | Vegetation | 2020-04-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 56 | 1326730930 | Yes | EAST ORLEANS | THDR | 29 | 2020-04-10 06:57 | 2020-04-10 07:08 | 2020-04-10 07:26 | 1624 | RCLR | 37793 | 4946452184 | 1204 | ENOI | 6 | 56 | EPOL | Equipment Failure - Pole | N | 2 broke poles, isulated and got recloser back in | -89.7692 | 30.0928 | Equipment Failure | Recloser | Equipment Failure | 2020-04-10 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 10 | 1326747880 | Yes | ORLEANS | THDR | 38 | 2020-04-10 09:40 | 2020-04-10 09:40 | 2020-04-10 10:18 | 380 | TFUS | 58865 | 39943475082 | 1712 | ENOI | 1 | 10 | LGHT | Lightning | N | refused transformer | -90.072 | 29.9673 | Lightning | Transformer Fuse | Lightning | 2020-04-10 | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 1 | 1326751623 | Yes | ORLEANS | THDR | 120 | 2020-04-10 10:01 | 2020-04-10 10:01 | 2020-04-10 12:01 | 120 | TFUS | 1096585 | 3929646618 | 2021 | ENOI | 1 | 1 | LGHT | Lightning | N | weather, refused | -90.0927 | 29.943 | Lightning | Transformer Fuse | Lightning | 2020-04-10 | DLIN | B | Council District B | Jay Banks | 70113 | 4
2020 | 98 | 1326788386 | Yes | EAST ORLEANS | THDR | 362 | 2020-04-10 10:48 | 2020-04-10 16:48 | 2020-04-10 16:51 | 35476 | LFUS | 25980 | 4212449674 | 1610 | ENOI | 6 | 98 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 120 | 1326788132 | Yes | ORLEANS | THDR | 122 | 2020-04-10 16:19 | 2020-04-10 17:02 | 2020-04-10 18:21 | 14640 | LFUS | 27697 | 3980948243 | 1705 | ENOI | 1 | 120 | EPOL | Equipment Failure - Pole | N | broke pole | -90.0758 | 29.9876 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-10 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 12 | 1326794775 | Yes | ORLEANS | FAIR | 101 | 2020-04-10 18:30 | 2020-04-10 18:30 | 2020-04-10 20:11 | 1212 | TFUS | 71021 | 39712482456 | 1705 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0789 | 29.9877 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-10 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 18 | 1326816365 | Yes | ORLEANS | FAIR | 112 | 2020-04-11 08:08 | 2020-04-11 08:09 | 2020-04-11 10:00 | 2016 | TFUS | 1400854 | 39268479955 | 912 | ENOI | 1 | 18 | AOTH | Animal - Other (Describe in Remarks Field) | N | crow | -90.0931 | 29.9809 | Animal | Transformer Fuse | Animal | 2020-04-11 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 68 | 1326826003 | Yes | ORLEANS | FAIR | 501 | 2020-04-11 08:09 | 2020-04-11 14:10 | 2020-04-11 16:30 | 34068 | LFUS | 21484 | 3923146070 | 1924 | ENOI | 1 | 68 | EPOL | Equipment Failure - Pole | N | replaced broke pole, customers back on | -90.095 | 29.928 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-11 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 12 | 1326817592 | Yes | ORLEANS | FAIR | 148 | 2020-04-11 08:32 | 2020-04-11 08:38 | 2020-04-11 11:00 | 1776 | TFUS | 28686 | 38486470894 | 2015 | ENOI | 1 | 12 | AOTH | Animal - Other (Describe in Remarks Field) | N | crow | -90.1181 | 29.9561 | Animal | Transformer Fuse | Animal | 2020-04-11 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 4
2020 | 63 | 1326824377 | Yes | ORLEANS | FAIR | 52 | 2020-04-11 10:52 | 2020-04-11 11:05 | 2020-04-11 11:44 | 3276 | LFUS | 97780 | 3989247799 | 615 | ENOI | 1 | 63 | VINE | Vine Growing into Line | N | Back on cleared trees | -90.0734 | 29.9753 | Vegetation | Line Fuse | Vegetation | 2020-04-11 | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 18 | 1326832748 | Yes | ORLEANS | FAIR | 204 | 2020-04-11 13:11 | 2020-04-11 15:48 | 2020-04-11 16:35 | 3672 | XFMR | 1400854 | 39268479955 | 912 | ENOI | 1 | 18 | SCHD | Scheduled Interruption | N | changed out transf. | -90.0931 | 29.9809 | Scheduled Interruption | Transformer | Scheduled Interruption | 2020-04-11 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 22 | 1326841490 | Yes | ORLEANS | FAIR | 162 | 2020-04-11 16:40 | 2020-04-11 16:50 | 2020-04-11 19:22 | 3564 | TFUS | 61864 | 39252460479 | 1924 | ENOI | 1 | 22 | EPOL | Equipment Failure - Pole | N | crew made repairs | -90.0942 | 29.9273 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-11 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 9 | 1326905599 | Yes | ORLEANS | WIND | 259 | 2020-04-12 10:20 | 2020-04-12 10:20 | 2020-04-12 14:39 | 2331 | TFUS | 56582 | 39533474552 | 907 | ENOI | 1 | 9 | EARM | Equipment Failure - Crossarm | N | secondary arm replaced | -90.0848 | 29.9659 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-12 | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 3 | 1326905718 | Yes | EAST ORLEANS | FAIR | 41 | 2020-04-12 10:21 | 2020-04-12 10:23 | 2020-04-12 11:02 | 123 | TFUS | 1324626 | 40667491561 | 502 | ENOI | 6 | 3 | EARM | Equipment Failure - Crossarm | N | sec x arm short..temp safe ..refused trans | -90.0485 | 30.0125 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-12 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 24 | 1326987204 | Yes | ORLEANS | THDR | 89 | 2020-04-12 14:27 | 2020-04-12 14:51 | 2020-04-12 15:56 | 2136 | LFUS | 36920 | 3912948070 | 904 | ENOI | 1 | 24 | LGHT | Lightning | N | weather | -90.0974 | 29.9829 | Lightning | Line Fuse | Lightning | 2020-04-12 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 1 | 1326989627 | Yes | EAST ORLEANS | WIND | 150 | 2020-04-12 14:48 | 2020-04-12 14:48 | 2020-04-12 17:18 | 150 | TFUS | 1336630 | 4107349839 | 1001 | ENOI | 6 | 1 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | repaiired brace..refused a phase.. | -90.0353 | 30.0308 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-12 | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 11 | 1326996836 | Yes | ORLEANS | WIND | 73 | 2020-04-12 15:12 | 2020-04-12 15:34 | 2020-04-12 16:25 | 803 | TFUS | 1466818 | 39921488745 | 1704 | ENOI | 1 | 11 | VLFL | Tree On Line Outside R.O.W | N | Trees took out switch in transformer | -90.0721 | 30.0048 | Vegetation | Transformer Fuse | Vegetation | 2020-04-12 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 95 | 1327000269 | Yes | EAST ORLEANS | WIND | 61 | 2020-04-12 15:18 | 2020-04-12 16:06 | 2020-04-12 16:19 | 5795 | LFUS | 27876 | 4359749690 | 1601 | ENOI | 6 | 95 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused lat 27876 B &amp;amp; C phase..wind | -89.9558 | 30.0259 | Other | Line Fuse | Other | 2020-04-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 12 | 1327021461 | Yes | ORLEANS | WIND | 176 | 2020-04-12 16:27 | 2020-04-12 16:27 | 2020-04-12 19:23 | 2112 | TFUS | 55737 | 40223487314 | 1704 | ENOI | 1 | 12 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Taken out by tree repaired | -90.0627 | 30.0007 | Vegetation | Transformer Fuse | Vegetation | 2020-04-12 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 2 | 1327038835 | Yes | ORLEANS | THDR | 157 | 2020-04-12 17:43 | 2020-04-12 17:51 | 2020-04-12 20:20 | 314 | TFUS | 1546470 | 4013246071 | 1911 | ENOI | 1 | 2 | SLAK | Slack Conductor / Loose Connection | N | Primary and guy wire close installed spacer | -90.0664 | 29.9278 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-12 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 95 | 1327056099 | Yes | EAST ORLEANS | THDR | 253 | 2020-04-12 18:55 | 2020-04-12 23:02 | 2020-04-12 23:08 | 24035 | LFUS | 27876 | 4359749690 | 1601 | ENOI | 6 | 95 | SLAK | Slack Conductor / Loose Connection | N | Crew installed spacers | -89.9558 | 30.0259 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 14 | 1327097573 | Yes | EAST ORLEANS | THDR | 205 | 2020-04-12 19:33 | 2020-04-12 20:54 | 2020-04-12 22:58 | 2870 | TFUS | 71144 | 40620477716 | 622 | ENOI | 6 | 14 | LGHT | Lightning | N | weather refused okay | -90.0503 | 29.9744 | Lightning | Transformer Fuse | Lightning | 2020-04-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 4 | 1327185933 | Yes | ORLEANS | THDR | 40 | 2020-04-12 20:54 | 2020-04-12 20:54 | 2020-04-12 21:34 | 160 | TFUS | 63874 | 38617470487 | 2015 | ENOI | 1 | 4 | EFSW | Equipment Failure - Fuse Switch | N | Riser came out of top of switch repaired | -90.114 | 29.9549 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-12 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 1 | 1327238091 | Yes | EAST ORLEANS | THDR | 210 | 2020-04-12 22:01 | 2020-04-12 22:20 | 2020-04-13 01:31 | 210 | SERV | SERVICE | 42713494067 | 1604 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | hot leg burned off at squeeze on open wire secondary. replaced all three connections at pole. had customer verify all lights and applicances back on. | -89.9836 | 30.0187 | Equipment Failure | Service Conductor | Equipment Failure | 2020-04-12 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 2 | 1327261824 | Yes | EAST ORLEANS | THDR | 82 | 2020-04-12 22:23 | 2020-04-12 22:23 | 2020-04-12 23:45 | 164 | TFUS | 78289 | 42002472445 | 2345 | ENOI | 6 | 2 | LGHT | Lightning | N | WIND | -90.0071 | 29.9593 | Lightning | Transformer Fuse | Lightning | 2020-04-12 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 2 | 1327261864 | Yes | ORLEANS | THDR | 65 | 2020-04-12 22:23 | 2020-04-12 22:23 | 2020-04-12 23:28 | 130 | TFUS | 28160 | 38467482925 | 407 | ENOI | 1 | 2 | SLAK | Slack Conductor / Loose Connection | N | Phase out from high winds. Refused ok | -90.1181 | 29.9893 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-12 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 8 | 1327276626 | Yes | ORLEANS | THDR | 63 | 2020-04-12 23:00 | 2020-04-12 23:00 | 2020-04-13 00:03 | 504 | TFUS | 67835 | 38533476792 | 2026 | ENOI | 1 | 8 | ECNS | Equipment Failure - Connector Sleeve | N | rier on switch | -90.1163 | 29.9725 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-12 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 9 | 1327356631 | Yes | ORLEANS | FAIR | 240 | 2020-04-13 04:25 | 2020-04-13 04:25 | 2020-04-13 08:25 | 2160 | LFUS | 13221 | 38376479437 | 400 | ENOI | 1 | 9 | UNKN | Inspected Unknown | N | b phase blow on lateral | -90.1213 | 29.9798 | Other | Line Fuse | Other | 2020-04-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 74 | 1327493389 | Yes | EAST ORLEANS | FAIR | 425 | 2020-04-13 08:58 | 2020-04-13 13:49 | 2020-04-13 16:03 | 31450 | DIS | 22751 | 4654451526 | 1202 | ENOI | 6 | 74 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.862 | 30.0753 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-04-13 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 5 | 1327463597 | Yes | ORLEANS | FAIR | 83 | 2020-04-13 11:40 | 2020-04-13 11:47 | 2020-04-13 13:03 | 415 | TFUS | 58389 | 40281489566 | 1704 | ENOI | 1 | 5 | EFLK | Equipment Failure - Fuse Link | N | REFUSED XFMR | -90.0607 | 30.007 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-13 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 9 | 1327514921 | Yes | ORLEANS | FAIR | 60 | 2020-04-13 14:25 | 2020-04-13 14:25 | 2020-04-13 15:26 | 540 | LFUS | 13221 | 3831747940 | 400 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1231 | 29.9796 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-04-13 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 14 | 1327825400 | Yes | ORLEANS | FAIR | 305 | 2020-04-14 17:15 | 2020-04-14 18:12 | 2020-04-14 22:20 | 4270 | LFUS | 33455 | 3866347238 | 2011 | ENOI | 1 | 14 | EPOL | Equipment Failure - Pole | N | replace | -90.1125 | 29.9602 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-14 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 6 | 1327885181 | Yes | ORLEANS | FAIR | 272 | 2020-04-15 04:58 | 2020-04-15 08:08 | 2020-04-15 09:30 | 1632 | TFUS | 52109 | 38371491817 | 409 | ENOI | 1 | 6 | VOHL | Overhanging Limb | N | tree branch got across transformer; trimmed dead branches and refused | -90.1209 | 30.0137 | Vegetation | Transformer Fuse | Vegetation | 2020-04-15 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 76 | 1327925033 | Yes | EAST ORLEANS | FAIR | 28 | 2020-04-15 10:32 | 2020-04-15 10:53 | 2020-04-15 11:00 | 2128 | LFUS | 21116 | 4094548019 | 621 | ENOI | 6 | 76 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0402 | 29.981 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-04-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 28 | 1327971627 | Yes | ORLEANS | FAIR | 44 | 2020-04-15 14:57 | 2020-04-15 14:57 | 2020-04-15 15:41 | 1232 | LFUS | 33059 | 3895147524 | 903 | ENOI | 1 | 28 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1031 | 29.9681 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-04-15 | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 73 | 1328044401 | Yes | EAST ORLEANS | FAIR | 297 | 2020-04-16 08:03 | 2020-04-16 08:32 | 2020-04-16 13:00 | 21681 | LFUS | 32497 | 4112647692 | 611 | ENOI | 6 | 73 | SCHD | Scheduled Interruption | N | Scheduled Interruption for safety to replace broken pole RELATED TO TKT#1328030710 (AKS) | -90.0346 | 29.972 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-04-16 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 5 | 1328065432 | Yes | ORLEANS | FAIR | 84 | 2020-04-16 10:42 | 2020-04-16 10:49 | 2020-04-16 12:07 | 420 | LFUS | 61731 | 38375461112 | 1917 | ENOI | 1 | 5 | VOHL | Overhanging Limb | N | tree limbs got lateral together; refused | -90.1219 | 29.9294 | Vegetation | Line Fuse | Vegetation | 2020-04-16 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 9 | 1328065709 | Yes | ORLEANS | FAIR | 80 | 2020-04-16 10:45 | 2020-04-16 11:27 | 2020-04-16 12:05 | 720 | LFUS | 69744 | 38350461226 | 1917 | ENOI | 1 | 9 | VOHL | Overhanging Limb | N | tree limbs got lateral together; made veg ticket; refused | -90.1227 | 29.9297 | Vegetation | Line Fuse | Vegetation | 2020-04-16 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 1 | 1328108630 | Yes | EAST ORLEANS | FAIR | 377 | 2020-04-16 17:00 | 2020-04-16 17:00 | 2020-04-16 23:17 | 377 | SERV | SERVICE | 48065512163 | 1204 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad underground connection in hole | -89.8138 | 30.0666 | Equipment Failure | Service Conductor | Equipment Failure | 2020-04-16 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 5 | 1328110621 | Yes | EAST ORLEANS | FAIR | 96 | 2020-04-16 17:21 | 2020-04-16 17:21 | 2020-04-16 18:57 | 480 | TFUS | 1087299 | 42802502570 | 2216 | ENOI | 6 | 5 | UNKN | Inspected Unknown | N | refused sand fuse in valt..good volt | -89.9807 | 30.042 | Other | Transformer Fuse | Other | 2020-04-16 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 401 | 1328235772 | Yes | ORLEANS | RAIN | 245 | 2020-04-18 01:24 | 2020-04-18 05:10 | 2020-04-18 05:29 | 98245 | DIS | 24655 | 3943947293 | 1513 | ENOI | 1 | 401 | ECAP | Equipment Failure - Capacitor | N | step retore | -90.0879 | 29.9616 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 1290 | 1328239789 | Yes | ORLEANS | THDR | 453 | 2020-04-18 01:24 | 2020-04-18 08:55 | 2020-04-18 08:57 | 584370 | DIS | D01640 | 3927347512 | 1513 | ENOI | 1 | 1290 | ECAP | Equipment Failure - Capacitor | N | Cleared twisted phases and cleared cap bank | -90.093 | 29.9676 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 104 | 1328231576 | Yes | EAST ORLEANS | FAIR | 289 | 2020-04-18 01:36 | 2020-04-18 06:09 | 2020-04-18 06:25 | 30056 | LFUS | 27803 | 4055548010 | 613 | ENOI | 6 | 104 | EARM | Equipment Failure - Crossarm | N |  | -90.0523 | 29.981 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 44 | 1328232509 | Yes | EAST ORLEANS | THDR | 354 | 2020-04-18 02:12 | 2020-04-18 06:07 | 2020-04-18 08:06 | 15576 | LFUS | 21745 | 4246649393 | 1607 | ENOI | 6 | 44 | EARM | Equipment Failure - Crossarm | N |  | -89.9914 | 30.0184 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 84 | 1328241156 | Yes | ORLEANS | THDR | 328 | 2020-04-18 05:49 | 2020-04-18 10:57 | 2020-04-18 11:17 | 27552 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 84 | EARM | Equipment Failure - Crossarm | N | Cross arm mary have taken out lateral. Refused OK HW | -90.0878 | 29.975 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 95 | 1328242037 | Yes | ORLEANS | THDR | 189 | 2020-04-18 05:58 | 2020-04-18 07:41 | 2020-04-18 09:07 | 17955 | LFUS | F05614 | 39978464632 | 2137 | ENOI | 1 | 95 | EARM | Equipment Failure - Crossarm | N | crossarm brace fell on jumper. cleared and refused lateral | -90.0713 | 29.9386 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 397 | 1328252072 | Yes | ORLEANS | THDR | 195 | 2020-04-18 06:17 | 2020-04-18 09:21 | 2020-04-18 09:32 | 77415 | DIS | 24403 | 3964845844 | 2147 | ENOI | 1 | 397 | EARM | Equipment Failure - Crossarm | N |  | -90.0819 | 29.9217 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 2410 | 1328242641 | Yes | ORLEANS | THDR | 110 | 2020-04-18 06:18 | 2020-04-18 08:02 | 2020-04-18 08:08 | 265100 | SBKR | 2147 | 4012946119 | 2147 | ENOI | 1 | 2410 | EARM | Equipment Failure - Crossarm | N | Opened mid point switch. still patrolling | -90.0666 | 29.929 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 914 | 1328243630 | Yes | ORLEANS | THDR | 181 | 2020-04-18 06:19 | 2020-04-18 09:17 | 2020-04-18 09:20 | 165434 | RCLR | 24210 | 3918445893 | 1923 | ENOI | 1 | 914 | EARM | Equipment Failure - Crossarm | N | broken cross arm | -90.0965 | 29.9232 | Equipment Failure | Recloser | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 3 | 1328246188 | Yes | ORLEANS | THDR | 543 | 2020-04-18 07:08 | 2020-04-18 07:08 | 2020-04-18 16:11 | 1629 | TFUS | 1256945 | 39327471365 | 1512 | ENOI | 1 | 3 | EARM | Equipment Failure - Crossarm | N | changed out broken lateral arm | -90.0915 | 29.9573 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 1973 | 1328252497 | Yes | EAST ORLEANS | THDR | 83 | 2020-04-18 07:22 | 2020-04-18 08:42 | 2020-04-18 08:46 | 163759 | RCLR | 25915 | 4284250608 | 2215 | ENOI | 6 | 1973 | EMER | Emergency Switching | N | Taken out when pole broke out due to fire. See breaker case. Went out at the same time | -89.9795 | 30.0516 | Other | Recloser | Emergency Switching | 2020-04-18 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 182 | 1328248973 | Yes | EAST ORLEANS | THDR | 425 | 2020-04-18 07:22 | 2020-04-18 14:20 | 2020-04-18 14:27 | 77350 | DIS | 24376 | 4269950499 | 2215 | ENOI | 6 | 182 | EPOL | Equipment Failure - Pole | N | Crew on site replacing pole | -89.9837 | 30.0488 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-04-18 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 999 | 1328247232 | Yes | EAST ORLEANS | THDR | 7 | 2020-04-18 07:23 | 2020-04-18 07:29 | 2020-04-18 07:29 | 6993 | SBKR | 2215 | 4334550772 | 2215 | ENOI | 6 | 999 | EPOL | Equipment Failure - Pole | N | Pole burned in half:; Recloser went out at the same time: | -89.9633 | 30.0559 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-04-18 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 1 | 1328249615 | Yes | EAST ORLEANS | THDR | 543 | 2020-04-18 07:57 | 2020-04-18 07:57 | 2020-04-18 17:00 | 543 | TFUS | 71197 | 43234492055 | 1612 | ENOI | 6 | 1 | EPOL | Equipment Failure - Pole | N | Crew on site replacing pole | -89.9674 | 30.0129 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-18 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 606 | 1328259542 | Yes | ORLEANS | THDR | 236 | 2020-04-18 08:55 | 2020-04-18 12:01 | 2020-04-18 12:51 | 143016 | DIS | 27016 | 39528460309 | 2147 | ENOI | 1 | 606 | EARM | Equipment Failure - Crossarm | N | Crew on site replacing cross arms | -90.0864 | 29.9264 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 50 | 1328256797 | Yes | ORLEANS | THDR | 60 | 2020-04-18 09:14 | 2020-04-18 10:01 | 2020-04-18 10:14 | 3000 | LFUS | 33992 | 3981445947 | 2147 | ENOI | 1 | 50 | ECON | Equipment Failure - Connector / Sleeve | N | repaired broken jumper at switch pole | -90.0767 | 29.9244 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 122 | 1328258228 | Yes | ORLEANS | THDR | 199 | 2020-04-18 09:32 | 2020-04-18 12:10 | 2020-04-18 12:51 | 24278 | DIS | 24113 | 3942345968 | 1923 | ENOI | 1 | 122 | EMER | Emergency Switching | N | Crew on site replacing cross arms | -90.0864 | 29.9264 | Other | Disconnect Switch | Emergency Switching | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 47 | 1328262165 | Yes | ORLEANS | THDR | 20 | 2020-04-18 10:20 | 2020-04-18 10:40 | 2020-04-18 10:41 | 940 | LFUS | 37999 | 3976747636 | 907 | ENOI | 1 | 47 | EARM | Equipment Failure - Crossarm | N | Crew On Site Working | -90.0774 | 29.9708 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 41 | 1328276688 | Yes | ORLEANS | THDR | 227 | 2020-04-18 15:21 | 2020-04-18 19:09 | 2020-04-18 19:08 | 9307 | LFUS | 17789 | 3901648762 | 403 | ENOI | 1 | 41 | ETRD | Equipment Failure - Transformer | N | transformer bad took out lateral troubleshooter got lateral in and crew changed transformer | -90.1008 | 30.0021 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 84 | 1328276701 | Yes | EAST ORLEANS | THDR | 189 | 2020-04-18 15:25 | 2020-04-18 16:06 | 2020-04-18 18:34 | 15876 | LFUS | 31589 | 40579484677 | 1710 | ENOI | 6 | 84 | LGHT | Lightning | N | found transformer and lateral switch blown at location. cust stated lightning hit pole with transformer. refused lateral and transformer. chk voltage. all lights back on, | -90.0517 | 29.9935 | Lightning | Line Fuse | Lightning | 2020-04-18 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 9 | 1328276628 | Yes | ORLEANS | RAIN | 776 | 2020-04-18 15:27 | 2020-04-18 19:20 | 2020-04-19 04:23 | 6984 | XFMR | 57979 | 39099461768 | 1922 | ENOI | 1 | 9 | ETRD | Equipment Failure - Transformer | N | 50 kva tranformer top blew off turn in to crew case gave to 306 | -90.099 | 29.9309 | Equipment Failure | Transformer | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 213 | 1328278670 | Yes | EAST ORLEANS | THDR | 54 | 2020-04-18 15:59 | 2020-04-18 16:37 | 2020-04-18 16:53 | 11502 | SBKR | 2347 | 4216047802 | 2347 | ENOI | 6 | 213 | LGHT | Lightning | N | Loop Scheme worked properly restoring all load down of reclosers | -90.0018 | 29.9747 | Lightning | Substation Breaker | Lightning | 2020-04-18 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 48 | 1328280581 | Yes | ORLEANS | FAIR | 500 | 2020-04-18 16:10 | 2020-04-19 00:27 | 2020-04-19 00:30 | 24000 | LFUS | 21404 | 3867746474 | 1554 | ENOI | 1 | 48 | LGHT | Lightning | N | found broken primary arm at 2620 joseph st. replaced primary arm. | -90.1122 | 29.9391 | Lightning | Line Fuse | Lightning | 2020-04-18 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 4
2020 | 92 | 1328280796 | Yes | ORLEANS | RAIN | 561 | 2020-04-18 16:17 | 2020-04-18 19:53 | 2020-04-19 01:38 | 51612 | LFUS | 38032 | 3893546975 | 2015 | ENOI | 1 | 92 | EARM | Equipment Failure - Crossarm | N | crossarm broken changed out | -90.1038 | 29.953 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 53 | 1328281315 | Yes | ORLEANS | THDR | 95 | 2020-04-18 16:25 | 2020-04-18 17:06 | 2020-04-18 18:00 | 5035 | LFUS | 33992 | 3981445947 | 2147 | ENOI | 1 | 53 | EARM | Equipment Failure - Crossarm | N | Crew on site replacing arm | -90.0767 | 29.9244 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 124 | 1328286127 | Yes | ORLEANS | THDR | 179 | 2020-04-18 17:16 | 2020-04-18 20:14 | 2020-04-18 20:16 | 22196 | LFUS | 27615 | 3972747795 | 615 | ENOI | 1 | 124 | EARM | Equipment Failure - Crossarm | N | changed crossarm | -90.0786 | 29.9753 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 4 | 1328286507 | Yes | ORLEANS | FAIR | 847 | 2020-04-18 17:30 | 2020-04-18 19:52 | 2020-04-19 07:37 | 3388 | TFUS | 23082 | 38455485577 | 410 | ENOI | 1 | 4 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.1186 | 29.9966 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-18 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 1138 | 1328288893 | Yes | ORLEANS | RAIN | 278 | 2020-04-18 17:31 | 2020-04-18 22:02 | 2020-04-18 22:09 | 316364 | DIS | 63257 | 39639473127 | 1511 | ENOI | 1 | 1138 | ECNS | Equipment Failure - Connector Sleeve | N | jumper sleeve burnt up, crew replaced | -90.0819 | 29.9621 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-04-18 | DLIN | B | Council District B | Jay Banks | 70112 | 4
2020 | 6 | 1328296360 | Yes | ORLEANS | FAIR | 619 | 2020-04-18 18:42 | 2020-04-19 00:50 | 2020-04-19 05:01 | 3714 | XFMR | 1537127 | 39979478467 | 615 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | CHANGED TRANSFORMER | -90.0707 | 29.9766 | Equipment Failure | Transformer | Equipment Failure | 2020-04-18 | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 10 | 1328302045 | Yes | ORLEANS | FAIR | 107 | 2020-04-18 19:26 | 2020-04-18 19:49 | 2020-04-18 21:13 | 1070 | TFUS | 18352 | 38939487697 | 403 | ENOI | 1 | 10 | LGHT | Lightning | N | refused ok. per 310 | -90.1032 | 30.0023 | Lightning | Transformer Fuse | Lightning | 2020-04-18 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 68 | 1328311357 | Yes | ORLEANS | FAIR | 260 | 2020-04-18 22:01 | 2020-04-19 02:16 | 2020-04-19 02:22 | 17680 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 68 | EARM | Equipment Failure - Crossarm | N | Repaired crossarm at 828 hagan | -90.0878 | 29.975 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-18 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 584 | 1328318653 | Yes | ORLEANS | FAIR | 104 | 2020-04-18 23:02 | 2020-04-19 00:46 | 2020-04-19 00:47 | 60736 | OPEN | 3990247381 | 3990247381 | 1511 | ENOI | 1 | 584 | ECNS | Equipment Failure - Connector Sleeve | N | A phase jumper burned open: Isolated & picked up load | -90.0733 | 29.9638 | Equipment Failure | Open | Equipment Failure | 2020-04-18 | DLIN | C | Council District C | Kristin Palmer | 70116 | 4
2020 | 862 | 1328324917 | Yes | ORLEANS | THDR | 230 | 2020-04-19 00:22 | 2020-04-19 03:30 | 2020-04-19 04:13 | 198260 | RCLR | 24783 | 3885346462 | 1926 | ENOI | 1 | 862 | LGHT | Lightning | N | refused | -90.1067 | 29.9388 | Lightning | Recloser | Lightning | 2020-04-19 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 87 | 1328325028 | Yes | ORLEANS | RAIN | 98 | 2020-04-19 02:05 | 2020-04-19 03:01 | 2020-04-19 03:44 | 8526 | LFUS | 38032 | 3893546975 | 2015 | ENOI | 1 | 87 | EINS | Equipment Failure - Insulator | N | Changed insulator at eden and salcedo | -90.1038 | 29.953 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-19 | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 5 | 1328327624 | Yes | ORLEANS | THDR | 80 | 2020-04-19 04:57 | 2020-04-19 04:58 | 2020-04-19 06:18 | 400 | LFUS | 61731 | 38375461112 | 1917 | ENOI | 1 | 5 | EONE | Equipment Failure - Neutral / Shield Conductor | N | found shield sleeve was pull out by tree. repaired laterial refused customer back in light. HW | -90.1219 | 29.9294 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-19 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 3 | 1328337251 | Yes | EAST ORLEANS | FAIR | 106 | 2020-04-19 09:15 | 2020-04-19 09:15 | 2020-04-19 11:01 | 318 | TFUS | 1307146 | 4073147859 | 622 | ENOI | 6 | 3 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Removed debris off wire | -90.0467 | 29.9767 | Other | Transformer Fuse | Other | 2020-04-19 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 43 | 1328337701 | Yes | ORLEANS | FAIR | 508 | 2020-04-19 09:25 | 2020-04-19 15:02 | 2020-04-19 17:53 | 21844 | LFUS | 33236 | 38237465803 | 2014 | ENOI | 1 | 43 | EARM | Equipment Failure - Crossarm | N | dead end crossarm broken, crew changed out arm | -90.1261 | 29.9423 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-19 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 52 | 1328352970 | Yes | ORLEANS | FAIR | 215 | 2020-04-19 12:15 | 2020-04-19 15:20 | 2020-04-19 15:50 | 11180 | LFUS | 21569 | 3903748059 | 904 | ENOI | 1 | 52 | EARM | Equipment Failure - Crossarm | N | crossarm broke changed out lateral arm and switches | -90.1004 | 29.9827 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-19 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 21 | 1328352964 | Yes | ORLEANS | FAIR | 222 | 2020-04-19 12:15 | 2020-04-19 12:59 | 2020-04-19 15:57 | 4662 | LFUS | 21568 | 3904648072 | 904 | ENOI | 1 | 21 | EARM | Equipment Failure - Crossarm | N | Crew on the way to replace cross arms | -90.1001 | 29.9831 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-19 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 8 | 1328475576 | Yes | EAST ORLEANS | THDR | 115 | 2020-04-20 07:05 | 2020-04-20 07:24 | 2020-04-20 09:00 | 920 | TFUS | 62115 | 40549488407 | 1702 | ENOI | 6 | 8 | LGHT | Lightning | N | blown fuse on transformer; refused | -90.0522 | 30.0037 | Lightning | Transformer Fuse | Lightning | 2020-04-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 9 | 1328475686 | Yes | ORLEANS | THDR | 112 | 2020-04-20 07:06 | 2020-04-20 07:44 | 2020-04-20 08:58 | 1008 | TFUS | 60379 | 39506479343 | 1705 | ENOI | 1 | 9 | LGHT | Lightning | N | Lightning; out from storm last night | -90.0856 | 29.9791 | Lightning | Transformer Fuse | Lightning | 2020-04-20 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 5 | 1328475910 | Yes | EAST ORLEANS | FAIR | 279 | 2020-04-20 07:15 | 2020-04-20 10:09 | 2020-04-20 11:54 | 1395 | TFUS | 1125645 | 43513495761 | 1612 | ENOI | 6 | 5 | ESEC | Secondary/Service Conductor | N | serparated open wire secondary tangled in tree; refused transformer | -89.9585 | 30.023 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-20 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 29 | 1328476758 | Yes | ORLEANS | FAIR | 91 | 2020-04-20 07:25 | 2020-04-20 08:27 | 2020-04-20 08:56 | 2639 | LFUS | 27933 | 4002247569 | 1712 | ENOI | 1 | 29 | LGHT | Lightning | N | Bc phases blown. Possibly from bad weather last night | -90.0694 | 29.9689 | Lightning | Line Fuse | Lightning | 2020-04-20 | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 1 | 1328478124 | Yes | EAST ORLEANS | FAIR | 289 | 2020-04-20 08:09 | 2020-04-20 10:22 | 2020-04-20 12:59 | 289 | TFUS | 64068 | 40338487485 | 1702 | ENOI | 6 | 1 | EARR | Equipment Failure - Arrestor | N | cleared blown arrestor and refused transformer | -90.0593 | 30.0012 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 61 | 1328538247 | Yes | ORLEANS | FAIR | 99 | 2020-04-21 07:04 | 2020-04-21 08:12 | 2020-04-21 08:43 | 6039 | LFUS | 33188 | 3971145871 | 2146 | ENOI | 1 | 61 | ASQL | Animal - Squirrel | N | b phase blown; taken out bby squirrel | -90.0798 | 29.9224 | Animal | Line Fuse | Animal | 2020-04-21 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 6 | 1328538517 | Yes | ORLEANS | FAIR | 113 | 2020-04-21 07:26 | 2020-04-21 08:15 | 2020-04-21 09:19 | 678 | TFUS | 17319 | 39682493252 | 510 | ENOI | 1 | 6 | UNKN | Inspected Unknown | N | blown fuse; refused ok | -90.0796 | 30.0174 | Other | Transformer Fuse | Other | 2020-04-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 9 | 1328552224 | Yes | ORLEANS | FAIR | 59 | 2020-04-21 14:02 | 2020-04-21 14:15 | 2020-04-21 15:01 | 531 | TFUS | 63578 | 39213462104 | 1924 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption; crew changing out wilson rack | -90.0953 | 29.9318 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-21 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 1 | 1328582850 | Yes | EAST ORLEANS | FAIR | 453 | 2020-04-22 09:07 | 2020-04-22 09:07 | 2020-04-22 16:40 | 453 | SERV | SERVICE | 44281499767 | 1601 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Need to crew to either locate or run new underground secondary service in the rear. Notified O.C. C. Bowers and you can put Brian Garnett s crew on the job. Made customer contact, advised of crew coming to make repairs. | -89.9339 | 30.0337 | Equipment Failure | Service Conductor | Equipment Failure | 2020-04-22 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 120 | 1328608621 | Yes | EAST ORLEANS | WIND | 96 | 2020-04-22 15:05 | 2020-04-22 16:27 | 2020-04-22 16:42 | 11520 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 120 | VHCL | Vehicle | N | Crew on site replacing broken pole | -90.0356 | 29.9933 | Public Damage | Substation Breaker | Public Damage | 2020-04-22 | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 10 | 1328634738 | Yes | EAST ORLEANS | WIND | 280 | 2020-04-22 17:08 | 2020-04-22 21:25 | 2020-04-22 21:48 | 2800 | TFUS | 75706 | 4086548444 | 612 | ENOI | 6 | 10 | VHCL | Vehicle | N | Had to leave transformer out for safety to replace broken pole, PID CHG to NO, related to #1328608621 (DGault) | -90.0424 | 29.9925 | Public Damage | Transformer Fuse | Public Damage | 2020-04-22 | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 37 | 1328777629 | Yes | EAST ORLEANS | THDR | 94 | 2020-04-23 05:36 | 2020-04-23 05:49 | 2020-04-23 07:10 | 3478 | LFUS | 28007 | 4153647424 | 2347 | ENOI | 6 | 37 | EFLK | Equipment Failure - Fuse Link | N | REFUSED OKAY | -90.0216 | 29.9645 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-23 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 6 | 1328795239 | Yes | ORLEANS | FAIR | 162 | 2020-04-23 06:27 | 2020-04-23 06:27 | 2020-04-23 09:09 | 972 | XFMR | 56611 | 39891486118 | 1703 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N |  | -90.0736 | 29.9976 | Equipment Failure | Transformer | Equipment Failure | 2020-04-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 4 | 1328795242 | Yes | ORLEANS | FAIR | 160 | 2020-04-23 06:28 | 2020-04-23 06:28 | 2020-04-23 09:08 | 640 | XFMR | 56163 | 39891486338 | 1703 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N |  | -90.0732 | 29.9982 | Equipment Failure | Transformer | Equipment Failure | 2020-04-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 327 | 1328799805 | Yes | ORLEANS | FAIR | 333 | 2020-04-23 08:00 | 2020-04-23 08:14 | 2020-04-23 13:33 | 108891 | OPEN | 4009046539 | 4009046539 | 1826 | ENOI | 1 | 327 | EARM | Equipment Failure - Crossarm | N | Equipment Failure -Broken Crossarm | -90.0676 | 29.9406 | Equipment Failure | Open | Equipment Failure | 2020-04-23 | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 5 | 1328830984 | Yes | EAST ORLEANS | THDR | 130 | 2020-04-23 10:48 | 2020-04-23 10:48 | 2020-04-23 12:58 | 650 | TFUS | 60539 | 41083487388 | 616 | ENOI | 6 | 5 | ECON | Equipment Failure - Connector / Sleeve | N | Hot leg connection burned at the pole.Also had to refuse stinger pot. Customer back in lights. Made customer contact, he verified that all equipment is up and running. | -90.0353 | 30.0007 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-23 | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 20 | 1328876112 | Yes | ORLEANS | FAIR | 191 | 2020-04-23 12:29 | 2020-04-23 12:32 | 2020-04-23 15:40 | 3820 | TFUS | 498854 | 38093471229 | B0527 | ENOI | 1 | 20 | VINE | Vine Growing into Line | N | REMOVED REFUSED | -90.1305 | 29.9572 | Vegetation | Transformer Fuse | Vegetation | 2020-04-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 15 | 1328992897 | Yes | ORLEANS | FAIR | 59 | 2020-04-25 06:54 | 2020-04-25 06:59 | 2020-04-25 07:53 | 885 | LFUS | 61341 | 3817446224 | 2013 | ENOI | 1 | 15 | VOHL | Overhanging Limb | N | REFUSED OKAY | -90.1283 | 29.9326 | Vegetation | Line Fuse | Vegetation | 2020-04-25 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 1536 | 1329000225 | Yes | EAST ORLEANS | FAIR | 45 | 2020-04-25 09:41 | 2020-04-25 10:51 | 2020-04-25 10:26 | 69120 | VFI | 27486 | 4366350629 | 2213 | ENOI | 6 | 1536 | HEID | Improper Design (Describe in Remarks Field) | N | Equipment labeled incorrectly from manufacturer: Fdr carrying portion of 2217 & all of Fdr 1603 & Fdr #1609 at the time | -97.0758 | 27.9066 | Human Error | Vacuum Fault Interrupter | Human Error | 2020-04-25 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 38 | 1329000156 | Yes | EAST ORLEANS | FAIR | 55 | 2020-04-25 09:43 | 2020-04-25 09:54 | 2020-04-25 10:38 | 2090 | LFUS | 36879F | 4372350002 | 1609 | ENOI | 6 | 38 | HEID | Improper Design (Describe in Remarks Field) | N | Equipment labeled incorrectly from manufacture | -97.0758 | 27.9066 | Human Error | Line Fuse | Human Error | 2020-04-25 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 1 | 1329002900 | Yes | ORLEANS | FAIR | 117 | 2020-04-25 10:22 | 2020-04-25 10:22 | 2020-04-25 12:19 | 117 | SERV | METER | 39235459460 | 1923 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | bad ami meter | -90.0949 | 29.9245 | Other | Service Conductor | Other | 2020-04-25 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 7 | 1329047348 | Yes | EAST ORLEANS | FAIR | 26 | 2020-04-25 22:10 | 2020-04-25 22:14 | 2020-04-25 22:36 | 182 | TFUS | 54299 | 43126496588 | 1611 | ENOI | 6 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9704 | 30.0254 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-25 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 3 | 1329090957 | Yes | ORLEANS | FAIR | 118 | 2020-04-27 00:11 | 2020-04-27 00:11 | 2020-04-27 02:09 | 354 | DIS | 23834 | 3957947276 | 1511 | ENOI | 1 | 3 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0834 | 29.9609 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-04-27 | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 35 | 1329100216 | Yes | ORLEANS | FAIR | 149 | 2020-04-27 06:59 | 2020-04-27 07:47 | 2020-04-27 09:28 | 5215 | LFUS | 37696 | 3962045874 | 1911 | ENOI | 1 | 35 | UNKN | Inspected Unknown | N | refused ok | -90.0828 | 29.9224 | Other | Line Fuse | Other | 2020-04-27 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 19 | 1329100712 | Yes | ORLEANS | FAIR | 135 | 2020-04-27 07:12 | 2020-04-27 07:18 | 2020-04-27 09:27 | 2565 | TFUS | 64298 | 39633458845 | 2147 | ENOI | 1 | 19 | UNKN | Inspected Unknown | N | refused ok | -90.0822 | 29.9228 | Other | Transformer Fuse | Other | 2020-04-27 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 39 | 1329102057 | Yes | ORLEANS | FAIR | 69 | 2020-04-27 08:14 | 2020-04-27 08:20 | 2020-04-27 09:23 | 2691 | LFUS | 33500 | 38848458600 | 1921 | ENOI | 1 | 39 | EFLK | Equipment Failure - Fuse Link | N | Refused transformer and lfus | -90.1071 | 29.9224 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-27 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 29 | 1329133998 | Yes | EAST ORLEANS | FAIR | 216 | 2020-04-28 04:32 | 2020-04-28 07:31 | 2020-04-28 08:08 | 6264 | LFUS | 82569 | 4192847736 | 2347 | ENOI | 6 | 29 | ASQL | Animal - Squirrel | N | Refused c phase lat cut out customers back in | -90.009 | 29.9728 | Animal | Line Fuse | Animal | 2020-04-28 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 14 | 1329158231 | Yes | EAST ORLEANS | FAIR | 121 | 2020-04-28 13:44 | 2020-04-28 13:44 | 2020-04-28 15:45 | 1694 | TFUS | 527849 | 40963476191 | 611 | ENOI | 6 | 14 | SCHD | Scheduled Interruption | N | back on | -90.0395 | 29.9701 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-04-28 | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 5 | 1329231073 | Yes | ORLEANS | THDR | 59 | 2020-04-28 20:43 | 2020-04-28 20:46 | 2020-04-28 21:42 | 295 | TFUS | 1003896 | 38911489462 | 413 | ENOI | 1 | 5 | VLGL | Tree/Limb Growing Inside R.O.W. | N | cleared palm tree from transformer. refused ok. per 310 | -90.1039 | 30.0071 | Vegetation | Transformer Fuse | Vegetation | 2020-04-28 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 89 | 1329232321 | Yes | ORLEANS | THDR | 190 | 2020-04-28 20:50 | 2020-04-28 22:54 | 2020-04-29 | 16910 | LFUS | 37943 | 3839445846 | 1914 | ENOI | 1 | 89 | VLFL | Tree On Line Outside R.O.W | N | tree on line | -90.1215 | 29.9221 | Vegetation | Line Fuse | Vegetation | 2020-04-28 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 4
2020 | 52 | 1329234929 | Yes | ORLEANS | THDR | 699 | 2020-04-28 20:56 | 2020-04-29 06:38 | 2020-04-29 08:35 | 36348 | LFUS | 21504 | 3917546299 | 1925 | ENOI | 1 | 52 | LGHT | Lightning | N | refused lateral, out due to overnight storm, no other problems found | -90.0967 | 29.9343 | Lightning | Line Fuse | Lightning | 2020-04-28 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 8 | 1329239534 | Yes | ORLEANS | THDR | 494 | 2020-04-28 21:11 | 2020-04-28 23:44 | 2020-04-29 05:25 | 3952 | TFUS | 71045 | 40352477036 | 1709 | ENOI | 1 | 8 | EARM | Equipment Failure - Crossarm | N | broke arm on lateral; secured; will make pink ticket to replace HW | -90.0589 | 29.9725 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-28 | DLIN | C | Council District C | Kristin Palmer | 70116 | 4
2020 | 37 | 1329238465 | Yes | ORLEANS | RAIN | 105 | 2020-04-28 21:12 | 2020-04-28 21:54 | 2020-04-28 22:57 | 3885 | LFUS | 44646 | 3853148813 | 410 | ENOI | 1 | 37 | SLAK | Slack Conductor / Loose Connection | N | found slack span in front of 247 26th st. refused ok got together during storm. per 310 | -90.1159 | 30.0035 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-28 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 5 | 1329240394 | Yes | EAST ORLEANS | THDR | 55 | 2020-04-28 21:14 | 2020-04-28 21:20 | 2020-04-28 22:09 | 275 | TFUS | 68163 | 42021478356 | 2325 | ENOI | 6 | 5 | VINE | Vine Growing into Line | N | refused trans..cleared vines | -90.0061 | 29.9756 | Vegetation | Transformer Fuse | Vegetation | 2020-04-28 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 19 | 1329244026 | Yes | EAST ORLEANS | THDR | 150 | 2020-04-28 21:31 | 2020-04-29 00:46 | 2020-04-29 00:01 | 2850 | LFUS | 27222 | 4250450158 | 2211 | ENOI | 6 | 19 | EELB | Equipment Failure - Elbow | N | replaced elbow | -89.9902 | 30.0392 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-28 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 9 | 1329246239 | Yes | EAST ORLEANS | THDR | 256 | 2020-04-28 21:47 | 2020-04-28 21:47 | 2020-04-29 02:03 | 2304 | TFUS | 78585 | 40983474510 | 622 | ENOI | 6 | 9 | EARM | Equipment Failure - Crossarm | N | fire dept put lat x arm out..temp safe will turn ticket.. | -90.039 | 29.9657 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-28 | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 5 | 1329248043 | Yes | EAST ORLEANS | THDR | 455 | 2020-04-28 21:50 | 2020-04-29 01:02 | 2020-04-29 05:25 | 2275 | TFUS | 58802 | 48464512640 | 1204 | ENOI | 6 | 5 | EARM | Equipment Failure - Crossarm | N | broke lateral arm | -89.8012 | 30.0678 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-28 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 168 | 1329252770 | Yes | ORLEANS | THDR | 536 | 2020-04-28 22:01 | 2020-04-29 06:30 | 2020-04-29 06:57 | 90048 | LFUS | 27894 | 3922646091 | 1924 | ENOI | 1 | 168 | EARM | Equipment Failure - Crossarm | N | Broken corner structure at Amelia & Dryades - Crew repaired - Portion of fdr 1922 dropped out for repairs | -90.0952 | 29.9286 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-28 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 71 | 1329258577 | Yes | EAST ORLEANS | THDR | 261 | 2020-04-28 22:25 | 2020-04-29 01:22 | 2020-04-29 02:46 | 18531 | LFUS | 27162 | 4203949893 | 2211 | ENOI | 6 | 71 | EELB | Equipment Failure - Elbow | N | changed out bad elbow in front of 7143 mayo blvd | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-28 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 62 | 1329268983 | Yes | ORLEANS | THDR | 197 | 2020-04-28 23:18 | 2020-04-29 01:41 | 2020-04-29 02:35 | 12214 | LFUS | 27741 | 3918647289 | 2025 | ENOI | 1 | 62 | LGHT | Lightning | N | b phase came down; picked up and refused | -90.096 | 29.9616 | Lightning | Line Fuse | Lightning | 2020-04-28 | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 265 | 1329318727 | Yes | EAST ORLEANS | THDR | 75 | 2020-04-29 04:10 | 2020-04-29 05:22 | 2020-04-29 05:25 | 19875 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 265 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.8029 | 30.0695 | Scheduled Interruption | Recloser | Scheduled Interruption | 2020-04-29 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 3 | 1329343316 | Yes | EAST ORLEANS | THDR | 259 | 2020-04-29 04:57 | 2020-04-29 04:57 | 2020-04-29 09:16 | 777 | TFUS | 31958 | 41345479463 | 621 | ENOI | 6 | 3 | EARR | Equipment Failure - Arrestor | N | crew is enroute to repair cable | -90.027 | 29.9789 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-29 | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 38 | 1329433498 | Yes | ORLEANS | THDR | 166 | 2020-04-29 06:54 | 2020-04-29 06:54 | 2020-04-29 09:40 | 6308 | LFUS | 21572 | 3881948253 | 903 | ENOI | 1 | 38 | LGHT | Lightning | N | refused b phase taken out by lightning | -90.1071 | 29.9879 | Lightning | Line Fuse | Lightning | 2020-04-29 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 64 | 1329433580 | Yes | ORLEANS | THDR | 167 | 2020-04-29 06:54 | 2020-04-29 06:54 | 2020-04-29 09:41 | 10688 | LFUS | 27794 | 3880948210 | 903 | ENOI | 1 | 64 | LGHT | Lightning | N | refused a phase taken out by lightning | -90.1073 | 29.987 | Lightning | Line Fuse | Lightning | 2020-04-29 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 16 | 1329386395 | Yes | EAST ORLEANS | THDR | 160 | 2020-04-29 07:15 | 2020-04-29 07:15 | 2020-04-29 09:55 | 2560 | TFUS | 1522654 | 42381492895 | 1607 | ENOI | 6 | 16 | VLFL | Tree On Line Outside R.O.W | N | Service man MJackson fixed hot leg on pole fix service to the house and refused transfomer. Due to ploe rocked when tree fell | -89.9942 | 30.0156 | Vegetation | Transformer Fuse | Vegetation | 2020-04-29 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 35 | 1329390864 | Yes | ORLEANS | THDR | 160 | 2020-04-29 07:25 | 2020-04-29 08:14 | 2020-04-29 10:05 | 5600 | LFUS | 21643 | 3970248481 | 1703 | ENOI | 1 | 35 | LGHT | Lightning | N |  | -90.0793 | 29.9941 | Lightning | Line Fuse | Lightning | 2020-04-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 172 | 1329397017 | Yes | EAST ORLEANS | THDR | 215 | 2020-04-29 07:55 | 2020-04-29 10:59 | 2020-04-29 11:30 | 36980 | LFUS | 25610 | 4335750498 | 2214 | ENOI | 6 | 172 | EELB | Equipment Failure - Elbow | N | Replace elbows at location CGould | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-29 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 19 | 1329397914 | Yes | EAST ORLEANS | RAIN | 210 | 2020-04-29 08:00 | 2020-04-29 10:34 | 2020-04-29 11:30 | 3990 | LFUS | 25651 | 4338850670 | 2214 | ENOI | 6 | 19 | EELB | Equipment Failure - Elbow | N | Replaced elbow at location CGould | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-04-29 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 42 | 1329427605 | Yes | ORLEANS | THDR | 161 | 2020-04-29 08:16 | 2020-04-29 10:28 | 2020-04-29 10:57 | 6762 | LFUS | 36644 | 4028748693 | 1708 | ENOI | 1 | 42 | LGHT | Lightning | N | 1 span #6 primary down - crew to pick up | -90.0607 | 29.9999 | Lightning | Line Fuse | Lightning | 2020-04-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 965 | 1329525099 | Yes | ORLEANS | THDR | 281 | 2020-04-29 08:45 | 2020-04-29 08:45 | 2020-04-29 13:26 | 271165 | DIS | 39544 | 38598459792 | 1917 | ENOI | 1 | 965 | EMER | Emergency Switching | N | Broken cross arm at location....switching was done to isolate....repaired arm and switched back in | -90.1148 | 29.9256 | Other | Disconnect Switch | Emergency Switching | 2020-04-29 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 4
2020 | 5 | 1329422545 | Yes | ORLEANS | THDR | 42 | 2020-04-29 09:09 | 2020-04-29 09:09 | 2020-04-29 09:51 | 210 | TFUS | 491803 | 38262464952 | 2014 | ENOI | 1 | 5 | VINE | Vine Growing into Line | N | refused transformer OK per A.Bengston - vines growing on transformer | -90.1253 | 29.94 | Vegetation | Transformer Fuse | Vegetation | 2020-04-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 3 | 1329426889 | Yes | EAST ORLEANS | WIND | 104 | 2020-04-29 09:21 | 2020-04-29 09:21 | 2020-04-29 11:05 | 312 | LFUS | 21238 | 44436494079 | 1203 | ENOI | 6 | 3 | VINE | Vine Growing into Line | N | Lat was taken out during high wind. re fused ok made customer contact MJackson | -89.9294 | 30.018 | Vegetation | Line Fuse | Vegetation | 2020-04-29 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 3 | 1329485598 | Yes | EAST ORLEANS | THDR | 105 | 2020-04-29 11:31 | 2020-04-29 12:06 | 2020-04-29 13:16 | 315 | LFUS | 76989 | 4242050231 | 2211 | ENOI | 6 | 3 | VLGL | Tree/Limb Growing Inside R.O.W. | N | A&B phase blown due to tree limb fell across phases. Made customer contact MJackson | -89.9927 | 30.0413 | Vegetation | Line Fuse | Vegetation | 2020-04-29 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 105 | 1329512455 | Yes | EAST ORLEANS | THDR | 148 | 2020-04-29 13:20 | 2020-04-29 14:47 | 2020-04-29 15:48 | 15540 | LFUS | 32139 | 4098847474 | 622 | ENOI | 6 | 105 | SCHD | Scheduled Interruption | N | crew is onsite making repairs | -90.0389 | 29.9661 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-04-29 | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 16 | 1329520003 | Yes | ORLEANS | THDR | 59 | 2020-04-29 13:43 | 2020-04-29 13:43 | 2020-04-29 14:42 | 944 | TFUS | 62626 | 3989947531 | 1512 | ENOI | 1 | 16 | LGHT | Lightning | N | weather |  |  | Lightning | Transformer Fuse | Lightning | 2020-04-29 | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 5 | 1329550751 | Yes | ORLEANS | THDR | 285 | 2020-04-29 15:27 | 2020-04-29 15:34 | 2020-04-29 20:12 | 1425 | TFUS | 59457 | 39625475328 | 907 | ENOI | 1 | 5 | FTNU | Foreign Trouble - Neighboring Utility | N | att&t knocked down primary RELATED TO TKT#1329589613 (A.STEWART) | -90.0821 | 29.968 | Foreign Trouble | Transformer Fuse | Foreign Trouble | 2020-04-29 | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 14 | 1329560681 | Yes | ORLEANS | THDR | 175 | 2020-04-29 15:51 | 2020-04-29 18:18 | 2020-04-29 18:46 | 2450 | TFUS | 1343359 | 39217462742 | 1925 | ENOI | 1 | 14 | LGHT | Lightning | N | weather | -90.0954 | 29.9336 | Lightning | Transformer Fuse | Lightning | 2020-04-29 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 10 | 1329566140 | Yes | EAST ORLEANS | THDR | 156 | 2020-04-29 16:03 | 2020-04-29 16:03 | 2020-04-29 18:39 | 1560 | TFUS | 61091 | 40429488201 | 1702 | ENOI | 6 | 10 | LGHT | Lightning | N | wather | -90.056 | 30.0032 | Lightning | Transformer Fuse | Lightning | 2020-04-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 15 | 1329643305 | Yes | ORLEANS | FAIR | 424 | 2020-04-29 21:38 | 2020-04-29 21:46 | 2020-04-30 04:42 | 6360 | TFUS | 1453518 | 39598457845 | 1911 | ENOI | 1 | 15 | EARM | Equipment Failure - Crossarm | N |  | -90.0833 | 29.9201 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-04-29 | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 23 | 1329716247 | Yes | EAST ORLEANS | FAIR | 143 | 2020-05-01 02:34 | 2020-05-01 02:48 | 2020-05-01 04:57 | 3289 | LFUS | 36878F | 4369350043 | 1609 | ENOI | 6 | 23 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | serviceman cleared grass from cub 488 refused okay | -97.0758 | 27.9066 | Other | Line Fuse | Other | 2020-05-01 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 31 | 1329727435 | Yes | ORLEANS | FAIR | 66 | 2020-05-01 10:26 | 2020-05-01 10:46 | 2020-05-01 11:32 | 2046 | SBKR | 1543 | 3950446996 | 1543 | ENOI | 1 | 31 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N | bird contacted B & C phase on T.P. # D01648; Repairs made & fdr restored | -90.086 | 29.9533 | Animal | Substation Breaker | Animal | 2020-05-01 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 18 | 1329769335 | Yes | EAST ORLEANS | FAIR | 137 | 2020-05-02 08:08 | 2020-05-02 08:47 | 2020-05-02 10:25 | 2466 | LFUS | 71456 | 4335750736 | 2217 | ENOI | 6 | 18 | EFLK | Equipment Failure - Fuse Link | N | Patrolled lateral refused lateral still holding | -89.963 | 30.0548 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-02 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 29 | 1329769508 | Yes | EAST ORLEANS | FAIR | 137 | 2020-05-02 08:11 | 2020-05-02 08:17 | 2020-05-02 10:28 | 3973 | LFUS | 21794 | 4337850707 | 2217 | ENOI | 6 | 29 | EFLK | Equipment Failure - Fuse Link | N | Refused lateral customer back on | -89.9624 | 30.054 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-02 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 88 | 1329776884 | Yes | ORLEANS | FAIR | 115 | 2020-05-02 12:49 | 2020-05-02 13:02 | 2020-05-02 14:44 | 13685 | LFUS | 21073 | 3876146762 | 1916 | ENOI | 1 | 88 | EARM | Equipment Failure - Crossarm | N | Replaced broken braces - B PHASE ONLY | -90.1095 | 29.9473 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-02 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 5
2020 | 1 | 1329779166 | Yes | EAST ORLEANS | FAIR | 46 | 2020-05-02 14:29 | 2020-05-02 14:29 | 2020-05-02 15:15 | 46 | SERV | METER | 4118648377 | 626 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N |  | -90.0324 | 29.9907 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-02 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 1 | 1329813568 | Yes | ORLEANS | FAIR | 114 | 2020-05-03 14:58 | 2020-05-03 14:58 | 2020-05-03 16:52 | 114 | SERV | SERVICE | 38887458254 | 1921 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | PID in progress HW replaced damage service | -90.1058 | 29.9215 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-03 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 12 | 1329816432 | Yes | ORLEANS | FAIR | 248 | 2020-05-03 17:20 | 2020-05-03 20:30 | 2020-05-03 21:28 | 2976 | LFUS | 17733 | 3864448471 | 408 | ENOI | 1 | 12 | VHCL | Vehicle | N | crew replacing broken pole | -90.1125 | 29.9942 | Public Damage | Line Fuse | Public Damage | 2020-05-03 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 119 | 1329824949 | Yes | ORLEANS | FAIR | 181 | 2020-05-04 01:29 | 2020-05-04 02:54 | 2020-05-04 04:30 | 21539 | LFUS | 21073 | 3876146762 | 1916 | ENOI | 1 | 119 | EMER | Emergency Switching | N | crew replacing cross arm on S Rocheblave | -90.1095 | 29.9473 | Other | Line Fuse | Emergency Switching | 2020-05-04 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 5
2020 | 17 | 1329905796 | Yes | ORLEANS | FAIR | 89 | 2020-05-05 11:08 | 2020-05-05 11:08 | 2020-05-05 12:38 | 1513 | LFUS | 75828 | 3989347536 | 1512 | ENOI | 1 | 17 | UNKN | Inspected Unknown | N | c phase on lateral was blown. inspected unknown. refused ok. | -90.0736 | 29.968 | Other | Line Fuse | Other | 2020-05-05 | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 11 | 1329925513 | Yes | ORLEANS | FAIR | 142 | 2020-05-05 15:46 | 2020-05-05 16:06 | 2020-05-05 18:08 | 1562 | TFUS | 1000489 | 39821458800 | 2147 | ENOI | 1 | 11 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0764 | 29.9226 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-05 | DLIN | B | Council District B | Jay Banks | 70130 | 5
2020 | 5 | 1329930285 | Yes | ORLEANS | FAIR | 174 | 2020-05-05 17:36 | 2020-05-05 18:17 | 2020-05-05 20:30 | 870 | XFMR | 1596406 | 3858348778 | 407 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | changed bad xfmr | -90.1146 | 30.0027 | Equipment Failure | Transformer | Equipment Failure | 2020-05-05 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 14 | 1329935577 | Yes | ORLEANS | FAIR | 136 | 2020-05-05 21:11 | 2020-05-05 21:11 | 2020-05-05 23:27 | 1904 | XFMR | 64432 | 39635478518 | 1705 | ENOI | 1 | 14 | ETRD | Equipment Failure - Transformer | N | bad transformer crew replaced | -90.0816 | 29.9767 | Equipment Failure | Transformer | Equipment Failure | 2020-05-05 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 7 | 1329965434 | Yes | ORLEANS | FAIR | 50 | 2020-05-06 09:10 | 2020-05-06 09:10 | 2020-05-06 10:00 | 350 | TFUS | 1165240 | 39842492859 | 510 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | crew on site | -90.0745 | 30.016 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-05-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 4 | 1329995258 | Yes | ORLEANS | FAIR | 152 | 2020-05-06 17:02 | 2020-05-06 17:02 | 2020-05-06 19:34 | 608 | TFUS | 23082 | 38455485577 | 410 | ENOI | 1 | 4 | ASQL | Animal - Squirrel | N | Taken out by squirrel refused ok | -90.1185 | 29.9967 | Animal | Transformer Fuse | Animal | 2020-05-06 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 29 | 1330015752 | Yes | ORLEANS | FAIR | 150 | 2020-05-07 06:10 | 2020-05-07 06:14 | 2020-05-07 08:40 | 4350 | LFUS | 27933 | 4002247569 | 1712 | ENOI | 1 | 29 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons were tangled in b and c phase causing the lat fuse to blow. balloons removed and fuses replaced HW | -90.0693 | 29.9688 | Other | Line Fuse | Other | 2020-05-07 | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 1 | 1330020010 | Yes | ORLEANS CBD | FAIR | 324 | 2020-05-07 08:37 | 2020-05-07 08:37 | 2020-05-07 14:01 | 324 | TFUS | 571537 | 3968246818 | 1543 | ENOI | 4 | 1 | AOTH | Animal - Other (Describe in Remarks Field) | N | a bird contacted switch in station | -90.0805 | 29.9484 | Animal | Transformer Fuse | Animal | 2020-05-07 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 10 | 1330020031 | Yes | ORLEANS | FAIR | 443 | 2020-05-07 08:38 | 2020-05-07 08:38 | 2020-05-07 16:01 | 4430 | TFUS | 62237 | 39248457780 | 1922 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Notified all customers | -90.0946 | 29.9198 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-05-07 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 6 | 1330023903 | Yes | ORLEANS | FAIR | 84 | 2020-05-07 09:16 | 2020-05-07 09:24 | 2020-05-07 10:40 | 504 | TFUS | 68159 | 38939477821 | 2026 | ENOI | 1 | 6 | ASQL | Animal - Squirrel | N | refused transformer, taken out by squirrel, installed animal gaurd | -90.1036 | 29.9751 | Animal | Transformer Fuse | Animal | 2020-05-07 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 387 | 1330059994 | Yes | EAST ORLEANS | FAIR | 46 | 2020-05-07 21:58 | 2020-05-07 22:42 | 2020-05-07 22:44 | 17802 | LFUS | 17996 | 4139649803 | 1010 | ENOI | 6 | 387 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | tranformer hanger broke | -90.0252 | 30.0298 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-07 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 60 | 1330155962 | Yes | ORLEANS | THDR | 176 | 2020-05-08 18:15 | 2020-05-08 18:20 | 2020-05-08 21:11 | 10560 | LFUS | 37784 | 3981748046 | 1709 | ENOI | 1 | 60 | EARM | Equipment Failure - Crossarm | N | REPAIRED CROSSARM | -90.0757 | 29.9822 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-08 | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 74 | 1330165160 | Yes | ORLEANS | THDR | 120 | 2020-05-08 20:03 | 2020-05-08 21:33 | 2020-05-08 22:03 | 8880 | LFUS | 27707 | 3919647432 | 912 | ENOI | 1 | 74 | EARM | Equipment Failure - Crossarm | N | Broken cross arm replaced | -90.0954 | 29.9654 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-08 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 46 | 1330168149 | Yes | ORLEANS | THDR | 118 | 2020-05-08 21:18 | 2020-05-08 21:57 | 2020-05-08 23:16 | 7788 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 46 | LGHT | Lightning | N | weather b phase taken out by lightning | -90.0879 | 29.975 | Lightning | Line Fuse | Lightning | 2020-05-08 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 546 | 1330171041 | Yes | EAST ORLEANS | THDR | 59 | 2020-05-08 22:46 | 2020-05-08 23:21 | 2020-05-08 23:45 | 32214 | RCLR | 24641 | 4090648904 | 617 | ENOI | 6 | 546 | EARM | Equipment Failure - Crossarm | N | broken x arm braces | -90.0409 | 30.0054 | Equipment Failure | Recloser | Equipment Failure | 2020-05-08 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 17 | 1330207494 | Yes | ORLEANS | FAIR | 110 | 2020-05-09 18:04 | 2020-05-09 18:32 | 2020-05-09 19:55 | 1870 | TFUS | 60031 | 38934473379 | 2017 | ENOI | 1 | 17 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.1039 | 29.9629 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-09 | DLIN | B | Council District B | Jay Banks | 70125 | 5
2020 | 12 | 1330225085 | Yes | ORLEANS | FAIR | 160 | 2020-05-10 07:02 | 2020-05-10 08:41 | 2020-05-10 09:42 | 1920 | TFUS | 61865 | 39010464161 | 1925 | ENOI | 1 | 12 | ASQL | Animal - Squirrel | N | squirrel got across top side of xfmr cleared squirrel refused xfmr | -90.1019 | 29.9376 | Animal | Transformer Fuse | Animal | 2020-05-10 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 8 | 1330245404 | Yes | ORLEANS | FAIR | 140 | 2020-05-10 17:49 | 2020-05-10 19:11 | 2020-05-10 20:09 | 1120 | TFUS | 1349191 | 38430468283 | 2016 | ENOI | 1 | 8 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Taken out by balloon refused ok | -90.1198 | 29.949 | Other | Transformer Fuse | Other | 2020-05-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 24 | 1330267184 | Yes | ORLEANS | FAIR | 85 | 2020-05-11 07:16 | 2020-05-11 07:20 | 2020-05-11 08:42 | 2040 | TFUS | 20432 | 38950495409 | 402 | ENOI | 1 | 24 | AOTH | Animal - Other (Describe in Remarks Field) | N | squirrel refusedSQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.1024 | 30.0234 | Animal | Transformer Fuse | Animal | 2020-05-11 | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 19 | 1330267215 | Yes | ORLEANS | FAIR | 50 | 2020-05-11 07:20 | 2020-05-11 07:36 | 2020-05-11 08:10 | 950 | TFUS | 26730 | 39048496285 | 402 | ENOI | 1 | 19 | ASQL | Animal - Squirrel | N | SQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.0994 | 30.0258 | Animal | Transformer Fuse | Animal | 2020-05-11 | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 16 | 1330267381 | Yes | ORLEANS | FAIR | 47 | 2020-05-11 07:24 | 2020-05-11 07:24 | 2020-05-11 08:11 | 752 | TFUS | 20937 | 38983494277 | 402 | ENOI | 1 | 16 | ASQL | Animal - Squirrel | N | SQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.1015 | 30.0204 | Animal | Transformer Fuse | Animal | 2020-05-11 | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 25 | 1330267400 | Yes | ORLEANS | FAIR | 43 | 2020-05-11 07:27 | 2020-05-11 07:27 | 2020-05-11 08:10 | 1075 | TFUS | 715357T | 38980494050 | 402 | ENOI | 1 | 25 | ASQL | Animal - Squirrel | N | SQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.1016 | 30.0197 | Animal | Transformer Fuse | Animal | 2020-05-11 | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 24 | 1330269146 | Yes | EAST ORLEANS | FAIR | 162 | 2020-05-11 08:15 | 2020-05-11 10:52 | 2020-05-11 10:58 | 3888 | LFUS | 17838 | 4086349242 | 505 | ENOI | 6 | 24 | ASQL | Animal - Squirrel | N | Refused B phase on lateral 17838 and transformer fuse by 4225 Mithra | -90.0422 | 30.0145 | Animal | Line Fuse | Animal | 2020-05-11 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 201 | 1330344055 | Yes | EAST ORLEANS | FAIR | 44 | 2020-05-11 20:01 | 2020-05-11 20:19 | 2020-05-11 20:45 | 8844 | SBKR | 2347 | 4216047802 | 2347 | ENOI | 6 | 201 | FTNU | Foreign Trouble - Neighboring Utility | N | Feeder burned down caused by AT&T pole set next to primary conductors | -90.0217 | 29.9642 | Foreign Trouble | Substation Breaker | Foreign Trouble | 2020-05-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 144 | 1330348082 | Yes | EAST ORLEANS | FAIR | 242 | 2020-05-11 20:09 | 2020-05-11 20:53 | 2020-05-12 00:11 | 8496 | DIS | 23562 | 4155947419 | 622 | ENOI | 6 | 144 | EPRI | Equipment Failure - Primary Conductor | N | Crew on the way to make repairs | -90.0217 | 29.9642 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-05-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 105 | 1330348208 | Yes | EAST ORLEANS | FAIR | 201 | 2020-05-11 20:53 | 2020-05-11 21:20 | 2020-05-12 00:14 | 21105 | DIS | 25786 | 4155947419 | 2345 | ENOI | 6 | 105 | EPRI | Equipment Failure - Primary Conductor | N | Crew on the way to make repairs | -90.0217 | 29.9642 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-05-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 210 | 1330349740 | Yes | EAST ORLEANS | FAIR | 193 | 2020-05-11 21:08 | 2020-05-12 00:09 | 2020-05-12 00:21 | 40530 | DIS | 25785 | 4140347427 | 622 | ENOI | 6 | 210 | EPRI | Equipment Failure - Primary Conductor | N | Cerw on the way to make repairs | -90.0217 | 29.9642 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-05-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 5 | 1330350483 | Yes | ORLEANS | FAIR | 61 | 2020-05-11 21:41 | 2020-05-11 21:49 | 2020-05-11 22:42 | 305 | TFUS | 67437 | 38720465716 | 2016 | ENOI | 1 | 5 | EFLK | Equipment Failure - Fuse Link | N | refused transformer | -90.1108 | 29.942 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-11 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 1 | 1330358845 | Yes | ORLEANS | FAIR | 1118 | 2020-05-12 04:12 | 2020-05-12 04:12 | 2020-05-12 22:51 | 1118 | SBKR | 1515 | 3951946983 | 1515 | ENOI | 1 | 1 | EPRI | Equipment Failure - Primary Conductor | N | Failed cable in manhole #3-1550 | -90.0855 | 29.953 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-05-12 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 5 | 1330425295 | Yes | ORLEANS | FAIR | 310 | 2020-05-12 18:57 | 2020-05-12 20:36 | 2020-05-13 00:07 | 1550 | XFMR | 67437 | 38720465716 | 2016 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | changed out bad transformer | -90.1108 | 29.942 | Equipment Failure | Transformer | Equipment Failure | 2020-05-12 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 1 | 1330426684 | Yes | ORLEANS | FAIR | 217 | 2020-05-12 19:25 | 2020-05-12 20:25 | 2020-05-12 23:02 | 217 | SERV | SERVICE | 39132463733 | 1925 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter opened remotely called amoc and turned on | -90.0981 | 29.9364 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-12 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 534 | 1330432634 | Yes | EAST ORLEANS | FAIR | 60 | 2020-05-12 21:33 | 2020-05-12 22:19 | 2020-05-12 22:33 | 32040 | VFI | 26140 | 4264649768 | 1610 | ENOI | 6 | 534 | AOTH | Animal - Other (Describe in Remarks Field) | N | rat contacted switch in cub. # 8 sw. # 76880 | -97.0758 | 27.9066 | Animal | Vacuum Fault Interrupter | Animal | 2020-05-12 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 102 | 1330445255 | Yes | ORLEANS | FAIR | 184 | 2020-05-13 02:02 | 2020-05-13 04:13 | 2020-05-13 05:06 | 18768 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 102 | SCHD | Scheduled Interruption | N | Outage to replace cross arm | -90.0879 | 29.975 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-05-13 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 96 | 1330491982 | Yes | EAST ORLEANS | FAIR | 122 | 2020-05-13 12:41 | 2020-05-13 14:30 | 2020-05-13 14:43 | 11712 | SWIT | 27036 | 4381950738 | 2213 | ENOI | 6 | 96 | EPRI | Equipment Failure - Primary Conductor | N | bad cable from cub #388 to cub #569 | -97.0758 | 27.9066 | Equipment Failure | Switch | Equipment Failure | 2020-05-13 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 511 | 1330496581 | Yes | EAST ORLEANS | FAIR | 122 | 2020-05-13 12:41 | 2020-05-13 14:45 | 2020-05-13 14:43 | 62342 | VFI | 27422 | 4366350629 | 2213 | ENOI | 6 | 511 | EPRI | Equipment Failure - Primary Conductor | N | bad primary in between cub# 388 to cub # 569 | -97.0758 | 27.9066 | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | 2020-05-13 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 159 | 1330498884 | Yes | EAST ORLEANS | FAIR | 169 | 2020-05-13 12:41 | 2020-05-13 15:03 | 2020-05-13 15:30 | 26871 | LFUS | 26296 | 4381351016 | 2213 | ENOI | 6 | 159 | EPRI | Equipment Failure - Primary Conductor | N | bad cable form cub 388 to 569 | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-13 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 162 | 1330486955 | Yes | EAST ORLEANS | FAIR | 55 | 2020-05-13 13:20 | 2020-05-13 13:20 | 2020-05-13 14:16 | 8910 | LFUS | 27845 | 4085148824 | 617 | ENOI | 6 | 162 | EARM | Equipment Failure - Crossarm | N |  | -90.0426 | 30.0032 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-13 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 1 | 1330510309 | Yes | EAST ORLEANS | FAIR | 257 | 2020-05-13 16:32 | 2020-05-13 16:32 | 2020-05-13 20:49 | 257 | SERV | SERVICE | 42819495980 | 1604 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | repaired | -89.9804 | 30.0239 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-13 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 11 | 1330563121 | Yes | ORLEANS | FAIR | 217 | 2020-05-14 09:53 | 2020-05-14 09:53 | 2020-05-14 13:30 | 2387 | TFUS | 1254921 | 39399464952 | 1915 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | replaced broken lateral switch and removed some milar baloons - lateral fuse not in gis | -90.0896 | 29.9397 | Other | Transformer Fuse | Other | 2020-05-14 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 143 | 1330576602 | Yes | EAST ORLEANS | FAIR | 189 | 2020-05-14 12:31 | 2020-05-14 15:28 | 2020-05-14 15:40 | 27027 | LFUS | 21614 | 4038048940 | 1702 | ENOI | 6 | 143 | EARM | Equipment Failure - Crossarm | N | crew replaced broke arm | -90.0578 | 30.0066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-14 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 6 | 1330606553 | Yes | ORLEANS | FAIR | 53 | 2020-05-14 16:31 | 2020-05-14 16:32 | 2020-05-14 17:24 | 318 | TFUS | 28059 | 39653492706 | 509 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | refused transformer | -90.0805 | 30.0156 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-14 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 577 | 1330633097 | Yes | ORLEANS | FAIR | 53 | 2020-05-14 18:41 | 2020-05-14 19:29 | 2020-05-14 19:34 | 30581 | RCLR | 71181 | 4025148173 | 1709 | ENOI | 1 | 577 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | ballons and streamers on lines cleared and closed recloser KC | -90.0618 | 29.9854 | Other | Recloser | Other | 2020-05-14 | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 23 | 1330678899 | Yes | ORLEANS | THDR | 765 | 2020-05-15 00:16 | 2020-05-15 09:11 | 2020-05-15 13:01 | 17595 | LFUS | 27621 | 3858046356 | 1926 | ENOI | 1 | 23 | EARM | Equipment Failure - Crossarm | N | broken arm in backyard, crew in route | -90.1154 | 29.9361 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-15 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 2113 | 1330665977 | Yes | ORLEANS | THDR | 73 | 2020-05-15 00:38 | 2020-05-15 02:09 | 2020-05-15 01:52 | 154249 | SBKR | 1513 | 3951246991 | 1513 | ENOI | 1 | 2113 | LGHT | Lightning | N | wather, crew rode out, back on now | -90.0857 | 29.9532 | Lightning | Substation Breaker | Lightning | 2020-05-15 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 36 | 1330671279 | Yes | ORLEANS | THDR | 459 | 2020-05-15 00:51 | 2020-05-15 07:25 | 2020-05-15 08:30 | 16524 | DIS | 25403 | 3892346761 | 1553 | ENOI | 1 | 36 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up primary | -90.1043 | 29.9472 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-05-15 | DLIN | B | Council District B | Jay Banks | 70125 | 5
2020 | 1255 | 1330667111 | Yes | ORLEANS | THDR | 86 | 2020-05-15 00:52 | 2020-05-15 02:12 | 2020-05-15 02:18 | 107930 | SBKR | 1553 | 3950346992 | 1553 | ENOI | 1 | 1255 | EPRI | Equipment Failure - Primary Conductor | N | wire down, switched out to pick up load | -90.086 | 29.9532 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-05-15 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 197 | 1330667652 | Yes | ORLEANS | THDR | 212 | 2020-05-15 00:52 | 2020-05-15 02:00 | 2020-05-15 04:24 | 41764 | LFUS | F99218 | 4021947492 | 1712 | ENOI | 1 | 197 | LGHT | Lightning | N | refused a and c phase taken out b weather | -90.0631 | 29.9669 | Lightning | Line Fuse | Lightning | 2020-05-15 | DLIN | C | Council District C | Kristin Palmer | 70116 | 5
2020 | 66 | 1330666974 | Yes | EAST ORLEANS | THDR | 148 | 2020-05-15 00:56 | 2020-05-15 02:22 | 2020-05-15 03:24 | 9768 | LFUS | 27850 | 4092947726 | 622 | ENOI | 6 | 66 | LGHT | Lightning | N | weather, back in | -90.0407 | 29.973 | Lightning | Line Fuse | Lightning | 2020-05-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 5
2020 | 33 | 1330668483 | Yes | EAST ORLEANS | THDR | 203 | 2020-05-15 01:13 | 2020-05-15 01:16 | 2020-05-15 04:36 | 6699 | LFUS | 17848 | 4076649426 | 508 | ENOI | 6 | 33 | LGHT | Lightning | N | weather, back on | -90.0452 | 30.0198 | Lightning | Line Fuse | Lightning | 2020-05-15 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 111 | 1330669967 | Yes | EAST ORLEANS | FAIR | 520 | 2020-05-15 01:30 | 2020-05-15 10:04 | 2020-05-15 10:10 | 57720 | LFUS | 17870 | 4036349293 | 506 | ENOI | 6 | 111 | EARM | Equipment Failure - Crossarm | N | crew replaced broke crossarm | -90.0582 | 30.0161 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 192 | 1330675315 | Yes | EAST ORLEANS | FAIR | 311 | 2020-05-15 03:29 | 2020-05-15 08:17 | 2020-05-15 08:41 | 59712 | NTWK | NTWK | 00000000000 | 1613 | ENOI | 6 | 192 | VHCL | Vehicle | N | vehicle hit cubicle |  |  | Public Damage | Network | Public Damage | 2020-05-15 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 45 | 1330681584 | Yes | ORLEANS | FAIR | 266 | 2020-05-15 06:24 | 2020-05-15 09:56 | 2020-05-15 10:50 | 11970 | LFUS | 17901 | 3974049424 | 510 | ENOI | 1 | 45 | EARM | Equipment Failure - Crossarm | N | Brokwdead end arm at duplesis and aviators crew repaired | -90.0777 | 30.0198 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 14 | 1330680910 | Yes | ORLEANS | THDR | 143 | 2020-05-15 06:27 | 2020-05-15 07:06 | 2020-05-15 08:50 | 2002 | LFUS | 38173 | 39395475907 | 1513 | ENOI | 1 | 14 | LGHT | Lightning | N | refused lateral | -90.0892 | 29.9696 | Lightning | Line Fuse | Lightning | 2020-05-15 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 121 | 1330683233 | Yes | ORLEANS | THDR | 76 | 2020-05-15 07:14 | 2020-05-15 07:53 | 2020-05-15 08:31 | 9196 | LFUS | 27678 | 3904546057 | 1924 | ENOI | 1 | 121 | LGHT | Lightning | N | Lightning | -90.1009 | 29.9277 | Lightning | Line Fuse | Lightning | 2020-05-15 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 1 | 1330684317 | Yes | ORLEANS | THDR | 98 | 2020-05-15 07:48 | 2020-05-15 08:03 | 2020-05-15 09:26 | 98 | LFUS | 22069 | 4020248327 | 627 | ENOI | 1 | 1 | LGHT | Lightning | N | refused b phase on lateral | -90.0634 | 29.9895 | Lightning | Line Fuse | Lightning | 2020-05-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 9 | 1330685705 | Yes | EAST ORLEANS | FAIR | 44 | 2020-05-15 08:15 | 2020-05-15 08:24 | 2020-05-15 08:59 | 396 | TFUS | 25629 | 41409497201 | 1010 | ENOI | 6 | 9 | ASQL | Animal - Squirrel | N | Inspected line and saw several squirrels in the vicinity. Refused pot customers back in lights | -90.025 | 30.0276 | Animal | Transformer Fuse | Animal | 2020-05-15 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 5 | 1330686117 | Yes | EAST ORLEANS | FAIR | 66 | 2020-05-15 08:24 | 2020-05-15 08:24 | 2020-05-15 09:30 | 330 | TFUS | 58802 | 48464512640 | 1204 | ENOI | 6 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.8012 | 30.0678 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-05-15 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 5
2020 | 9 | 1330689839 | Yes | ORLEANS | FAIR | 170 | 2020-05-15 09:15 | 2020-05-15 09:15 | 2020-05-15 12:05 | 1530 | TFUS | 530324 | 3839845814 | 1914 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1213 | 29.9211 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-05-15 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 58 | 1330693033 | Yes | EAST ORLEANS | FAIR | 132 | 2020-05-15 09:38 | 2020-05-15 11:15 | 2020-05-15 11:51 | 7656 | LFUS | 24738 | 4346351051 | 2223 | ENOI | 6 | 58 | ASQL | Animal - Squirrel | N | Had squirrels at the base of the pole. Inspected line and energized main lateral. Also had to pick up had to pick up several spans of down service wire. Follow | -89.9595 | 30.0636 | Animal | Line Fuse | Animal | 2020-05-15 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 37 | 1330693066 | Yes | EAST ORLEANS | FAIR | 131 | 2020-05-15 09:39 | 2020-05-15 10:39 | 2020-05-15 11:50 | 4847 | LFUS | 26048 | 4353050960 | 2217 | ENOI | 6 | 37 | ASQL | Animal - Squirrel | N | Had squirrels at the base of the pole. Inspected line and energized main lateral. Also had to pick up had to pick up several spans of down service wire. Follow up needed. | -89.9574 | 30.061 | Animal | Line Fuse | Animal | 2020-05-15 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 15 | 1330700447 | Yes | EAST ORLEANS | FAIR | 443 | 2020-05-15 10:09 | 2020-05-15 11:33 | 2020-05-15 17:32 | 6645 | LFUS | 21045 | 4109548720 | 616 | ENOI | 6 | 15 | ETRD | Equipment Failure - Transformer | N | crew changed out bad pot | -90.0352 | 30.0002 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-15 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 37 | 1330703024 | Yes | EAST ORLEANS | FAIR | 155 | 2020-05-15 12:10 | 2020-05-15 14:27 | 2020-05-15 14:45 | 5735 | LFUS | 26048 | 4353050960 | 2217 | ENOI | 6 | 37 | EOSC | Equipment Failure - Shield Conductor | N | the shield fell into primary causing the primary dead end to come apart; made repairs and customers back in lights | -89.9574 | 30.061 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-15 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 128 | 1330727105 | Yes | EAST ORLEANS | FAIR | 161 | 2020-05-15 19:10 | 2020-05-15 21:12 | 2020-05-15 21:51 | 20608 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 128 | EPOL | Equipment Failure - Pole | N | crew replaced pole, customers back on | -90.044 | 29.9708 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-15 | DLIN | C | Council District C | Kristin Palmer | 70117 | 5
2020 | 2110 | 1330788429 | Yes | ORLEANS | FAIR | 112 | 2020-05-16 11:22 | 2020-05-16 12:24 | 2020-05-16 13:14 | 334706 | DIS | 23013 | 3947147058 | 1513 | ENOI | 1 | 2110 | EPRI | Equipment Failure - Primary Conductor | N | target on a phase exit cable bet MH 10-545 to MH3-54 | -90.0871 | 29.9551 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-05-16 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 1 | 1330788026 | Yes | ORLEANS | FAIR | 210 | 2020-05-16 13:36 | 2020-05-16 13:36 | 2020-05-16 17:06 | 210 | PRIM | 3844246320 | 3844246320 | 2024 | ENOI | 1 | 1 | ASQL | Animal - Squirrel | N | squirrel took out xfmr; refused and lights back on | -90.1198 | 29.9351 | Animal | Primary Meter | Animal | 2020-05-16 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 109 | 1330837213 | Yes | ORLEANS | FAIR | 465 | 2020-05-17 06:40 | 2020-05-17 12:58 | 2020-05-17 14:25 | 50685 | LFUS | 37763 | 4035847763 | 1709 | ENOI | 1 | 109 | EARM | Equipment Failure - Crossarm | N | crew replaced primary arm | -90.0586 | 29.9744 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-17 | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 72 | 1330839655 | Yes | EAST ORLEANS | FAIR | 124 | 2020-05-17 07:46 | 2020-05-17 09:11 | 2020-05-17 09:50 | 8928 | LFUS | 27691 | 4298950696 | 2215 | ENOI | 6 | 72 | HEMC | Mis-Coordination (Describe in remarks) | N | transformer fuse blown; refused transformer and sub lateral and main lateral | -89.9747 | 30.054 | Human Error | Line Fuse | Human Error | 2020-05-17 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 11 | 1330841866 | Yes | EAST ORLEANS | FAIR | 270 | 2020-05-17 09:01 | 2020-05-17 09:15 | 2020-05-17 13:31 | 2970 | XFMR | 1052320 | 4374351056 | 2217 | ENOI | 6 | 11 | ETRD | Equipment Failure - Transformer | N | crew change out submersible transformer | -89.9506 | 30.0636 | Equipment Failure | Transformer | Equipment Failure | 2020-05-17 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 58 | 1330847188 | Yes | EAST ORLEANS | FAIR | 8 | 2020-05-17 13:02 | 2020-05-17 13:07 | 2020-05-17 13:10 | 464 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 58 | EMER | Emergency Switching | N | Taken out for safety of crew to replace a failed sub. trans | -89.9561 | 30.0595 | Other | Line Fuse | Emergency Switching | 2020-05-17 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 8 | 1330847277 | Yes | EAST ORLEANS | FAIR | 10 | 2020-05-17 13:06 | 2020-05-17 13:06 | 2020-05-17 13:16 | 80 | TFUS | 677437 | 43644509686 | 2217 | ENOI | 6 | 8 | EMER | Emergency Switching | N | Taken out for safety of crew to switch lateral back to normal configuration | -89.9538 | 30.0612 | Other | Transformer Fuse | Emergency Switching | 2020-05-17 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 109 | 1330875601 | Yes | ORLEANS | FAIR | 86 | 2020-05-18 06:53 | 2020-05-18 07:26 | 2020-05-18 08:19 | 9374 | LFUS | 27642 | 3849547154 | 2015 | ENOI | 1 | 109 | VLFL | Tree On Line Outside R.O.W | N | A Phase blown limb on line HW | -90.1179 | 29.9579 | Vegetation | Line Fuse | Vegetation | 2020-05-18 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 5
2020 | 8 | 1330880818 | Yes | EAST ORLEANS | FAIR | 211 | 2020-05-18 09:00 | 2020-05-18 09:00 | 2020-05-18 12:31 | 1688 | TFUS | 1146111 | 40338489518 | 1702 | ENOI | 6 | 8 | SCHD | Scheduled Interruption | N | crew working on pole | -90.0591 | 30.0068 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-05-18 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 12 | 1330901890 | Yes | EAST ORLEANS | FAIR | 145 | 2020-05-18 13:39 | 2020-05-18 13:39 | 2020-05-18 16:04 | 1740 | TFUS | 1365684 | 40615480141 | 613 | ENOI | 6 | 12 | EARM | Equipment Failure - Crossarm | N | changed secondary arm | -90.0505 | 29.9811 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-18 | DLIN | D | Council District D | Jared Brossett | 70117 | 5
2020 | 5 | 1330911972 | Yes | EAST ORLEANS | FAIR | 275 | 2020-05-18 15:03 | 2020-05-18 17:14 | 2020-05-18 19:38 | 1375 | TFUS | 73565 | 42153493209 | 1604 | ENOI | 6 | 5 | ESEC | Secondary/Service Conductor | N | SERVICEMAN CALLED THE DOC AND REQUESTED TICKET FOR VEGETATION - GAVE EMPTY LOT ADDRESS | -90.0013 | 30.0164 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 31 | 1330924517 | Yes | ORLEANS | FAIR | 52 | 2020-05-18 20:24 | 2020-05-18 20:28 | 2020-05-18 21:16 | 1612 | LFUS | 28057 | 3935546596 | 1915 | ENOI | 1 | 31 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | BALLONS | -90.091 | 29.9424 | Other | Line Fuse | Other | 2020-05-18 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 1 | 1330948760 | Yes | ORLEANS | FAIR | 161 | 2020-05-19 10:19 | 2020-05-19 10:19 | 2020-05-19 13:01 | 161 | SERV | METER | 38629461970 | 1926 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | had to change out meter | -90.1139 | 29.9317 | Other | Service Conductor | Other | 2020-05-19 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 1 | 1331002598 | Yes | ORLEANS | FAIR | 97 | 2020-05-20 11:32 | 2020-05-20 11:32 | 2020-05-20 13:09 | 97 | SERV | METER | 38994475708 | 2011 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter off remotely call AMOC turned meter on | -90.102 | 29.9693 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-20 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 1 | 1331003965 | Yes | ORLEANS | FAIR | 60 | 2020-05-20 12:00 | 2020-05-20 12:00 | 2020-05-20 13:00 | 60 | TFUS | 1031021 | 4004048095 | 1712 | ENOI | 1 | 1 | AOTH | Animal - Other (Describe in Remarks Field) | N | transformer taken out by a bird refused ok per RBILES | -90.0687 | 29.9832 | Animal | Transformer Fuse | Animal | 2020-05-20 | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 1 | 1331008899 | Yes | ORLEANS | FAIR | 110 | 2020-05-20 13:49 | 2020-05-20 13:49 | 2020-05-20 15:39 | 110 | SERV | SERVICE | 39306476587 | 912 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.0921 | 29.9715 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-20 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 225 | 1331027686 | Yes | ORLEANS | FAIR | 88 | 2020-05-20 19:45 | 2020-05-20 21:15 | 2020-05-20 21:13 | 19800 | DIS | 23596 | 3953947389 | 907 | ENOI | 1 | 225 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Suspect balloons root cause along with phase slap afterwards: See breaker case | -90.0846 | 29.9641 | Other | Disconnect Switch | Other | 2020-05-20 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 536 | 1331028744 | Yes | ORLEANS | FAIR | 106 | 2020-05-20 19:45 | 2020-05-20 21:23 | 2020-05-20 21:31 | 56816 | DIS | 23879 | 3956947403 | 907 | ENOI | 1 | 536 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | suspect balloons root cause with phase slap afterwards: See breaker case | -90.0838 | 29.9646 | Other | Disconnect Switch | Other | 2020-05-20 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 1420 | 1331029587 | Yes | ORLEANS | FAIR | 125 | 2020-05-20 19:45 | 2020-05-20 21:56 | 2020-05-20 21:50 | 177500 | DIS | 23739 | 3970447578 | 907 | ENOI | 1 | 1420 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Suspect balloons was root cause with phase slap afterwards: See breaker case | -90.0794 | 29.9693 | Other | Disconnect Switch | Other | 2020-05-20 | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 186 | 1331025850 | Yes | ORLEANS | FAIR | 57 | 2020-05-20 19:45 | 2020-05-20 20:41 | 2020-05-20 20:43 | 10602 | SBKR | 907 | 3897447411 | 907 | ENOI | 1 | 186 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | opened 23596 and closed bkr in: Suspect balloons on N. Rochablave, Orleans to St. Peter | -90.1026 | 29.9649 | Other | Substation Breaker | Other | 2020-05-20 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 6 | 1331039050 | Yes | ORLEANS | FAIR | 193 | 2020-05-21 07:57 | 2020-05-21 07:57 | 2020-05-21 11:10 | 1158 | TFUS | 69592 | 39446475774 | 1513 | ENOI | 1 | 6 | AOTH | Animal - Other (Describe in Remarks Field) | N | trasnsformer out refused ok per RBILES transformer taken out by bird | -90.0876 | 29.9694 | Animal | Transformer Fuse | Animal | 2020-05-21 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 6 | 1331051743 | Yes | EAST ORLEANS | FAIR | 60 | 2020-05-21 12:54 | 2020-05-21 12:56 | 2020-05-21 13:54 | 360 | TFUS | 65670 | 42759494914 | 1604 | ENOI | 6 | 6 | ASQL | Animal - Squirrel | N | Transformer fuse blown at loc refused ok | -89.9824 | 30.021 | Animal | Transformer Fuse | Animal | 2020-05-21 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 706 | 1331064901 | Yes | EAST ORLEANS | FAIR | 65 | 2020-05-21 17:27 | 2020-05-21 18:23 | 2020-05-21 18:32 | 45890 | RCLR | 37681 | 4061148946 | 1702 | ENOI | 6 | 706 | EPRI | Equipment Failure - Primary Conductor | N | primary burned down possibly from overhanging limb | -90.0505 | 30.0066 | Equipment Failure | Recloser | Equipment Failure | 2020-05-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 30 | 1331066380 | Yes | EAST ORLEANS | FAIR | 120 | 2020-05-21 17:27 | 2020-05-21 17:37 | 2020-05-21 19:27 | 3720 | LFUS | 21612 | 4048848961 | 1702 | ENOI | 6 | 30 | EPRI | Equipment Failure - Primary Conductor | N | primary down | -90.0543 | 30.007 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 17 | 1331066690 | Yes | EAST ORLEANS | FAIR | 123 | 2020-05-21 17:27 | 2020-05-21 17:27 | 2020-05-21 19:30 | 2091 | TFUS | 68781 | 40477489476 | 1702 | ENOI | 6 | 17 | EPRI | Equipment Failure - Primary Conductor | N | primary down | -90.0546 | 30.0068 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 43 | 1331066593 | Yes | EAST ORLEANS | FAIR | 124 | 2020-05-21 17:27 | 2020-05-21 18:14 | 2020-05-21 19:31 | 5332 | LFUS | 21623 | 4049048938 | 1702 | ENOI | 6 | 43 | EPRI | Equipment Failure - Primary Conductor | N | primary down | -90.0543 | 30.0064 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 76 | 1331065683 | Yes | EAST ORLEANS | FAIR | 180 | 2020-05-21 17:50 | 2020-05-21 19:35 | 2020-05-21 20:50 | 13680 | LFUS | 21750 | 4237949491 | 1604 | ENOI | 6 | 76 | UNKN | Inspected Unknown | N | refused lateral; lights back on | -89.9943 | 30.021 | Other | Line Fuse | Other | 2020-05-21 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 27 | 1331092394 | Yes | EAST ORLEANS | FAIR | 233 | 2020-05-22 01:52 | 2020-05-22 01:58 | 2020-05-22 05:45 | 6291 | LFUS | 25735-F | 4282650283 | 2216 | ENOI | 6 | 27 | EPRI | Equipment Failure - Primary Conductor | N | FLDIncomplete Remarks: 2020-05-22-05:00 000027027- map 33 C phase hot to v42..arcoss crew brian.. | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-22 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 23 | 1331116716 | Yes | EAST ORLEANS | FAIR | 165 | 2020-05-22 06:51 | 2020-05-22 08:50 | 2020-05-22 09:36 | 3795 | TFUS | 80377 | 42895502009 | 2216 | ENOI | 6 | 23 | ESWC | Switching Cabinet | N | back on | -89.9775 | 30.0405 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-22 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 12 | 1331172961 | Yes | ORLEANS | FAIR | 283 | 2020-05-22 18:02 | 2020-05-22 18:34 | 2020-05-22 22:45 | 3396 | TFUS | 58903 | 39972475467 | 1712 | ENOI | 1 | 12 | FOTH | Fire - Other (Describe in Remarks Field) | N | 2 alarm fire | -90.0711 | 29.9684 | Other | Transformer Fuse | Other | 2020-05-22 | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 22 | 1331192284 | Yes | ORLEANS | FAIR | 25 | 2020-05-22 22:20 | 2020-05-22 22:24 | 2020-05-22 22:45 | 550 | TFUS | C72989 | 40049476465 | 1712 | ENOI | 1 | 22 | FOTH | Fire - Other (Describe in Remarks Field) | N | 2 alarm fire | -90.0686 | 29.9711 | Other | Transformer Fuse | Other | 2020-05-22 | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 10 | 1331194913 | Yes | ORLEANS | FAIR | 59 | 2020-05-22 23:21 | 2020-05-22 23:21 | 2020-05-23 00:20 | 590 | TFUS | 3004338 | 38349471193 | 2016 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1223 | 29.9571 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-05-22 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 38 | 1331247338 | Yes | ORLEANS | FAIR | 141 | 2020-05-23 15:05 | 2020-05-23 15:10 | 2020-05-23 17:26 | 5358 | LFUS | 21686 | 39696476310 | 907 | ENOI | 1 | 38 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | blown lateral C phase blown cause was balloons | -90.0796 | 29.9708 | Other | Line Fuse | Other | 2020-05-23 | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 83 | 1331259716 | Yes | ORLEANS | THDR | 174 | 2020-05-23 18:02 | 2020-05-23 20:26 | 2020-05-23 20:56 | 14442 | LFUS | 21366 | 4001347443 | 1512 | ENOI | 1 | 83 | EARM | Equipment Failure - Crossarm | N | broken x arm | -90.0698 | 29.9654 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-23 | DLIN | C | Council District C | Kristin Palmer | 70116 | 5
2020 | 1 | 1331259986 | Yes | ORLEANS | FAIR | 87 | 2020-05-23 18:14 | 2020-05-23 19:06 | 2020-05-23 19:41 | 87 | SERV | SERVICE | 38041465503 | B0527 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | hot leg burned off at transformer | -90.1324 | 29.9415 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 43 | 1331260411 | Yes | EAST ORLEANS | THDR | 253 | 2020-05-23 18:25 | 2020-05-23 21:39 | 2020-05-23 22:39 | 10879 | LFUS | 31644 | 4115547434 | 2347 | ENOI | 6 | 43 | LGHT | Lightning | N | refused ok | -90.0336 | 29.965 | Lightning | Line Fuse | Lightning | 2020-05-23 | DLIN | C | Council District C | Kristin Palmer | 70117 | 5
2020 | 5 | 1331267147 | Yes | ORLEANS | THDR | 126 | 2020-05-23 20:44 | 2020-05-23 20:45 | 2020-05-23 22:50 | 630 | XFMR | 78198 | 38798463576 | 1927 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | CHANGED TRANSFORMER | -90.1085 | 29.9359 | Equipment Failure | Transformer | Equipment Failure | 2020-05-23 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 10 | 1331268020 | Yes | EAST ORLEANS | THDR | 211 | 2020-05-23 21:02 | 2020-05-23 21:33 | 2020-05-24 00:33 | 2110 | XFMR | 53581 | 41458499139 | 1010 | ENOI | 6 | 10 | ETRD | Equipment Failure - Transformer | N | crew to change bad transformer | -90.0232 | 30.033 | Equipment Failure | Transformer | Equipment Failure | 2020-05-23 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 8 | 1331270112 | Yes | ORLEANS | THDR | 98 | 2020-05-23 21:53 | 2020-05-23 22:27 | 2020-05-23 23:31 | 784 | TFUS | 619393 | 3986048910 | 1704 | ENOI | 1 | 8 | LGHT | Lightning | N | transformer refused ok | -90.0742 | 30.0058 | Lightning | Transformer Fuse | Lightning | 2020-05-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 66 | 1331283420 | Yes | ORLEANS | FAIR | 152 | 2020-05-24 05:40 | 2020-05-24 07:17 | 2020-05-24 08:12 | 10032 | LFUS | 21463 | 3920545882 | 1923 | ENOI | 1 | 66 | VLGL | Tree/Limb Growing Inside R.O.W. | N | limb on line C phase blown refused ok | -90.0959 | 29.923 | Vegetation | Line Fuse | Vegetation | 2020-05-24 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 12 | 1331295825 | Yes | ORLEANS | FAIR | 67 | 2020-05-24 10:19 | 2020-05-24 10:24 | 2020-05-24 11:26 | 804 | TFUS | 694320 | 39218473125 | 2025 | ENOI | 1 | 12 | VLFL | Tree On Line Outside R.O.W | N | limb on top of transformer | -90.0948 | 29.9622 | Vegetation | Transformer Fuse | Vegetation | 2020-05-24 | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 3 | 1331380316 | Yes | EAST ORLEANS | FAIR | 118 | 2020-05-25 11:53 | 2020-05-25 11:53 | 2020-05-25 13:51 | 354 | TFUS | 1161472 | 5041254760 | 1204 | ENOI | 6 | 3 | VOHL | Overhanging Limb | N | removed, spliced out and back on | -89.7383 | 30.1633 | Vegetation | Transformer Fuse | Vegetation | 2020-05-25 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 5
2020 | 19 | 1331388519 | Yes | ORLEANS | RAIN | 230 | 2020-05-25 14:12 | 2020-05-25 14:19 | 2020-05-25 18:02 | 4370 | TFUS | 66611 | 40298485353 | 1708 | ENOI | 1 | 19 | EFSW | Equipment Failure - Fuse Switch | N | replaced bad switch at location | -90.0603 | 29.9954 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-25 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 23 | 1331406298 | Yes | EAST ORLEANS | RAIN | 150 | 2020-05-25 17:38 | 2020-05-25 19:40 | 2020-05-25 20:08 | 3450 | TFUS | 65808 | 40616476870 | 622 | ENOI | 6 | 23 | EFLK | Equipment Failure - Fuse Link | N | refused transformer | -90.0504 | 29.972 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-25 | DLIN | C | Council District C | Kristin Palmer | 70117 | 5
2020 | 229 | 1331460994 | Yes | ORLEANS | FAIR | 71 | 2020-05-26 07:19 | 2020-05-26 08:13 | 2020-05-26 08:30 | 16259 | LFUS | 38007 | 3980547500 | 907 | ENOI | 1 | 229 | UNKI | Unknown - Under Investigation | N | refused 2 phases out, customer back on | -90.0763 | 29.9673 | Other | Line Fuse | Other | 2020-05-26 | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 11 | 1331463282 | Yes | ORLEANS | FAIR | 103 | 2020-05-26 07:59 | 2020-05-26 08:31 | 2020-05-26 09:42 | 1133 | TFUS | 1000462 | 39789459299 | 2147 | ENOI | 1 | 11 | ASQL | Animal - Squirrel | N | taken out by squirrel refused ok | -90.0773 | 29.9239 | Animal | Transformer Fuse | Animal | 2020-05-26 | DLIN | B | Council District B | Jay Banks | 70130 | 5
2020 | 15 | 1331496483 | Yes | ORLEANS | THDR | 167 | 2020-05-26 11:34 | 2020-05-26 11:44 | 2020-05-26 14:21 | 2505 | TFUS | 29345 | 39798487477 | 1704 | ENOI | 1 | 15 | EARM | Equipment Failure - Crossarm | N | Changed broken feeder arm | -90.0759 | 30.0014 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-26 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 24 | 1331506621 | Yes | ORLEANS | FAIR | 68 | 2020-05-26 12:11 | 2020-05-26 12:55 | 2020-05-26 13:19 | 1632 | LFUS | 37925 | 3855847562 | 2012 | ENOI | 1 | 24 | LGHT | Lightning | N | bad weather in area | -90.1156 | 29.9693 | Lightning | Line Fuse | Lightning | 2020-05-26 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 461 | 1331523595 | Yes | ORLEANS | FAIR | 92 | 2020-05-26 12:39 | 2020-05-26 14:19 | 2020-05-26 14:11 | 42412 | RCLR | 24555 | 3978448919 | 1704 | ENOI | 1 | 461 | EARM | Equipment Failure - Crossarm | N | crossarm broke at perlita at mandolin | -90.0763 | 30.006 | Equipment Failure | Recloser | Equipment Failure | 2020-05-26 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 1761 | 1331547286 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 13:20 | 2020-05-26 14:15 | 2020-05-26 14:13 | 93333 | SUBN | 613 | 4081548420 | 613 | ENOI | 6 | 1761 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0441 | 29.9921 | Equipment Failure | Substation | Equipment Failure | 2020-05-26 | DSUB | D | Council District D | Jared Brossett | 70126 | 5
2020 | 2306 | 1331552667 | NO | ORLEANS | FAIR | 53 | 2020-05-26 13:20 | 2020-05-26 14:13 | 2020-05-26 14:13 | 122218 | SUBN | 614 | 4081448420 | 614 | ENOI | 1 | 2306 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0441 | 29.9921 | Equipment Failure | Substation | Equipment Failure | 2020-05-26 | DSUB | D | Council District D | Jared Brossett | 70126 | 5
2020 | 122 | 1331553195 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 13:20 | 2020-05-26 13:53 | 2020-05-26 14:13 | 6466 | SUBN | 612 | 4081648420 | 612 | ENOI | 6 | 122 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0441 | 29.9921 | Equipment Failure | Substation | Equipment Failure | 2020-05-26 | DSUB | D | Council District D | Jared Brossett | 70126 | 5
2020 | 729 | 1331554315 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 13:20 | 2020-05-26 14:13 | 2020-05-26 14:13 | 38637 | SUBN | 617 | 4081048420 | 617 | ENOI | 6 | 729 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0442 | 29.9921 | Equipment Failure | Substation | Equipment Failure | 2020-05-26 | DSUB | D | Council District D | Jared Brossett | 70126 | 5
2020 | 2101 | 1331559065 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 13:20 | 2020-05-26 14:13 | 2020-05-26 14:13 | 111353 | SUBN | 611 | 4081848420 | 611 | ENOI | 6 | 2101 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.044 | 29.9921 | Equipment Failure | Substation | Equipment Failure | 2020-05-26 | DSUB | D | Council District D | Jared Brossett | 70126 | 5
2020 | 150 | 1331561189 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 13:20 | 2020-05-26 14:02 | 2020-05-26 14:13 | 7950 | SUBN | 616 | 4081148420 | 616 | ENOI | 6 | 150 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0442 | 29.9921 | Equipment Failure | Substation | Equipment Failure | 2020-05-26 | DSUB | D | Council District D | Jared Brossett | 70126 | 5
2020 | 169 | 1331547225 | Yes | ORLEANS | THDR | 218 | 2020-05-26 13:22 | 2020-05-26 15:07 | 2020-05-26 17:00 | 36842 | LFUS | 21462 | 3916245912 | 1923 | ENOI | 1 | 169 | EFSW | Equipment Failure - Fuse Switch | N | crew changed switch | -90.0971 | 29.9237 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-26 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 50 | 1331565281 | Yes | EAST ORLEANS | THDR | 146 | 2020-05-26 13:27 | 2020-05-26 13:46 | 2020-05-26 15:53 | 7300 | LFUS | 68289 | 40680483837 | 1708 | ENOI | 6 | 50 | LGHT | Lightning | N | weather | -90.0482 | 29.9912 | Lightning | Line Fuse | Lightning | 2020-05-26 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 1 | 1331565781 | Yes | ORLEANS | FAIR | 97 | 2020-05-26 13:36 | 2020-05-26 13:36 | 2020-05-26 15:13 | 97 | SERV | SERVICE COND | 38665462793 | 1927 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.1127 | 29.9339 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-26 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 1125 | 1331616285 | Yes | ORLEANS | FAIR | 61 | 2020-05-26 14:44 | 2020-05-26 15:48 | 2020-05-26 15:45 | 68625 | RCLR | 25190 | 4015448032 | 627 | ENOI | 1 | 1125 | EARR | Equipment Failure - Arrestor | N | Failed arrestor on C phase at Maniville & Abundance | -90.0649 | 29.9816 | Equipment Failure | Recloser | Equipment Failure | 2020-05-26 | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 56 | 1331679281 | Yes | EAST ORLEANS | THDR | 42 | 2020-05-26 16:21 | 2020-05-26 16:56 | 2020-05-26 17:03 | 2352 | LFUS | 21009 | 4043448299 | 613 | ENOI | 6 | 56 | EARR | Equipment Failure - Arrestor | N | removed arrestor and refused lateral | -90.056 | 29.989 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-26 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 29 | 1331790819 | Yes | ORLEANS | FAIR | 81 | 2020-05-26 23:18 | 2020-05-26 23:18 | 2020-05-27 00:39 | 2349 | XFMR | 79237 | 38870462985 | 1554 | ENOI | 1 | 29 | ETRD | Equipment Failure - Transformer | N |  | -90.1063 | 29.9344 | Equipment Failure | Transformer | Equipment Failure | 2020-05-26 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 16 | 1331796991 | Yes | ORLEANS | FAIR | 80 | 2020-05-27 01:26 | 2020-05-27 01:26 | 2020-05-27 02:46 | 1280 | TFUS | 497054 | 38780464215 | 1926 | ENOI | 1 | 16 | EARM | Equipment Failure - Crossarm | N | crew changing x arm secondary | -90.1092 | 29.9376 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-05-27 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 19 | 1331835563 | Yes | EAST ORLEANS | FAIR | 153 | 2020-05-27 14:54 | 2020-05-27 16:08 | 2020-05-27 17:27 | 2907 | LFUS | 21216 | 4109648387 | 626 | ENOI | 6 | 19 | EOSC | Equipment Failure - Shield Conductor | N | repaired | -90.0352 | 29.991 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-27 | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 1 | 1331943395 | Yes | ORLEANS | FAIR | 244 | 2020-05-28 09:44 | 2020-05-28 09:44 | 2020-05-28 13:48 | 244 | XFMR | 68185 | 38827477293 | 2026 | ENOI | 1 | 1 | ETRD | Equipment Failure - Transformer | N | Changed out transformer everyone back in lights, mismatch customers | -90.107 | 29.9736 | Equipment Failure | Transformer | Equipment Failure | 2020-05-28 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 8 | 1331963304 | Yes | ORLEANS | FAIR | 144 | 2020-05-28 14:47 | 2020-05-28 15:08 | 2020-05-28 17:11 | 1152 | TFUS | 1342953 | 4020349326 | 503 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | crew changing out secondary arm | -90.0632 | 30.017 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-05-28 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 79 | 1331974211 | Yes | ORLEANS | FAIR | 366 | 2020-05-28 16:20 | 2020-05-28 16:41 | 2020-05-28 22:26 | 28914 | OPEN | 4013048427 | 4013048427 | 1708 | ENOI | 1 | 79 | VHCL | Vehicle | N | car hit pole at intersecton of allen & pleasure; broke pole and primary down PID in Progress KC - ALSO SEE #1331969611 (DGAULT) | -90.0657 | 29.9925 | Public Damage | Open | Public Damage | 2020-05-28 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 100 | 1331969611 | Yes | ORLEANS | FAIR | 39 | 2020-05-28 16:21 | 2020-05-28 17:14 | 2020-05-28 17:00 | 3900 | LFUS | 27677 | 4025648435 | 1708 | ENOI | 1 | 100 | VHCL | Vehicle | N | car broke pole and primary down KC - CHGD PID TO NO - RELATED TO #1331974211 (DGAULT) | -90.0618 | 29.9927 | Public Damage | Line Fuse | Public Damage | 2020-05-28 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 1 | 1331998631 | Yes | EAST ORLEANS | FAIR | 37 | 2020-05-29 09:57 | 2020-05-29 09:57 | 2020-05-29 10:35 | 37 | SERV | METER | 41960497608 | 2212 | ENOI | 6 | 1 | MTEX | Meter Exchange | N | Contractor in area changing meters cust was not informed meter was being changed Meter change was completed and power back on | -90.0075 | 30.0287 | Other | Service Conductor | Other | 2020-05-29 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 1 | 1332002483 | Yes | ORLEANS | FAIR | 41 | 2020-05-29 11:51 | 2020-05-29 11:51 | 2020-05-29 12:32 | 41 | SERV | METER | 39610464869 | 2132 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | amoc failed to turn on meter for us again | -90.0827 | 29.9393 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-29 | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 1 | 1332012128 | Yes | EAST ORLEANS | FAIR | 154 | 2020-05-29 17:27 | 2020-05-29 17:27 | 2020-05-29 20:01 | 154 | SERV | SERVICE | 42119501342 | 2212 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | burnt wire in hand hole repaired | -90.0023 | 30.0389 | Equipment Failure | Service Conductor | Equipment Failure | 2020-05-29 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 3 | 1332038205 | Yes | ORLEANS | FAIR | 11 | 2020-05-30 16:44 | 2020-05-30 16:46 | 2020-05-30 16:55 | 33 | TFUS | 59150 | 39069458193 | 1923 | ENOI | 1 | 3 | ASQL | Animal - Squirrel | N | refused | -90.1003 | 29.9211 | Animal | Transformer Fuse | Animal | 2020-05-30 | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 76 | 1332042762 | Yes | ORLEANS | FAIR | 145 | 2020-05-30 18:04 | 2020-05-30 20:01 | 2020-05-30 20:29 | 11020 | LFUS | 27749 | 3881148017 | 2011 | ENOI | 1 | 76 | EARR | Equipment Failure - Arrestor | N | Arrestor, replaced | -90.1073 | 29.9816 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-30 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 10 | 1332046475 | Yes | ORLEANS | FAIR | 433 | 2020-05-30 20:52 | 2020-05-30 23:06 | 2020-05-31 04:06 | 4330 | LFUS | 17669 | 3978949022 | 512 | ENOI | 1 | 10 | VLFL | Tree On Line Outside R.O.W | N | removed tree, picked up wire and replaced crossarms | -90.0762 | 30.009 | Vegetation | Line Fuse | Vegetation | 2020-05-30 | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 4 | 1332055787 | Yes | ORLEANS | FAIR | 157 | 2020-05-31 02:15 | 2020-05-31 02:15 | 2020-05-31 04:52 | 628 | XFMR | 1482256 | 38319483226 | 412 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.1228 | 29.9902 | Equipment Failure | Transformer | Equipment Failure | 2020-05-31 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 149 | 1332065414 | Yes | EAST ORLEANS | FAIR | 130 | 2020-05-31 09:06 | 2020-05-31 10:01 | 2020-05-31 11:16 | 19370 | LFUS | 26215 | 4280450443 | 2216 | ENOI | 6 | 149 | ETRD | Equipment Failure - Transformer | N | Crew to replace bad padmount | -89.9806 | 30.0469 | Equipment Failure | Line Fuse | Equipment Failure | 2020-05-31 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 20 | 1332069340 | Yes | EAST ORLEANS | FAIR | 228 | 2020-05-31 10:00 | 2020-05-31 10:00 | 2020-05-31 13:48 | 4560 | XFMR | 1372130 | 42791504916 | 2216 | ENOI | 6 | 20 | ETRD | Equipment Failure - Transformer | N |  | -89.981 | 30.0484 | Equipment Failure | Transformer | Equipment Failure | 2020-05-31 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 10 | 1332071241 | Yes | ORLEANS | FAIR | 386 | 2020-05-31 12:04 | 2020-05-31 16:19 | 2020-05-31 18:30 | 3860 | XFMR | 53669 | 38859487011 | 405 | ENOI | 1 | 10 | ETRD | Equipment Failure - Transformer | N | Crew on the way to replace bad transformer | -90.1058 | 30.0004 | Equipment Failure | Transformer | Equipment Failure | 2020-05-31 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 271 | 1332092492 | Yes | ORLEANS | FAIR | 200 | 2020-06-01 03:51 | 2020-06-01 06:31 | 2020-06-01 07:11 | 54200 | LFUS | 21522 | 3894446708 | 1925 | ENOI | 1 | 271 | VHCL | Vehicle | N | broke pole caused by truck picking up dumpters RELATED TO TKT#1332088960 (A.STEWART) | -90.1038 | 29.9457 | Public Damage | Line Fuse | Public Damage | 2020-06-01 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 205 | 1332109656 | Yes | ORLEANS | FAIR | 151 | 2020-06-01 12:35 | 2020-06-01 14:01 | 2020-06-01 15:06 | 30955 | LFUS | 97107 | 4016948726 | 1704 | ENOI | 1 | 205 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | lot of mylar ballons took out lateral, sub lateral and tfuse; cleared balloons and refused | -90.0642 | 30.0006 | Other | Line Fuse | Other | 2020-06-01 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 11 | 1332116630 | Yes | ORLEANS | FAIR | 50 | 2020-06-01 14:35 | 2020-06-01 14:35 | 2020-06-01 15:25 | 550 | TFUS | 56189 | 40199476023 | 614 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0639 | 29.9698 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-01 | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 9 | 1332121699 | Yes | EAST ORLEANS | FAIR | 104 | 2020-06-01 16:20 | 2020-06-01 16:20 | 2020-06-01 18:04 | 936 | TFUS | 57170 | 40502478854 | 613 | ENOI | 6 | 9 | ASQL | Animal - Squirrel | N | refused | -90.054 | 29.9775 | Animal | Transformer Fuse | Animal | 2020-06-01 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 2 | 1332140508 | Yes | EAST ORLEANS | FAIR | 427 | 2020-06-02 07:24 | 2020-06-02 07:24 | 2020-06-02 14:31 | 854 | XFMR | 1454647 | 41446499086 | 1010 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N | crew changed out pot | -90.0234 | 30.0329 | Equipment Failure | Transformer | Equipment Failure | 2020-06-02 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 56 | 1332142267 | Yes | ORLEANS | FAIR | 491 | 2020-06-02 08:05 | 2020-06-02 10:03 | 2020-06-02 16:16 | 27496 | LFUS | 21027 | 4017847648 | 614 | ENOI | 1 | 56 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0645 | 29.9709 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-02 | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 10 | 1332146024 | Yes | EAST ORLEANS | FAIR | 305 | 2020-06-02 08:55 | 2020-06-02 08:55 | 2020-06-02 14:00 | 3050 | TFUS | 74547 | 41026476240 | 611 | ENOI | 6 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0377 | 29.9702 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-02 | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 9 | 1332161825 | Yes | EAST ORLEANS | FAIR | 265 | 2020-06-02 11:32 | 2020-06-02 11:32 | 2020-06-02 15:57 | 2385 | TFUS | 1049544 | 41845474743 | 2347 | ENOI | 6 | 9 | VHCL | Vehicle | N | vehicle hit pole | -90.0119 | 29.9657 | Public Damage | Transformer Fuse | Public Damage | 2020-06-02 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 4 | 1332172550 | Yes | EAST ORLEANS | FAIR | 12 | 2020-06-02 15:19 | 2020-06-02 15:19 | 2020-06-02 15:31 | 48 | TFUS | 1522713 | 41850474478 | 2347 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0116 | 29.965 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-02 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 4 | 1332197352 | Yes | ORLEANS | FAIR | 415 | 2020-06-03 08:05 | 2020-06-03 08:05 | 2020-06-03 15:00 | 1660 | TFUS | 68857 | 39978489265 | 1704 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0704 | 30.0062 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-03 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 109 | 1332198679 | Yes | EAST ORLEANS | FAIR | 485 | 2020-06-03 08:30 | 2020-06-03 14:39 | 2020-06-03 16:35 | 52865 | LFUS | 21024 | 4046347924 | 613 | ENOI | 6 | 109 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0552 | 29.9787 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-03 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 5 | 1332204038 | Yes | EAST ORLEANS | FAIR | 64 | 2020-06-03 10:27 | 2020-06-03 10:27 | 2020-06-03 11:31 | 320 | TFUS | 1190793 | 41070491992 | 501 | ENOI | 6 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0358 | 30.0133 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-03 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 6 | 1332215038 | Yes | ORLEANS | FAIR | 96 | 2020-06-03 14:07 | 2020-06-03 14:07 | 2020-06-03 15:44 | 576 | TFUS | 69023 | 40146485975 | 1704 | ENOI | 1 | 6 | UNKN | Inspected Unknown | N | unknown what took out transforner, was tested ok, refused ok,. transformer does have animal guard. | -90.0651 | 29.9971 | Other | Transformer Fuse | Other | 2020-06-03 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 6 | 1332220636 | Yes | ORLEANS | FAIR | 81 | 2020-06-03 15:10 | 2020-06-03 15:10 | 2020-06-03 16:31 | 486 | TFUS | 59762 | 39967488805 | 1704 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0706 | 30.005 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-03 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 159 | 1332243281 | Yes | EAST ORLEANS | FAIR | 29 | 2020-06-03 18:41 | 2020-06-03 18:59 | 2020-06-03 19:10 | 4611 | LFUS | 27893 | 4082548786 | 625 | ENOI | 6 | 159 | SCHD | Scheduled Interruption | N | Crew working at location | -90.0435 | 30.0021 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-03 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 30 | 1332262706 | Yes | ORLEANS | FAIR | 95 | 2020-06-04 05:36 | 2020-06-04 06:07 | 2020-06-04 07:11 | 2850 | LFUS | 84239 | 3940545840 | 2147 | ENOI | 1 | 30 | UNKN | Inspected Unknown | N | refused ok | -90.0896 | 29.9216 | Other | Line Fuse | Other | 2020-06-04 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 69 | 1332264706 | Yes | ORLEANS | FAIR | 266 | 2020-06-04 06:04 | 2020-06-04 09:08 | 2020-06-04 10:30 | 18354 | LFUS | 21455 | 3935745789 | 1922 | ENOI | 1 | 69 | EARM | Equipment Failure - Crossarm | N | crew needs to replace single phase cross arm | -90.0909 | 29.9201 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-04 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 71 | 1332270155 | Yes | ORLEANS | FAIR | 103 | 2020-06-04 07:54 | 2020-06-04 08:38 | 2020-06-04 09:37 | 7313 | LFUS | 37635 | 3979848210 | 1705 | ENOI | 1 | 71 | ASQL | Animal - Squirrel | N |  | -90.0763 | 29.9865 | Animal | Line Fuse | Animal | 2020-06-04 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 1 | 1332281834 | Yes | EAST ORLEANS | FAIR | 173 | 2020-06-04 10:18 | 2020-06-04 10:18 | 2020-06-04 13:11 | 173 | SERV | SERVICE | 00000000000 | 611 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N | Replaced missing meter customer back in lights |  |  | Equipment Failure | Service Conductor | Equipment Failure | 2020-06-04 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 30 | 1332295679 | Yes | ORLEANS | FAIR | 126 | 2020-06-04 15:22 | 2020-06-04 15:55 | 2020-06-04 17:28 | 3780 | LFUS | 89174 | 3907846707 | 1922 | ENOI | 1 | 30 | VINE | Vine Growing into Line | N | Vines took out transformer & apparent flashover also took out lateral | -90.0995 | 29.9454 | Vegetation | Line Fuse | Vegetation | 2020-06-04 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 7 | 1332296675 | Yes | ORLEANS | FAIR | 93 | 2020-06-04 15:52 | 2020-06-04 15:52 | 2020-06-04 17:25 | 651 | TFUS | 1096588 | 39041467957 | 1553 | ENOI | 1 | 7 | VINE | Vine Growing into Line | N |  | -90.1006 | 29.948 | Vegetation | Transformer Fuse | Vegetation | 2020-06-04 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 2 | 1332305188 | Yes | EAST ORLEANS | FAIR | 32 | 2020-06-04 20:08 | 2020-06-04 20:08 | 2020-06-04 20:40 | 64 | DIS | 16212 | 4126949011 | 507 | ENOI | 6 | 2 | EABS | Equipment Failure - Air Break / Disconnect Switch | N | repaired | -90.0295 | 30.0081 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-06-04 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 3 | 1332323007 | Yes | EAST ORLEANS | FAIR | 58 | 2020-06-05 13:12 | 2020-06-05 13:12 | 2020-06-05 14:10 | 174 | TFUS | 58769 | 41143476587 | 611 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | contract crew on site | -90.0337 | 29.9711 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-05 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 7 | 1332453070 | Yes | ORLEANS | FAIR | 47 | 2020-06-06 07:48 | 2020-06-06 07:50 | 2020-06-06 08:35 | 329 | TFUS | 72330 | 38956483423 | 904 | ENOI | 1 | 7 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.1028 | 29.9906 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-06 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 278 | 1332457581 | Yes | EAST ORLEANS | FAIR | 250 | 2020-06-06 08:45 | 2020-06-06 09:51 | 2020-06-06 12:55 | 69500 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 278 | SCHD | Scheduled Interruption | N | #6 copper | -90.0335 | 29.9718 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-06 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 40 | 1332478850 | Yes | EAST ORLEANS | FAIR | 58 | 2020-06-06 13:28 | 2020-06-06 13:38 | 2020-06-06 14:26 | 2320 | LFUS | 17870 | 4036349293 | 506 | ENOI | 6 | 40 | ECNS | Equipment Failure - Connector Sleeve | N | bottom side jumper of switch burned out of switch on c phase | -90.0582 | 30.0161 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 23 | 1332494416 | Yes | EAST ORLEANS | FAIR | 187 | 2020-06-06 16:25 | 2020-06-06 17:17 | 2020-06-06 19:33 | 4301 | LFUS | 37022 | 4107847270 | 2347 | ENOI | 6 | 23 | EARM | Equipment Failure - Crossarm | N | crew repaired broke crossarm | -90.0359 | 29.9604 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-06 | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 39 | 1332512186 | Yes | EAST ORLEANS | FAIR | 323 | 2020-06-06 21:37 | 2020-06-07 01:34 | 2020-06-07 03:00 | 12597 | LFUS | 25646 | 4272849783 | 1602 | ENOI | 6 | 39 | UNKN | Inspected Unknown | N | lights back on | -97.0758 | 27.9066 | Other | Line Fuse | Other | 2020-06-06 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 4 | 1332513277 | Yes | ORLEANS | FAIR | 163 | 2020-06-06 22:18 | 2020-06-06 22:22 | 2020-06-07 01:01 | 652 | TFUS | 63605 | 39128467547 | 2021 | ENOI | 1 | 4 | ECNS | Equipment Failure - Connector Sleeve | N | Transformer riser came off. Replaced ok | -90.0978 | 29.9469 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-06 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 1 | 1332513575 | Yes | ORLEANS | FAIR | 324 | 2020-06-06 22:38 | 2020-06-06 22:38 | 2020-06-07 04:02 | 324 | SERV | SERVICE COND | 38582458445 | 1913 | ENOI | 1 | 1 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Trees rubbing on service burned phase Fixed ok | -90.1155 | 29.9221 | Vegetation | Service Conductor | Vegetation | 2020-06-06 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 89 | 1332519399 | Yes | EAST ORLEANS | RAIN | 289 | 2020-06-07 00:55 | 2020-06-07 04:44 | 2020-06-07 05:44 | 25721 | LFUS | 27327 | 4260850041 | 2216 | ENOI | 6 | 89 | EELB | Equipment Failure - Elbow | N | BAD ELBOW SALEM | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-07 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 46 | 1332520170 | Yes | ORLEANS | RAIN | 230 | 2020-06-07 01:34 | 2020-06-07 04:56 | 2020-06-07 05:24 | 10580 | LFUS | 27898 | 3992248185 | 1709 | ENOI | 1 | 46 | EARM | Equipment Failure - Crossarm | N | Bad crossarm at industry and republic crew replaced | -90.0725 | 29.986 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-07 | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 167 | 1332520121 | Yes | ORLEANS | FAIR | 138 | 2020-06-07 01:45 | 2020-06-07 01:55 | 2020-06-07 04:03 | 23046 | LFUS | 21369 | 3997847553 | 1712 | ENOI | 1 | 167 | VLFL | Tree On Line Outside R.O.W | N | Trees took out lateral switch refused ok | -90.0709 | 29.9686 | Vegetation | Line Fuse | Vegetation | 2020-06-07 | DLIN | D | Council District D | Jared Brossett | 70116 | 6
2020 | 62 | 1332522083 | Yes | ORLEANS | FAIR | 159 | 2020-06-07 03:47 | 2020-06-07 03:53 | 2020-06-07 06:26 | 9858 | LFUS | 21184 | 3802346703 | B0527 | ENOI | 1 | 62 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Tree on lateral trimmed tree | -90.1327 | 29.9458 | Vegetation | Line Fuse | Vegetation | 2020-06-07 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 135 | 1332522022 | Yes | EAST ORLEANS | THDR | 68 | 2020-06-07 03:48 | 2020-06-07 04:39 | 2020-06-07 04:56 | 9180 | LFUS | 21145 | 4065847641 | 622 | ENOI | 6 | 135 | VLFL | Tree On Line Outside R.O.W | N | Refused B and C phase at lateral sw.. Dead palm limbs fell into lateral | -90.0492 | 29.9709 | Vegetation | Line Fuse | Vegetation | 2020-06-07 | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 14 | 1332522095 | Yes | EAST ORLEANS | FAIR | 174 | 2020-06-07 03:53 | 2020-06-07 03:58 | 2020-06-07 06:47 | 2436 | LFUS | 21258 | 4189950117 | 2212 | ENOI | 6 | 14 | VLFL | Tree On Line Outside R.O.W | N | removed and refused | -90.0092 | 30.0385 | Vegetation | Line Fuse | Vegetation | 2020-06-07 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 12 | 1332522734 | Yes | ORLEANS | WIND | 60 | 2020-06-07 05:01 | 2020-06-07 05:01 | 2020-06-07 06:01 | 720 | TFUS | 33037 | 38934491554 | 413 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption had to take slack out of open wire secondary | -90.1033 | 30.0128 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-07 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 16 | 1332529957 | Yes | ORLEANS | FAIR | 55 | 2020-06-07 07:45 | 2020-06-07 07:45 | 2020-06-07 08:40 | 880 | TFUS | 1513065 | 39127478230 | 911 | ENOI | 1 | 16 | UNKN | Inspected Unknown | N |  | -90.0976 | 29.9762 | Other | Transformer Fuse | Other | 2020-06-07 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 135 | 1332538496 | Yes | EAST ORLEANS | THDR | 67 | 2020-06-07 10:08 | 2020-06-07 10:18 | 2020-06-07 11:15 | 9045 | LFUS | 21145 | 4065847641 | 622 | ENOI | 6 | 135 | VLFL | Tree On Line Outside R.O.W | N | palm tree needs to be trimmed STORM - WO VSTO 2064873454; M WO 4315859; | -90.0492 | 29.9709 | Vegetation | Line Fuse | Vegetation | 2020-06-07 | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 27 | 1332545286 | Yes | ORLEANS | THDR | 130 | 2020-06-07 10:27 | 2020-06-07 10:27 | 2020-06-07 12:37 | 3510 | DIS | 25810 | 3982647107 | 1543 | ENOI | 1 | 27 | UNKN | Inspected Unknown | N | Storm | -90.0759 | 29.9563 | Other | Disconnect Switch | Other | 2020-06-07 | DLIN | B | Council District B | Jay Banks | 70112 | 6
2020 | 4 | 1332541060 | Yes | ORLEANS | THDR | 49 | 2020-06-07 10:28 | 2020-06-07 10:33 | 2020-06-07 11:16 | 196 | SBKR | 1543 | 3950446996 | 1543 | ENOI | 1 | 4 | UNKN | Inspected Unknown | N | storm fault is on overhead behind switch 25810 | -90.086 | 29.9533 | Other | Substation Breaker | Other | 2020-06-07 | DLIN | B | Council District B | Jay Banks | 70113 | 6
2020 | 1 | 1332548001 | Yes | EAST ORLEANS | RAIN | 154 | 2020-06-07 11:44 | 2020-06-07 11:44 | 2020-06-07 14:18 | 154 | SERV | SERVICE | 43804496816 | 1601 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | BAD CONNECTION IN TRANSFORMER | -89.9494 | 30.0258 | Equipment Failure | Service Conductor | Equipment Failure | 2020-06-07 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 1 | 1332548786 | Yes | ORLEANS | THDR | 115 | 2020-06-07 12:00 | 2020-06-07 12:00 | 2020-06-07 13:55 | 115 | TFUS | 1355697 | 38590472530 | 2015 | ENOI | 1 | 1 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.1147 | 29.9607 | Vegetation | Transformer Fuse | Vegetation | 2020-06-07 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 62 | 1332554335 | Yes | ORLEANS | THDR | 159 | 2020-06-07 13:12 | 2020-06-07 13:24 | 2020-06-07 15:51 | 9858 | LFUS | 21370 | 4003647425 | 1512 | ENOI | 1 | 62 | VOHL | Overhanging Limb | N | B phase on lateral blown do to vegitation | -90.0691 | 29.9649 | Vegetation | Line Fuse | Vegetation | 2020-06-07 | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 11 | 1332554354 | Yes | ORLEANS | THDR | 171 | 2020-06-07 13:14 | 2020-06-07 13:14 | 2020-06-07 16:05 | 1881 | TFUS | 58719 | 39648477283 | 907 | ENOI | 1 | 11 | EFSW | Equipment Failure - Fuse Switch | N | Replaced riser on transformer switch | -90.0812 | 29.9733 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-07 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 12 | 1332556343 | Yes | ORLEANS | THDR | 146 | 2020-06-07 13:47 | 2020-06-07 13:47 | 2020-06-07 16:13 | 1752 | TFUS | 1046933 | 40201493395 | 503 | ENOI | 1 | 12 | CORR | Corrosion | N |  | -90.0632 | 30.0174 | Other | Transformer Fuse | Other | 2020-06-07 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 25 | 1332556627 | Yes | EAST ORLEANS | THDR | 72 | 2020-06-07 13:49 | 2020-06-07 14:23 | 2020-06-07 15:01 | 1800 | DIS | 25271 | 4255449627 | 1610 | ENOI | 6 | 25 | FTNU | Foreign Trouble - Neighboring Utility | N | WIRE LOW TOUCHING STREET LIGHT STANDARD: Open for safety to make repairs | -89.9888 | 30.0247 | Foreign Trouble | Disconnect Switch | Foreign Trouble | 2020-06-07 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 4 | 1332562157 | Yes | EAST ORLEANS | FAIR | 20 | 2020-06-07 16:00 | 2020-06-07 16:00 | 2020-06-07 16:20 | 80 | LFUS | 37126 | 4080148127 | 622 | ENOI | 6 | 4 | EMER | Emergency Switching | N |  | -90.0444 | 29.9843 | Other | Line Fuse | Emergency Switching | 2020-06-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 115 | 1332564727 | Yes | EAST ORLEANS | FAIR | 235 | 2020-06-07 17:01 | 2020-06-07 20:54 | 2020-06-07 20:56 | 27025 | RCLR | 37793 | 4946452184 | 1204 | ENOI | 6 | 115 | EPRI | Equipment Failure - Primary Conductor | N | found wire down; cleared and closed back in | -89.7692 | 30.0928 | Equipment Failure | Recloser | Equipment Failure | 2020-06-07 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 6
2020 | 2 | 1332581406 | Yes | EAST ORLEANS | RAIN | 2560 | 2020-06-07 17:13 | 2020-06-07 17:13 | 2020-06-09 11:53 | 5120 | TFUS | 1026789 | 5038654837 | 1204 | ENOI | 6 | 2 | EPRI | Equipment Failure - Primary Conductor | N | repaired | -89.7393 | 30.1647 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-07 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 6
2020 | 7 | 1332578227 | Yes | ORLEANS | FAIR | 133 | 2020-06-07 19:54 | 2020-06-07 20:05 | 2020-06-07 22:07 | 931 | XFMR | 613015 | 38896493950 | 402 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N | bad transformer crew replaced | -90.1043 | 30.0193 | Equipment Failure | Transformer | Equipment Failure | 2020-06-07 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 6 | 1332579461 | Yes | EAST ORLEANS | FAIR | 85 | 2020-06-07 20:16 | 2020-06-07 20:17 | 2020-06-07 21:41 | 510 | TFUS | 61392 | 42467503910 | 2215 | ENOI | 6 | 6 | UNKN | Inspected Unknown | N | Fuse blown went back in weather is fair | -89.9911 | 30.0459 | Other | Transformer Fuse | Other | 2020-06-07 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 13 | 1332580320 | Yes | ORLEANS | RAIN | 70 | 2020-06-07 20:45 | 2020-06-07 20:45 | 2020-06-07 21:55 | 910 | TFUS | 1417056 | 38757470419 | 2015 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1096 | 29.9548 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-07 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 1 | 1332641764 | Yes | EAST ORLEANS | RAIN | 125 | 2020-06-08 09:03 | 2020-06-08 09:03 | 2020-06-08 11:08 | 125 | TFUS | RXBS2559 | 41338496115 | 1002 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | repaired riser on switch customer back on | -90.027 | 30.0244 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-08 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 11 | 1332667181 | Yes | ORLEANS | RAIN | 86 | 2020-06-08 10:52 | 2020-06-08 11:00 | 2020-06-08 12:19 | 946 | TFUS | 517221 | 38337458934 | 1914 | ENOI | 1 | 11 | ESEC | Secondary/Service Conductor | N | refused | -90.1231 | 29.9233 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 102 | 1332687929 | Yes | ORLEANS | RAIN | 141 | 2020-06-08 13:07 | 2020-06-08 13:27 | 2020-06-08 15:28 | 14382 | DIS | 25385 | 3860746363 | 1926 | ENOI | 1 | 102 | VLGL | Tree/Limb Growing Inside R.O.W. | N | picked up down primary wireTREE CAUSED C PHASE TO BURN DOWN, TREE LIMB WAS REMOVED | -90.1144 | 29.9362 | Vegetation | Disconnect Switch | Vegetation | 2020-06-08 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 7 | 1332688125 | Yes | ORLEANS | FAIR | 130 | 2020-06-08 13:12 | 2020-06-08 13:12 | 2020-06-08 15:22 | 910 | TFUS | 61621 | 38708466353 | 1916 | ENOI | 1 | 7 | EARM | Equipment Failure - Crossarm | N | broken crossarms and downed secondary | -90.1112 | 29.9438 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-08 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 6
2020 | 7 | 1332739620 | Yes | ORLEANS | THDR | 68 | 2020-06-08 18:22 | 2020-06-08 18:22 | 2020-06-08 19:30 | 476 | TFUS | 62239 | 39435458191 | 2147 | ENOI | 1 | 7 | LGHT | Lightning | N | taken out by lightning in thunderstorm this evening refused ok | -90.0885 | 29.9209 | Lightning | Transformer Fuse | Lightning | 2020-06-08 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 91 | 1332778700 | Yes | EAST ORLEANS | FAIR | 177 | 2020-06-09 00:20 | 2020-06-09 00:20 | 2020-06-09 03:17 | 16107 | TFUS | 507029 | 41783501450 | 2212 | ENOI | 6 | 91 | EFLK | Equipment Failure - Fuse Link | N | refused lateral on pole and cubical a phase - lateral fuse not predictable, can't get customer ct | -90.0131 | 30.0393 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-09 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 23 | 1332784990 | Yes | ORLEANS | FAIR | 88 | 2020-06-09 03:07 | 2020-06-09 03:29 | 2020-06-09 04:36 | 2024 | LFUS | 36892 | 3844646852 | 2016 | ENOI | 1 | 23 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1194 | 29.9495 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 114 | 1332793735 | Yes | ORLEANS | FAIR | 181 | 2020-06-09 07:50 | 2020-06-09 10:03 | 2020-06-09 10:51 | 20634 | LFUS | 76997 | 39933478674 | 907 | ENOI | 1 | 114 | SCHD | Scheduled Interruption | N |  | -90.0722 | 29.9771 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-09 | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 4 | 1332807230 | Yes | EAST ORLEANS | FAIR | 65 | 2020-06-09 09:57 | 2020-06-09 09:57 | 2020-06-09 11:02 | 260 | TFUS | 69609 | 42039475082 | 2345 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N |  | -90.0055 | 29.9666 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-09 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 1 | 1332846802 | Yes | EAST ORLEANS | FAIR | 143 | 2020-06-09 17:41 | 2020-06-09 17:41 | 2020-06-09 20:05 | 143 | SERV | SERVICE COND | 42511502901 | 2215 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | changed connections at pole; good voltage | -89.9896 | 30.0431 | Equipment Failure | Service Conductor | Equipment Failure | 2020-06-09 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 7 | 1332848514 | Yes | ORLEANS | FAIR | 9 | 2020-06-09 18:31 | 2020-06-09 18:31 | 2020-06-09 18:40 | 63 | TFUS | 66220 | 39421460869 | 2147 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0889 | 29.9282 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-09 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 2 | 1332849300 | Yes | EAST ORLEANS | FAIR | 171 | 2020-06-09 18:55 | 2020-06-09 18:55 | 2020-06-09 21:46 | 342 | XFMR | 1125301 | 4355849783 | 1601 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N | crew changed out submersible transformer | -89.9569 | 30.0286 | Equipment Failure | Transformer | Equipment Failure | 2020-06-09 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 54 | 1332853836 | Yes | EAST ORLEANS | FAIR | 46 | 2020-06-09 20:45 | 2020-06-09 21:10 | 2020-06-09 21:31 | 2484 | LFUS | 27018 | 4356549765 | 1601 | ENOI | 6 | 54 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9566 | 30.0283 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-09 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 11 | 1332887487 | Yes | EAST ORLEANS | FAIR | 412 | 2020-06-10 08:34 | 2020-06-10 11:55 | 2020-06-10 15:26 | 4532 | XFMR | 31538 | 41660473151 | 2346 | ENOI | 6 | 11 | ETRD | Equipment Failure - Transformer | N | replaced | -90.0177 | 29.9615 | Equipment Failure | Transformer | Equipment Failure | 2020-06-10 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 1 | 1332889191 | Yes | EAST ORLEANS | BLNK | 133 | 2020-06-10 08:49 | 2020-06-10 08:49 | 2020-06-10 11:02 | 133 | TFUS | 1075630 | 4159047990 | 612 | ENOI | 6 | 1 | EPRI | Equipment Failure - Primary Conductor | N | see click | -90.0197 | 29.98 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 20 | 1332893096 | Yes | ORLEANS | FAIR | 339 | 2020-06-10 09:22 | 2020-06-10 09:24 | 2020-06-10 15:01 | 6780 | XFMR | 31174 | 38911478917 | 2011 | ENOI | 1 | 20 | LGHT | Lightning | N | CHANGED TRANSFORMER | -90.1045 | 29.9782 | Lightning | Transformer | Lightning | 2020-06-10 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 4 | 1332896314 | Yes | ORLEANS | FAIR | 43 | 2020-06-10 10:06 | 2020-06-10 10:06 | 2020-06-10 10:49 | 172 | TFUS | 62939 | 39314467651 | 2021 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | scheduled outage, customer was notified | -90.092 | 29.947 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-10 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 126 | 1332900914 | Yes | EAST ORLEANS | FAIR | 345 | 2020-06-10 11:30 | 2020-06-10 17:05 | 2020-06-10 17:15 | 43470 | LFUS | 17998 | 4158049987 | 2212 | ENOI | 6 | 126 | SCHD | Scheduled Interruption | N |  | -90.0195 | 30.0348 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 7 | 1332913133 | Yes | ORLEANS | FAIR | 276 | 2020-06-10 12:20 | 2020-06-10 12:20 | 2020-06-10 16:57 | 1932 | XFMR | 74477 | 39811487372 | 1704 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N | CHANGED OUT TRANSFORMER | -90.0756 | 30.001 | Equipment Failure | Transformer | Equipment Failure | 2020-06-10 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 1 | 1332906762 | Yes | EAST ORLEANS | FAIR | 255 | 2020-06-10 13:05 | 2020-06-10 15:06 | 2020-06-10 17:21 | 255 | XFMR | 1546002 | 43485495078 | 1612 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | replaced transformer | -89.9593 | 30.0211 | Equipment Failure | Transformer | Equipment Failure | 2020-06-10 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 35 | 1332910098 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-10 14:13 | 2020-06-10 14:15 | 2020-06-10 17:12 | 6265 | LFUS | 37102 | 4308850547 | 2215 | ENOI | 6 | 35 | EFLK | Equipment Failure - Fuse Link | N | refused | -89.9715 | 30.0497 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-10 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 9 | 1332922746 | Yes | EAST ORLEANS | FAIR | 259 | 2020-06-10 19:45 | 2020-06-10 20:37 | 2020-06-11 00:04 | 2331 | XFMR | 24516 | 41644492034 | 1001 | ENOI | 6 | 9 | ETRD | Equipment Failure - Transformer | N |  | -90.0174 | 30.0134 | Equipment Failure | Transformer | Equipment Failure | 2020-06-10 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 11 | 1332923841 | Yes | ORLEANS | FAIR | 320 | 2020-06-10 20:25 | 2020-06-10 23:23 | 2020-06-11 01:45 | 3520 | XFMR | 77959 | 40130487367 | 1704 | ENOI | 1 | 11 | ETRD | Equipment Failure - Transformer | N | Changed out bad transformer and increased the size do to overload | -90.0656 | 30.001 | Equipment Failure | Transformer | Equipment Failure | 2020-06-10 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 67 | 1332933772 | Yes | EAST ORLEANS | FAIR | 112 | 2020-06-11 06:42 | 2020-06-11 08:11 | 2020-06-11 08:34 | 7504 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 67 | ASQL | Animal - Squirrel | N | refused | -89.959 | 30.0234 | Animal | Line Fuse | Animal | 2020-06-11 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 8 | 1332936778 | Yes | ORLEANS | FAIR | 355 | 2020-06-11 08:43 | 2020-06-11 08:43 | 2020-06-11 14:38 | 2840 | DIS | 61181 | 3930846808 | 2021 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption Changing a Pole | -90.0922 | 29.9484 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-06-11 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 109 | 1332937241 | Yes | ORLEANS | FAIR | 338 | 2020-06-11 08:55 | 2020-06-11 11:19 | 2020-06-11 14:33 | 36842 | DIS | 48419 | 3928746821 | 1553 | ENOI | 1 | 109 | SCHD | Scheduled Interruption | N | DSR # 48784 Scheduled Interruption Changing a Pole | -90.0929 | 29.9487 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-06-11 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 1486 | 1332937358 | Yes | ORLEANS | FAIR | 48 | 2020-06-11 08:55 | 2020-06-11 09:43 | 2020-06-11 09:43 | 62412 | SBKR | 2015 | 3847647388 | 2015 | ENOI | 1 | 1486 | FTNU | Foreign Trouble - Neighboring Utility | N | att contractor set new pole into primary wires, dropped out for safety, woulod not close by scada, field switched RELATED TO AM 1332939453 | -90.1183 | 29.9644 | Foreign Trouble | Substation Breaker | Foreign Trouble | 2020-06-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 1833 | 1332939453 | Yes | ORLEANS | FAIR | 52 | 2020-06-11 08:55 | 2020-06-11 09:48 | 2020-06-11 09:47 | 100815 | DIS | 23726 | 3856047253 | 2015 | ENOI | 1 | 1833 | FTNU | Foreign Trouble - Neighboring Utility | N | att contractor set new pole into primary wires, dropped out for safety, woulod not close by scada, field switched DUPLICATE RELATED TO AMFM 1332937358 | -90.1156 | 29.9606 | Foreign Trouble | Disconnect Switch | Foreign Trouble | 2020-06-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 52 | 1332965516 | Yes | EAST ORLEANS | FAIR | 82 | 2020-06-11 18:18 | 2020-06-11 19:35 | 2020-06-11 19:40 | 4264 | LFUS | 21124 | 4118747946 | 621 | ENOI | 6 | 52 | ETRD | Equipment Failure - Transformer | N | bad transformer took lateral out 64977 | -90.0325 | 29.9789 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-11 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 8 | 1332967321 | Yes | EAST ORLEANS | FAIR | 235 | 2020-06-11 18:18 | 2020-06-11 20:27 | 2020-06-11 22:13 | 1880 | XFMR | 64977 | 41183479325 | 621 | ENOI | 6 | 8 | ETRD | Equipment Failure - Transformer | N |  | -90.0326 | 29.9786 | Equipment Failure | Transformer | Equipment Failure | 2020-06-11 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 1 | 1332984099 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-12 10:35 | 2020-06-12 10:35 | 2020-06-12 13:34 | 179 | TFUS | 1272291 | 41915477388 | 2347 | ENOI | 6 | 1 | ASQL | Animal - Squirrel | N | Refused C phase transformer taken out by squirrel | -90.0095 | 29.9729 | Animal | Transformer Fuse | Animal | 2020-06-12 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 45 | 1333004464 | Yes | EAST ORLEANS | FAIR | 140 | 2020-06-13 02:41 | 2020-06-13 03:25 | 2020-06-13 05:01 | 6300 | LFUS | 27991 | 4125647540 | 611 | ENOI | 6 | 45 | VHCL | Vehicle | N | car hit pole; isolated pole by opening sub-lateral cut-outs RELATED TO TKT# 1333005336 (A.STEWART) | -90.0303 | 29.9676 | Public Damage | Line Fuse | Public Damage | 2020-06-13 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 41 | 1333005336 | Yes | EAST ORLEANS | FAIR | 501 | 2020-06-13 02:41 | 2020-06-13 07:49 | 2020-06-13 11:03 | 20541 | LFUS | 37097 | 4127147536 | 611 | ENOI | 6 | 41 | VHCL | Vehicle | N | CAR HIT POLE REPLACE POLE AND TRANSFORMER; RELATED TO TKT# 1333004464 (A.STEWART) | -90.0297 | 29.9676 | Public Damage | Line Fuse | Public Damage | 2020-06-13 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 9 | 1333011431 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-13 08:40 | 2020-06-13 09:17 | 2020-06-13 11:40 | 1611 | LFUS | 57582 | 4198347797 | 2325 | ENOI | 6 | 9 | VINE | Vine Growing into Line | N | cleared vines refused ok | -90.0072 | 29.9745 | Vegetation | Line Fuse | Vegetation | 2020-06-13 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 1 | 1333015636 | Yes | ORLEANS | FAIR | 225 | 2020-06-13 10:59 | 2020-06-13 10:59 | 2020-06-13 14:44 | 225 | SERV | METER | 38554457177 | 1913 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | meter was opened up, disc. was worked and no install was completed | -90.1164 | 29.9184 | Equipment Failure | Service Conductor | Equipment Failure | 2020-06-13 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 40 | 1333023090 | Yes | ORLEANS | FAIR | 402 | 2020-06-13 14:18 | 2020-06-13 16:31 | 2020-06-13 21:01 | 16080 | LFUS | 21513 | 3904846397 | 1925 | ENOI | 1 | 40 | EARM | Equipment Failure - Crossarm | N | crew to change x arm | -90.1008 | 29.9371 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-13 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 1 | 1333027393 | Yes | ORLEANS | FAIR | 287 | 2020-06-13 17:14 | 2020-06-13 17:14 | 2020-06-13 22:01 | 287 | SERV | METER | 38306468034 | 2013 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | change out bad ami meter | -90.124 | 29.9485 | Equipment Failure | Service Conductor | Equipment Failure | 2020-06-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 31 | 1333057543 | Yes | EAST ORLEANS | FAIR | 93 | 2020-06-14 14:21 | 2020-06-14 14:59 | 2020-06-14 15:54 | 3818 | LFUS | 37015 | 4208449910 | 2212 | ENOI | 6 | 31 | ETRD | Equipment Failure - Transformer | N | crew to change | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-14 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 6 | 1333061327 | Yes | ORLEANS | FAIR | 536 | 2020-06-14 17:02 | 2020-06-14 21:10 | 2020-06-15 01:58 | 3216 | XFMR | 51114 | 38586484379 | 407 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | replaced broken primary arms and replaced bad transformer | -90.1145 | 29.9932 | Equipment Failure | Transformer | Equipment Failure | 2020-06-14 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 1 | 1333063372 | Yes | ORLEANS | FAIR | 128 | 2020-06-14 18:09 | 2020-06-14 18:09 | 2020-06-14 20:17 | 128 | SERV | METER | 38315467599 | 2013 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | AMI meter opened internaly amock won t answer changed out meter | -90.1237 | 29.9473 | Other | Service Conductor | Other | 2020-06-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 8 | 1333072397 | Yes | EAST ORLEANS | FAIR | 282 | 2020-06-15 01:19 | 2020-06-15 01:48 | 2020-06-15 06:01 | 2256 | XFMR | 64157 | 41009476922 | 611 | ENOI | 6 | 8 | ETRD | Equipment Failure - Transformer | N | replaced transformer | -90.0379 | 29.9721 | Equipment Failure | Transformer | Equipment Failure | 2020-06-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 13 | 1333073807 | Yes | ORLEANS | FAIR | 104 | 2020-06-15 04:01 | 2020-06-15 04:41 | 2020-06-15 05:45 | 6968 | LFUS | 21921 | 3861648402 | 407 | ENOI | 1 | 13 | EARR | Equipment Failure - Arrestor | N |  | -90.1136 | 29.9922 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-15 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 132 | 1333078694 | Yes | EAST ORLEANS | FAIR | 30 | 2020-06-15 06:49 | 2020-06-15 07:19 | 2020-06-15 07:19 | 3960 | LFUS | 81486 | 4250450410 | 2215 | ENOI | 6 | 132 | ASQL | Animal - Squirrel | N |  | -89.9899 | 30.0464 | Animal | Line Fuse | Animal | 2020-06-15 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 19 | 1333097236 | Yes | EAST ORLEANS | FAIR | 54 | 2020-06-15 13:50 | 2020-06-15 13:53 | 2020-06-15 14:44 | 1026 | LFUS | 21262 | 4224350265 | 2212 | ENOI | 6 | 19 | VHCL | Vehicle | N | car hit pole it took lateral out on gus refused and customers are back in lights | -89.9982 | 30.0424 | Public Damage | Line Fuse | Public Damage | 2020-06-15 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 6 | 1333098000 | Yes | EAST ORLEANS | FAIR | 95 | 2020-06-15 14:13 | 2020-06-15 14:13 | 2020-06-15 15:48 | 570 | TFUS | 66883 | 40820476016 | 614 | ENOI | 6 | 6 | VHCL | Vehicle | N | dumpped truck hit service line ripped it down and broke open wire secondary burned insulation fell on customer vehicle and burned his paint off but i picked up open wire and and cut down service that was hit | -90.0441 | 29.9697 | Public Damage | Transformer Fuse | Public Damage | 2020-06-15 | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 9 | 1333115830 | Yes | ORLEANS | FAIR | 345 | 2020-06-16 05:18 | 2020-06-16 05:18 | 2020-06-16 11:03 | 3105 | TFUS | 3001548 | 38950457703 | 1921 | ENOI | 1 | 9 | ECON | Equipment Failure - Connector / Sleeve | N | changed conections at pole | -90.1037 | 29.9198 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-16 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 7 | 1333119827 | Yes | EAST ORLEANS | FAIR | 94 | 2020-06-16 08:04 | 2020-06-16 08:04 | 2020-06-16 09:38 | 658 | TFUS | 566788 | 40676494014 | 506 | ENOI | 6 | 7 | ASQL | Animal - Squirrel | N | Refused transformer taken out by squirrel | -90.0482 | 30.019 | Animal | Transformer Fuse | Animal | 2020-06-16 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 69 | 1333120481 | Yes | ORLEANS | FAIR | 162 | 2020-06-16 08:09 | 2020-06-16 09:49 | 2020-06-16 10:51 | 11178 | LFUS | 21484 | 3923146070 | 1924 | ENOI | 1 | 69 | EFSW | Equipment Failure - Fuse Switch | N | Replaced bad switch | -90.095 | 29.928 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-16 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 42 | 1333125808 | Yes | EAST ORLEANS | FAIR | 24 | 2020-06-16 10:01 | 2020-06-16 10:09 | 2020-06-16 10:25 | 1008 | LFUS | 16057-F | 4167149321 | 1001 | ENOI | 6 | 42 | SCHD | Scheduled Interruption | N |  | -90.0168 | 30.0167 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-16 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 124 | 1333125835 | Yes | EAST ORLEANS | FAIR | 130 | 2020-06-16 10:03 | 2020-06-16 10:16 | 2020-06-16 12:13 | 16120 | LFUS | 17971 | 4163749296 | 1001 | ENOI | 6 | 124 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | Contractor in the past put switch riser on C phase instead of B Phase like its engineered for. It has since been corrected | -90.0176 | 30.016 | Public Damage | Line Fuse | Public Damage | 2020-06-16 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 10 | 1333125945 | Yes | ORLEANS | FAIR | 432 | 2020-06-16 10:07 | 2020-06-16 16:33 | 2020-06-16 17:20 | 4320 | TFUS | 77859 | 39302461416 | 1924 | ENOI | 1 | 10 | EFLK | Equipment Failure - Fuse Link | N | found bad fuse barrel stuck in fiberglass split replaced fuse barrel refused ok | -90.0927 | 29.93 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-16 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 11 | 1333126912 | Yes | EAST ORLEANS | FAIR | 111 | 2020-06-16 10:20 | 2020-06-16 10:20 | 2020-06-16 12:11 | 1221 | LFUS | 25844 | 4162647810 | 2325 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Crew On Site Working | -90.0187 | 29.975 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-16 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 244 | 1333153301 | Yes | EAST ORLEANS | FAIR | 41 | 2020-06-16 18:17 | 2020-06-16 19:01 | 2020-06-16 18:59 | 10004 | RCLR | 92431 | 4143549262 | 1010 | ENOI | 6 | 244 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Baloons | -90.0241 | 30.015 | Other | Recloser | Other | 2020-06-16 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 6 | 1333164128 | Yes | ORLEANS | FAIR | 109 | 2020-06-17 07:26 | 2020-06-17 07:26 | 2020-06-17 09:15 | 654 | TFUS | 57973 | 39667488116 | 1704 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0803 | 30.0031 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-17 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 11 | 1333165798 | Yes | EAST ORLEANS | FAIR | 190 | 2020-06-17 08:00 | 2020-06-17 08:00 | 2020-06-17 11:10 | 2090 | TFUS | 58868 | 41114475406 | 611 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0347 | 29.9678 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 10 | 1333166355 | Yes | ORLEANS | FAIR | 72 | 2020-06-17 08:24 | 2020-06-17 08:24 | 2020-06-17 09:36 | 720 | TFUS | 56513 | 39737489643 | 1704 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.078 | 30.0072 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-17 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 1 | 1333166463 | Yes | ORLEANS | FAIR | 146 | 2020-06-17 08:25 | 2020-06-17 08:25 | 2020-06-17 10:51 | 146 | TFUS | 1305459 | 38300465286 | 2014 | ENOI | 1 | 1 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1241 | 29.9408 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-17 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 6 | 1333168986 | Yes | EAST ORLEANS | FAIR | 58 | 2020-06-17 08:47 | 2020-06-17 08:47 | 2020-06-17 09:45 | 348 | LFUS | 89813 | 4164747805 | 2325 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0182 | 29.9749 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-17 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 24 | 1333169664 | Yes | ORLEANS | FAIR | 323 | 2020-06-17 09:00 | 2020-06-17 09:51 | 2020-06-17 14:23 | 7752 | OPEN | 3942546875 | 3942546875 | 1554 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | Scheduled Interruption Change Pole | -90.0885 | 29.95 | Scheduled Interruption | Open | Scheduled Interruption | 2020-06-17 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 36 | 1333174135 | Yes | EAST ORLEANS | FAIR | 20 | 2020-06-17 10:29 | 2020-06-17 10:35 | 2020-06-17 10:49 | 720 | LFUS | 37015 | 4208449910 | 2212 | ENOI | 6 | 36 | HECD | Company - Distribution Business (Describe in remar | N | Underground crew was switching the loop back to normal when the fuse blew Cable was tested and was good prior to switching Crew refused lateral Customers back in lights | -97.0758 | 27.9066 | Human Error | Line Fuse | Human Error | 2020-06-17 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 1 | 1333180768 | Yes | EAST ORLEANS | FAIR | 92 | 2020-06-17 12:56 | 2020-06-17 12:56 | 2020-06-17 14:28 | 92 | TFUS | 1413542 | 41136476300 | 611 | ENOI | 6 | 1 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.034 | 29.9703 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 7 | 1333180876 | Yes | EAST ORLEANS | FAIR | 92 | 2020-06-17 12:56 | 2020-06-17 12:56 | 2020-06-17 14:28 | 644 | TFUS | 71019 | 41133476214 | 611 | ENOI | 6 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0341 | 29.97 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 8 | 1333184155 | Yes | EAST ORLEANS | FAIR | 47 | 2020-06-17 14:37 | 2020-06-17 15:00 | 2020-06-17 15:24 | 376 | TFUS | 70051 | 4082247647 | 622 | ENOI | 6 | 8 | UNKN | Inspected Unknown | N | Refused transformer Inspected unknown | -90.044 | 29.9708 | Other | Transformer Fuse | Other | 2020-06-17 | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 31 | 1333203281 | Yes | EAST ORLEANS | FAIR | 281 | 2020-06-17 20:15 | 2020-06-17 20:46 | 2020-06-18 00:56 | 8711 | LFUS | 25724 | 4319150521 | 2214 | ENOI | 6 | 31 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-17 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 4 | 1333205602 | Yes | EAST ORLEANS | FAIR | 214 | 2020-06-17 22:43 | 2020-06-17 22:44 | 2020-06-18 02:17 | 856 | XFMR | 1003345 | 42188497835 | 2212 | ENOI | 6 | 4 | ETRD | Equipment Failure - Transformer | N | CHANGED TRANSFORMER | -90.0003 | 30.0292 | Equipment Failure | Transformer | Equipment Failure | 2020-06-17 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 237 | 1333212662 | Yes | EAST ORLEANS | FAIR | 415 | 2020-06-18 08:05 | 2020-06-18 15:07 | 2020-06-18 15:01 | 98355 | LFUS | 17998 | 4158049987 | 2212 | ENOI | 6 | 237 | SCHD | Scheduled Interruption | N | contract crew | -90.0195 | 30.0348 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 6 | 1333237263 | Yes | EAST ORLEANS | FAIR | 148 | 2020-06-18 19:53 | 2020-06-18 20:05 | 2020-06-18 22:21 | 888 | XFMR | 19087 | 41572499268 | 2212 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N |  | -90.0196 | 30.0332 | Equipment Failure | Transformer | Equipment Failure | 2020-06-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 1 | 1333250548 | Yes | ORLEANS | FAIR | 56 | 2020-06-19 08:48 | 2020-06-19 08:48 | 2020-06-19 09:44 | 56 | SERV | SERVICE | 39308462481 | 1554 | ENOI | 1 | 1 | HECO | Human Error - Company (Describe in Remarks Field) | N | AMOC turned off wrong meter | -90.0923 | 29.933 | Human Error | Service Conductor | Human Error | 2020-06-19 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 11 | 1333262323 | Yes | ORLEANS | FAIR | 193 | 2020-06-19 14:45 | 2020-06-19 14:45 | 2020-06-19 17:58 | 2123 | TFUS | 1254921 | 39399464952 | 1915 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons took lateral out cleared refused ok - lfus not in gis | -90.0896 | 29.9397 | Other | Transformer Fuse | Other | 2020-06-19 | DLIN | B | Council District B | Jay Banks | 70113 | 6
2020 | 7 | 1333304996 | Yes | ORLEANS | FAIR | 45 | 2020-06-20 10:37 | 2020-06-20 10:37 | 2020-06-20 11:22 | 315 | TFUS | 71373 | 40138487847 | 1704 | ENOI | 1 | 7 | ECNS | Equipment Failure - Connector Sleeve | N | trans riser off | -90.0654 | 30.0023 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 117 | 1333309416 | Yes | EAST ORLEANS | FAIR | 182 | 2020-06-20 13:04 | 2020-06-20 15:25 | 2020-06-20 16:06 | 21294 | LFUS | 38367 | 4079449113 | 501 | ENOI | 6 | 117 | ASQL | Animal - Squirrel | N | w | -90.0445 | 30.011 | Animal | Line Fuse | Animal | 2020-06-20 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 23 | 1333325959 | Yes | ORLEANS | FAIR | 102 | 2020-06-20 18:54 | 2020-06-20 19:52 | 2020-06-20 20:36 | 2346 | LFUS | 27715 | 3916545880 | 1923 | ENOI | 1 | 23 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons took out B phase lateral | -90.097 | 29.9228 | Other | Line Fuse | Other | 2020-06-20 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 4 | 1333384123 | Yes | EAST ORLEANS | FAIR | 36 | 2020-06-21 20:24 | 2020-06-21 20:29 | 2020-06-21 21:01 | 144 | TFUS | 559321 | 42629493295 | 1604 | ENOI | 6 | 4 | ASQL | Animal - Squirrel | N | refused ok | -89.9863 | 30.0166 | Animal | Transformer Fuse | Animal | 2020-06-21 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 13 | 1333404102 | Yes | EAST ORLEANS | THDR | 334 | 2020-06-22 02:31 | 2020-06-22 07:09 | 2020-06-22 08:05 | 4342 | LFUS | 25370 | 4385351220 | 2217 | ENOI | 6 | 13 | EPRI | Equipment Failure - Primary Conductor | N | bad underground cable V-13 to V-14 | -89.9472 | 30.0681 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-22 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 370 | 1333407075 | Yes | EAST ORLEANS | THDR | 239 | 2020-06-22 03:55 | 2020-06-22 07:49 | 2020-06-22 07:54 | 88430 | LFUS | 27045 | 4279549796 | 2211 | ENOI | 6 | 370 | AOTH | Animal - Other (Describe in Remarks Field) | N | VFI 248 opened tripped closed okay Found rat nest & switch flashed over in cub # 8 R.S. I-10 up of Plaza Dr. | -97.0758 | 27.9066 | Animal | Line Fuse | Animal | 2020-06-22 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 57 | 1333431194 | Yes | ORLEANS | THDR | 136 | 2020-06-22 08:40 | 2020-06-22 10:21 | 2020-06-22 10:56 | 7752 | LFUS | 33223 | 3874248657 | 408 | ENOI | 1 | 57 | VINE | Vine Growing into Line | N |  | -90.1094 | 29.9993 | Vegetation | Line Fuse | Vegetation | 2020-06-22 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 246 | 1333431435 | Yes | ORLEANS | THDR | 302 | 2020-06-22 08:42 | 2020-06-22 12:47 | 2020-06-22 13:44 | 74292 | LFUS | 37780 | 3990648264 | 1709 | ENOI | 1 | 246 | EARM | Equipment Failure - Crossarm | N |  | -90.0728 | 29.9879 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-22 | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 1959 | 1333439250 | Yes | ORLEANS | THDR | 7 | 2020-06-22 09:35 | 2020-06-22 09:41 | 2020-06-22 09:41 | 13713 | SBKR | 2027 | 3848547391 | 2027 | ENOI | 1 | 1959 | EMER | Emergency Switching | N | had to emergency switch due to crossarm braces breaking and phase laying on arm due to squirrel at Burdette & Collipissa | -90.1127 | 29.959 | Other | Substation Breaker | Emergency Switching | 2020-06-22 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 12 | 1333445809 | Yes | ORLEANS | THDR | 61 | 2020-06-22 10:17 | 2020-06-22 10:17 | 2020-06-22 11:18 | 732 | TFUS | 58355 | 39713473480 | 1512 | ENOI | 1 | 12 | EARR | Equipment Failure - Arrestor | N | arrestor gave way cleared refused okay per ryan price | -90.0793 | 29.9629 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-22 | DLIN | B | Council District B | Jay Banks | 70112 | 6
2020 | 85 | 1333481087 | Yes | ORLEANS | FAIR | 170 | 2020-06-22 13:53 | 2020-06-22 16:06 | 2020-06-22 16:43 | 14450 | LFUS | 27623 | 3826946524 | 2014 | ENOI | 1 | 85 | EARM | Equipment Failure - Crossarm | N | Bad crossarm at St Charles and pine crew replaced | -90.1252 | 29.9408 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-22 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 4 | 1333522572 | Yes | EAST ORLEANS | FAIR | 248 | 2020-06-23 07:08 | 2020-06-23 07:08 | 2020-06-23 11:16 | 992 | XFMR | 23303 | 41680496592 | 1001 | ENOI | 6 | 4 | ETRD | Equipment Failure - Transformer | N |  | -90.0162 | 30.0259 | Equipment Failure | Transformer | Equipment Failure | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 2 | 1333522911 | Yes | ORLEANS | FAIR | 120 | 2020-06-23 07:31 | 2020-06-23 09:09 | 2020-06-23 09:31 | 240 | TFUS | 69114 | 38585476539 | 2026 | ENOI | 1 | 2 | ASQL | Animal - Squirrel | N | squirrel on tf blown fuse refused ok | -90.1146 | 29.9717 | Animal | Transformer Fuse | Animal | 2020-06-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 22 | 1333523047 | Yes | ORLEANS | FAIR | 358 | 2020-06-23 07:35 | 2020-06-23 12:11 | 2020-06-23 13:34 | 7876 | TFUS | 1351409 | 3972447529 | 907 | ENOI | 1 | 22 | SCHD | Scheduled Interruption | N | crew on site to repair riser on pole | -90.0789 | 29.968 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 3 | 1333532614 | Yes | EAST ORLEANS | FAIR | 373 | 2020-06-23 07:43 | 2020-06-23 10:02 | 2020-06-23 13:56 | 1119 | TFUS | 3009794 | 49677530926 | 1204 | ENOI | 6 | 3 | TSCF | Transformer Splicing chamber failure | N |  | -89.7622 | 30.1176 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-23 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 6
2020 | 1 | 1333560528 | Yes | EAST ORLEANS | FAIR | 82 | 2020-06-23 14:13 | 2020-06-23 14:19 | 2020-06-23 15:35 | 82 | SERV | SERVICE | 40306494902 | 506 | ENOI | 6 | 1 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | unknown vehicle hit service while cleaning out empty lot next to location ripped down service and damaged meter pan stem pipe HOLD FOR PERMIT | -90.0597 | 30.0216 | Public Damage | Service Conductor | Public Damage | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 35 | 1333571139 | Yes | EAST ORLEANS | RAIN | 89 | 2020-06-23 15:57 | 2020-06-23 16:43 | 2020-06-23 17:26 | 3115 | LFUS | 21259 | 4249750190 | 2216 | ENOI | 6 | 35 | LGHT | Lightning | N | refused lat | -89.9903 | 30.04 | Lightning | Line Fuse | Lightning | 2020-06-23 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 65 | 1333585727 | Yes | ORLEANS | THDR | 119 | 2020-06-23 16:07 | 2020-06-23 17:03 | 2020-06-23 18:06 | 7735 | LFUS | 27792 | 3925145879 | 1923 | ENOI | 1 | 65 | LGHT | Lightning | N |  | -90.0945 | 29.9228 | Lightning | Line Fuse | Lightning | 2020-06-23 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 1 | 1333572692 | Yes | EAST ORLEANS | THDR | 147 | 2020-06-23 16:10 | 2020-06-23 16:10 | 2020-06-23 18:37 | 147 | SERV | METER | 41600492214 | 1010 | ENOI | 6 | 1 | MTEX | Meter Exchange | N | changed meter | -90.019 | 30.0139 | Other | Service Conductor | Other | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 12 | 1333573668 | Yes | ORLEANS | FAIR | 91 | 2020-06-23 16:23 | 2020-06-23 17:16 | 2020-06-23 17:54 | 1092 | TFUS | 3010046 | 39332457070 | 1922 | ENOI | 1 | 12 | LGHT | Lightning | N |  | -90.0919 | 29.9179 | Lightning | Transformer Fuse | Lightning | 2020-06-23 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 69 | 1333585739 | Yes | ORLEANS | THDR | 77 | 2020-06-23 17:07 | 2020-06-23 18:12 | 2020-06-23 18:24 | 5313 | LFUS | 21465 | 3928745922 | 1923 | ENOI | 1 | 69 | LGHT | Lightning | N | refused | -90.0933 | 29.9237 | Lightning | Line Fuse | Lightning | 2020-06-23 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 48 | 1333583790 | Yes | ORLEANS | THDR | 162 | 2020-06-23 17:14 | 2020-06-23 18:33 | 2020-06-23 19:56 | 7776 | LFUS | 28068 | 3960648669 | 1703 | ENOI | 1 | 48 | LGHT | Lightning | N | refused | -90.0821 | 29.9993 | Lightning | Line Fuse | Lightning | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 413 | 1333584625 | Yes | ORLEANS | THDR | 105 | 2020-06-23 17:16 | 2020-06-23 18:57 | 2020-06-23 19:01 | 43365 | LFUS | 27700 | 4030447510 | 614 | ENOI | 1 | 413 | LGHT | Lightning | N | refused | -90.0603 | 29.9673 | Lightning | Line Fuse | Lightning | 2020-06-23 | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 111 | 1333588099 | Yes | ORLEANS | THDR | 270 | 2020-06-23 17:31 | 2020-06-23 21:17 | 2020-06-23 22:01 | 29970 | LFUS | 17745 | 3856249404 | 409 | ENOI | 1 | 111 | ECNS | Equipment Failure - Connector Sleeve | N | primary jumper broke, repaired and customer back in | -90.1147 | 30.0198 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-23 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 8 | 1333587360 | Yes | ORLEANS | THDR | 434 | 2020-06-23 17:31 | 2020-06-23 20:44 | 2020-06-24 00:46 | 3472 | TFUS | 71038 | 40203480659 | 627 | ENOI | 1 | 8 | EARM | Equipment Failure - Crossarm | N | replaced rotten Wilson rack, spaced out vertical open wire secondary to prevent hot legs from touching | -90.0635 | 29.9824 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 72 | 1333587831 | Yes | EAST ORLEANS | FAIR | 241 | 2020-06-23 17:37 | 2020-06-23 20:21 | 2020-06-23 21:38 | 17352 | LFUS | 77900 | 4157249422 | 1010 | ENOI | 6 | 72 | ECNS | Equipment Failure - Connector Sleeve | N | repaired jumper conn | -90.02 | 30.0194 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 45 | 1333588583 | Yes | ORLEANS | THDR | 112 | 2020-06-23 17:45 | 2020-06-23 18:05 | 2020-06-23 19:37 | 5040 | LFUS | 36644 | 4028748693 | 1708 | ENOI | 1 | 45 | LGHT | Lightning | N | refused | -90.0607 | 29.9999 | Lightning | Line Fuse | Lightning | 2020-06-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 33 | 1333591046 | Yes | ORLEANS | THDR | 334 | 2020-06-23 18:07 | 2020-06-23 18:15 | 2020-06-23 23:41 | 11022 | TFUS | 67342 | 39388478514 | 912 | ENOI | 1 | 33 | LGHT | Lightning | N | refused | -90.0895 | 29.977 | Lightning | Transformer Fuse | Lightning | 2020-06-23 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 5 | 1333619723 | Yes | EAST ORLEANS | THDR | 238 | 2020-06-24 06:33 | 2020-06-24 06:33 | 2020-06-24 10:31 | 1190 | TFUS | 73782 | 41446474331 | 2347 | ENOI | 6 | 5 | EARM | Equipment Failure - Crossarm | N | changed x arm | -90.0246 | 29.9649 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 10 | 1333619744 | Yes | ORLEANS | THDR | 94 | 2020-06-24 06:35 | 2020-06-24 06:35 | 2020-06-24 08:10 | 940 | TFUS | 1527752 | 38973491142 | 403 | ENOI | 1 | 10 | VLFL | Tree On Line Outside R.O.W | N | limb on service pulled out of connections | -90.102 | 30.0118 | Vegetation | Transformer Fuse | Vegetation | 2020-06-24 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 21 | 1333619879 | Yes | EAST ORLEANS | THDR | 139 | 2020-06-24 06:38 | 2020-06-24 08:02 | 2020-06-24 08:57 | 2919 | LFUS | 28002 | 4146247489 | 2347 | ENOI | 6 | 21 | EARM | Equipment Failure - Crossarm | N |  | -90.0241 | 29.9663 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 25 | 1333647910 | Yes | EAST ORLEANS | THDR | 389 | 2020-06-24 06:43 | 2020-06-24 13:08 | 2020-06-24 13:12 | 9725 | LFUS | 27931 | 4063848907 | 1702 | ENOI | 6 | 25 | EARM | Equipment Failure - Crossarm | N |  | -90.0494 | 30.0055 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-24 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 44 | 1333624070 | Yes | ORLEANS | THDR | 49 | 2020-06-24 08:09 | 2020-06-24 08:28 | 2020-06-24 08:58 | 2156 | LFUS | 17771 | 3855249253 | 411 | ENOI | 1 | 44 | LGHT | Lightning | N | B phase only out for lightning | -90.115 | 30.0157 | Lightning | Line Fuse | Lightning | 2020-06-24 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 21 | 1333627284 | Yes | ORLEANS | THDR | 110 | 2020-06-24 08:55 | 2020-06-24 08:55 | 2020-06-24 10:45 | 2310 | TFUS | 1002544 | 39508462370 | 2146 | ENOI | 1 | 21 | SCHD | Scheduled Interruption | N | crew had to repair secondary arm | -90.086 | 29.9326 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-24 | DLIN | B | Council District B | Jay Banks | 70113 | 6
2020 | 872 | 1333630661 | Yes | EAST ORLEANS | THDR | 152 | 2020-06-24 08:58 | 2020-06-24 11:27 | 2020-06-24 11:30 | 85816 | DIS | 25329 | 4325550890 | 2223 | ENOI | 6 | 872 | ESLV | Equipment Failure - Automatic Sleeve | N | wire down primary at branch and haynes : Possible lightning strike? | -89.9655 | 30.0597 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 296 | 1333627636 | Yes | EAST ORLEANS | THDR | 43 | 2020-06-24 08:59 | 2020-06-24 09:38 | 2020-06-24 09:42 | 12728 | SBKR | 2223 | 4334850763 | 2223 | ENOI | 6 | 296 | ESLV | Equipment Failure - Automatic Sleeve | N | Wire burned down at an auto sleeve Possible lightning strike | -89.9655 | 30.0597 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 16 | 1333634617 | Yes | EAST ORLEANS | THDR | 267 | 2020-06-24 10:13 | 2020-06-24 10:58 | 2020-06-24 14:40 | 4272 | XFMR | 78347 | 40490475901 | 623 | ENOI | 6 | 16 | ETRD | Equipment Failure - Transformer | N |  | -90.0544 | 29.9695 | Equipment Failure | Transformer | Equipment Failure | 2020-06-24 | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 75 | 1333637766 | Yes | ORLEANS | THDR | 42 | 2020-06-24 10:47 | 2020-06-24 11:01 | 2020-06-24 11:29 | 3150 | LFUS | 27800 | 3921945756 | 1922 | ENOI | 1 | 75 | LGHT | Lightning | N | weather | -90.0955 | 29.9192 | Lightning | Line Fuse | Lightning | 2020-06-24 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 20 | 1333643806 | Yes | ORLEANS | THDR | 114 | 2020-06-24 11:14 | 2020-06-24 12:27 | 2020-06-24 13:08 | 2280 | LFUS | 33642 | 3853646279 | 1926 | ENOI | 1 | 20 | SCHD | Scheduled Interruption | N | crew on site | -90.117 | 29.9339 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-24 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 6 | 1333643921 | Yes | ORLEANS | THDR | 198 | 2020-06-24 11:18 | 2020-06-24 11:18 | 2020-06-24 14:36 | 1188 | XFMR | 57049 | 40292486217 | 1708 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | completed | -90.0605 | 29.9977 | Equipment Failure | Transformer | Equipment Failure | 2020-06-24 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 27 | 1333647918 | Yes | EAST ORLEANS | THDR | 100 | 2020-06-24 11:31 | 2020-06-24 12:11 | 2020-06-24 13:11 | 2700 | LFUS | 27963 | 4064048886 | 1702 | ENOI | 6 | 27 | EARM | Equipment Failure - Crossarm | N |  | -90.0493 | 30.005 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-24 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 5 | 1333646550 | Yes | ORLEANS | THDR | 210 | 2020-06-24 11:48 | 2020-06-24 11:48 | 2020-06-24 15:18 | 1050 | LFUS | 56819 | 3829546523 | 2014 | ENOI | 1 | 5 | VLFL | Tree On Line Outside R.O.W | N | Tree pinned down primary back energized | -90.1243 | 29.9405 | Vegetation | Line Fuse | Vegetation | 2020-06-24 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 3 | 1333646810 | Yes | ORLEANS | THDR | 70 | 2020-06-24 11:52 | 2020-06-24 11:52 | 2020-06-24 13:02 | 210 | TFUS | 613294 | 4038047469 | 614 | ENOI | 1 | 3 | VLFL | Tree On Line Outside R.O.W | N | limbs pulled service out of connections | -90.058 | 29.9662 | Vegetation | Transformer Fuse | Vegetation | 2020-06-24 | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 62 | 1333647584 | Yes | ORLEANS | THDR | 78 | 2020-06-24 12:07 | 2020-06-24 12:18 | 2020-06-24 13:25 | 4836 | LFUS | 60740 | 38393496276 | 409 | ENOI | 1 | 62 | LGHT | Lightning | N | taken out by lightning refused ok | -90.1202 | 30.026 | Lightning | Line Fuse | Lightning | 2020-06-24 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 6 | 1333648486 | Yes | EAST ORLEANS | THDR | 191 | 2020-06-24 12:20 | 2020-06-24 12:50 | 2020-06-24 15:31 | 1146 | XFMR | 74204 | 40497479460 | 613 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N |  | -90.0541 | 29.9792 | Equipment Failure | Transformer | Equipment Failure | 2020-06-24 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 30 | 1333658927 | Yes | ORLEANS | THDR | 93 | 2020-06-24 14:01 | 2020-06-24 14:42 | 2020-06-24 15:34 | 2790 | LFUS | 28016 | 3959645842 | 2147 | ENOI | 1 | 30 | ASQL | Animal - Squirrel | N | Taken out by squirrel | -90.0832 | 29.9216 | Animal | Line Fuse | Animal | 2020-06-24 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 43 | 1333665571 | Yes | EAST ORLEANS | THDR | 227 | 2020-06-24 15:16 | 2020-06-24 16:32 | 2020-06-24 19:03 | 9761 | LFUS | 21799 | 4392951465 | 2223 | ENOI | 6 | 43 | ETRD | Equipment Failure - Transformer | N | BAD TRANSFORMERS AT BASS | -89.9445 | 30.0749 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 35 | 1333666539 | Yes | EAST ORLEANS | THDR | 232 | 2020-06-24 15:18 | 2020-06-24 17:27 | 2020-06-24 19:10 | 8120 | LFUS | 26127 | 4386451333 | 2223 | ENOI | 6 | 35 | ETRD | Equipment Failure - Transformer | N | replaced | -89.9467 | 30.0711 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 41 | 1333689041 | Yes | EAST ORLEANS | FAIR | 219 | 2020-06-24 22:31 | 2020-06-24 23:27 | 2020-06-25 02:10 | 8979 | LFUS | 23024 | 4187250055 | 2212 | ENOI | 6 | 41 | EELB | Equipment Failure - Elbow | N | made up new elbow | -90.01 | 30.0367 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 42 | 1333689652 | Yes | EAST ORLEANS | THDR | 274 | 2020-06-24 23:33 | 2020-06-25 02:58 | 2020-06-25 04:07 | 11508 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 42 | EPRI | Equipment Failure - Primary Conductor | N | Failed cable in vault #4 isolated going to vlt. #3 | -89.9561 | 30.0595 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-24 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 15 | 1333708534 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-25 06:33 | 2020-06-25 06:46 | 2020-06-25 09:32 | 2685 | XFMR | 69605 | 40694489268 | 1702 | ENOI | 6 | 15 | ETRD | Equipment Failure - Transformer | N | bad transformer lid blown off oil on ground call ervironmental called crew Chad Gould | -90.0476 | 30.0061 | Equipment Failure | Transformer | Equipment Failure | 2020-06-25 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 10 | 1333708543 | Yes | EAST ORLEANS | FAIR | 86 | 2020-06-25 06:34 | 2020-06-25 07:22 | 2020-06-25 08:00 | 860 | XFMR | 56467 | 40684488987 | 1702 | ENOI | 6 | 10 | ETRD | Equipment Failure - Transformer | N | transformer lid blown off oil on ground call environmental called crew Chad Gould | -90.048 | 30.0054 | Equipment Failure | Transformer | Equipment Failure | 2020-06-25 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 2 | 1333711300 | Yes | ORLEANS | FAIR | 190 | 2020-06-25 07:20 | 2020-06-25 07:20 | 2020-06-25 10:30 | 380 | TFUS | 66182 | 39386460688 | 2147 | ENOI | 1 | 2 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.09 | 29.928 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-25 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 116 | 1333711659 | Yes | EAST ORLEANS | FAIR | 356 | 2020-06-25 07:38 | 2020-06-25 13:19 | 2020-06-25 13:34 | 41296 | LFUS | 32647 | 4123847544 | 611 | ENOI | 6 | 116 | SCHD | Scheduled Interruption | N |  | -90.0309 | 29.9678 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-25 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 4 | 1333711757 | Yes | ORLEANS | FAIR | 124 | 2020-06-25 07:41 | 2020-06-25 07:41 | 2020-06-25 09:46 | 496 | TFUS | 1002081 | 40095462381 | 2142 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N |  | -90.0675 | 29.9323 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-25 | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 5 | 1333721976 | Yes | ORLEANS | FAIR | 94 | 2020-06-25 11:07 | 2020-06-25 11:07 | 2020-06-25 12:41 | 470 | TFUS | 3001560 | 39771487672 | 1704 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N |  | -90.0768 | 30.0019 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-25 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 15 | 1333728302 | Yes | ORLEANS | FAIR | 65 | 2020-06-25 13:05 | 2020-06-25 13:05 | 2020-06-25 14:10 | 975 | TFUS | 1027451 | 39043466975 | 1925 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1006 | 29.9452 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-25 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 16 | 1333729167 | Yes | ORLEANS | FAIR | 73 | 2020-06-25 13:17 | 2020-06-25 13:17 | 2020-06-25 14:30 | 1168 | TFUS | 1464763 | 39976463231 | 2142 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0711 | 29.9347 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-25 | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 824 | 1333730057 | Yes | ORLEANS | FAIR | 57 | 2020-06-25 13:20 | 2020-06-25 13:57 | 2020-06-25 14:17 | 46968 | RCLR | 46606 | 3985746421 | 2137 | ENOI | 1 | 824 | VHCL | Vehicle | N | car hit guy wire and caused shield wire to come down SUBMITTED IN MINIMAL CLAIMS | -90.0748 | 29.9374 | Public Damage | Recloser | Public Damage | 2020-06-25 | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 1052 | 1333734478 | Yes | EAST ORLEANS | RAIN | 42 | 2020-06-25 14:11 | 2020-06-25 14:51 | 2020-06-25 14:54 | 44184 | SBKR | 510 | 4075449220 | 510 | ENOI | 6 | 1052 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons on primary; removed and closed back bkr | -90.0457 | 30.0141 | Other | Substation Breaker | Other | 2020-06-25 | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 6 | 1333764141 | Yes | ORLEANS | FAIR | 181 | 2020-06-25 14:59 | 2020-06-25 15:15 | 2020-06-25 18:00 | 1086 | XFMR | 698206 | 40011464683 | 2137 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | crew replacing pot | -90.07 | 29.9387 | Equipment Failure | Transformer | Equipment Failure | 2020-06-25 | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 555 | 1333765610 | Yes | ORLEANS | FAIR | 100 | 2020-06-25 15:03 | 2020-06-25 16:39 | 2020-06-25 16:43 | 55500 | RCLR | 54026 | 3988249289 | 510 | ENOI | 1 | 555 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up on pelita north of prentiss | -90.0733 | 30.0161 | Equipment Failure | Recloser | Equipment Failure | 2020-06-25 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 14 | 1333793221 | Yes | EAST ORLEANS | THDR | 225 | 2020-06-25 16:45 | 2020-06-25 16:49 | 2020-06-25 20:30 | 3150 | TFUS | 52647 | 40497491301 | 502 | ENOI | 6 | 14 | LGHT | Lightning | N | weather, back on | -90.0537 | 30.0114 | Lightning | Transformer Fuse | Lightning | 2020-06-25 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 496 | 1333878870 | Yes | ORLEANS | FAIR | 92 | 2020-06-26 13:28 | 2020-06-26 14:56 | 2020-06-26 15:00 | 45632 | RCLR | 62257 | 3890445946 | 1914 | ENOI | 1 | 496 | EARM | Equipment Failure - Crossarm | N | broken x arm | -90.1054 | 29.9247 | Equipment Failure | Recloser | Equipment Failure | 2020-06-26 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 111 | 1333880469 | Yes | ORLEANS | FAIR | 113 | 2020-06-26 13:37 | 2020-06-26 14:13 | 2020-06-26 15:30 | 12543 | LFUS | 21442 | 3868446213 | 1926 | ENOI | 1 | 111 | EARM | Equipment Failure - Crossarm | N | back in | -90.1121 | 29.9321 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-26 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 105 | 1333887668 | Yes | ORLEANS | FAIR | 199 | 2020-06-26 14:26 | 2020-06-26 17:39 | 2020-06-26 17:45 | 20895 | LFUS | 21436 | 3886145950 | 1921 | ENOI | 1 | 105 | EARM | Equipment Failure - Crossarm | N | repaired | -90.1065 | 29.9247 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-26 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 376 | 1333929364 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-27 06:45 | 2020-06-27 09:36 | 2020-06-27 09:44 | 67304 | LFUS | 27045 | 4279549796 | 2211 | ENOI | 6 | 376 | AOTH | Animal - Other (Describe in Remarks Field) | N | closed vfi s 26140 & 26135; crew still investigating cause of outage: Rat got into cub 8 | -97.0758 | 27.9066 | Animal | Line Fuse | Animal | 2020-06-27 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 42 | 1333933077 | Yes | ORLEANS | FAIR | 149 | 2020-06-27 10:40 | 2020-06-27 11:40 | 2020-06-27 13:09 | 6258 | OPEN | 3947547564 | 3947547564 | 907 | ENOI | 1 | 42 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0867 | 29.9689 | Scheduled Interruption | Open | Scheduled Interruption | 2020-06-27 | DLIN | B | Council District B | Jay Banks | 70119 | 6
2020 | 3 | 1333933571 | Yes | EAST ORLEANS | FAIR | 265 | 2020-06-27 11:00 | 2020-06-27 11:00 | 2020-06-27 15:25 | 795 | TFUS | 58599 | 40450482323 | 613 | ENOI | 6 | 3 | ASQL | Animal - Squirrel | N | Refused transformer taken out by squirrel | -90.0556 | 29.9869 | Animal | Transformer Fuse | Animal | 2020-06-27 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 12 | 1333933704 | Yes | ORLEANS | FAIR | 169 | 2020-06-27 11:07 | 2020-06-27 11:25 | 2020-06-27 13:56 | 2028 | LFUS | L21373 | 40070476003 | 1712 | ENOI | 1 | 12 | EFLK | Equipment Failure - Fuse Link | N | fuse blew on later and caused jumper to burn up on xfmr | -90.0679 | 29.9699 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-27 | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 12 | 1333943636 | Yes | EAST ORLEANS | FAIR | 165 | 2020-06-27 17:00 | 2020-06-27 17:45 | 2020-06-27 19:45 | 1980 | TFUS | 1468356 | 40718480225 | 613 | ENOI | 6 | 12 | ESEC | Secondary/Service Conductor | N |  | -90.0472 | 29.9814 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-27 | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 3 | 1333955834 | Yes | EAST ORLEANS | FAIR | 220 | 2020-06-28 06:33 | 2020-06-28 08:13 | 2020-06-28 10:13 | 660 | TFUS | 73813 | 41970477030 | 2347 | ENOI | 6 | 3 | VINE | Vine Growing into Line | N | cleared vines off of pole and refused pot | -90.0079 | 29.972 | Vegetation | Transformer Fuse | Vegetation | 2020-06-28 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 5 | 1333956683 | Yes | ORLEANS | FAIR | 65 | 2020-06-28 07:56 | 2020-06-28 07:58 | 2020-06-28 09:01 | 325 | TFUS | 58290 | 39656485112 | 1703 | ENOI | 1 | 5 | ASQL | Animal - Squirrel | N | refused pot | -90.0805 | 29.9949 | Animal | Transformer Fuse | Animal | 2020-06-28 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 27 | 1333959403 | Yes | ORLEANS | FAIR | 6 | 2020-06-28 11:00 | 2020-06-28 11:00 | 2020-06-28 11:06 | 162 | LFUS | 36854 | 3915045734 | 1922 | ENOI | 1 | 27 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0977 | 29.9187 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-28 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 7 | 1333971659 | Yes | ORLEANS | FAIR | 481 | 2020-06-28 17:45 | 2020-06-28 21:09 | 2020-06-29 01:46 | 3367 | XFMR | 66932 | 39168466267 | 1922 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N |  | -90.0969 | 29.9433 | Equipment Failure | Transformer | Equipment Failure | 2020-06-28 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 76 | 1333991456 | Yes | ORLEANS | FAIR | 106 | 2020-06-29 02:54 | 2020-06-29 03:18 | 2020-06-29 04:40 | 8056 | LFUS | 91343 | 3828347053 | 2013 | ENOI | 1 | 76 | EMER | Emergency Switching | N | broken crossarm | -90.1246 | 29.9551 | Other | Line Fuse | Emergency Switching | 2020-06-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 30 | 1333998174 | Yes | EAST ORLEANS | FAIR | 79 | 2020-06-29 07:11 | 2020-06-29 08:09 | 2020-06-29 08:30 | 2370 | LFUS | 21743 | 4244349367 | 1604 | ENOI | 6 | 30 | SCHD | Scheduled Interruption | N |  | -89.9924 | 30.0175 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-29 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 8 | 1333998899 | Yes | EAST ORLEANS | FAIR | 49 | 2020-06-29 07:42 | 2020-06-29 07:42 | 2020-06-29 08:31 | 392 | TFUS | 68283 | 4245749238 | 1607 | ENOI | 6 | 8 | SCHD | Scheduled Interruption | N |  | -89.992 | 30.0141 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-29 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 4 | 1333999630 | Yes | ORLEANS | FAIR | 238 | 2020-06-29 08:02 | 2020-06-29 08:02 | 2020-06-29 12:00 | 952 | TFUS | 63555 | 39493460432 | 2147 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N |  | -90.0867 | 29.9273 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-29 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 67 | 1334006568 | Yes | ORLEANS | FAIR | 507 | 2020-06-29 08:33 | 2020-06-29 09:59 | 2020-06-29 17:01 | 33969 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 67 | SCHD | Scheduled Interruption | N | Contractor on site working | -90.0879 | 29.975 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-29 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 11 | 1334006985 | Yes | ORLEANS | FAIR | 69 | 2020-06-29 08:51 | 2020-06-29 08:51 | 2020-06-29 10:00 | 759 | TFUS | 60257 | 39337457415 | 1922 | ENOI | 1 | 11 | EPOL | Equipment Failure - Pole | N |  | -90.0917 | 29.919 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-29 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 3033 | 1334007784 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 09:06 | 2020-06-29 09:45 | 2020-06-29 09:43 | 112221 | SUBN | 623 | 4081748423 | 623 | ENOI | 6 | 3033 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.044 | 29.9922 | Animal | Substation | Animal | 2020-06-29 | DSUB | D | Council District D | Jared Brossett | 70126 | 6
2020 | 713 | 1334008015 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 09:06 | 2020-06-29 09:42 | 2020-06-29 09:43 | 26381 | SUBN | 626 | 4081248423 | 626 | ENOI | 6 | 713 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0442 | 29.9922 | Animal | Substation | Animal | 2020-06-29 | DSUB | D | Council District D | Jared Brossett | 70126 | 6
2020 | 311 | 1334008118 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 09:06 | 2020-06-29 09:42 | 2020-06-29 09:43 | 11507 | SUBN | 625 | 4081348423 | 625 | ENOI | 6 | 311 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0441 | 29.9922 | Animal | Substation | Animal | 2020-06-29 | DSUB | D | Council District D | Jared Brossett | 70126 | 6
2020 | 1050 | 1334008170 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 09:06 | 2020-06-29 09:47 | 2020-06-29 09:44 | 38850 | SUBN | 621 | 4082548424 | 621 | ENOI | 6 | 1050 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0438 | 29.9922 | Animal | Substation | Animal | 2020-06-29 | DSUB | D | Council District D | Jared Brossett | 70126 | 6
2020 | 1840 | 1334008312 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 09:06 | 2020-06-29 09:42 | 2020-06-29 09:43 | 68080 | SUBN | 622 | 4082448424 | 622 | ENOI | 6 | 1840 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0438 | 29.9922 | Animal | Substation | Animal | 2020-06-29 | DSUB | D | Council District D | Jared Brossett | 70126 | 6
2020 | 2890 | 1334008664 | NO | ORLEANS | FAIR | 37 | 2020-06-29 09:06 | 2020-06-29 09:47 | 2020-06-29 09:43 | 106930 | SUBN | 627 | 4081148423 | 627 | ENOI | 1 | 2890 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0442 | 29.9922 | Animal | Substation | Animal | 2020-06-29 | DSUB | D | Council District D | Jared Brossett | 70126 | 6
2020 | 7 | 1334011350 | Yes | ORLEANS | FAIR | 122 | 2020-06-29 09:27 | 2020-06-29 09:27 | 2020-06-29 11:29 | 854 | TFUS | 58654 | 38998465345 | 1925 | ENOI | 1 | 7 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -90.1022 | 29.9408 | Other | Transformer Fuse | Other | 2020-06-29 | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 9 | 1334018406 | Yes | ORLEANS | FAIR | 111 | 2020-06-29 11:27 | 2020-06-29 11:27 | 2020-06-29 13:18 | 999 | TFUS | 1650346 | 38124468101 | 2014 | ENOI | 1 | 9 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -90.1297 | 29.9486 | Other | Transformer Fuse | Other | 2020-06-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 7 | 1334030555 | Yes | ORLEANS | FAIR | 105 | 2020-06-29 13:04 | 2020-06-29 13:08 | 2020-06-29 14:49 | 735 | TFUS | 78564 | 38489463105 | 1926 | ENOI | 1 | 7 | EFSW | Equipment Failure - Fuse Switch | N |  | -90.1184 | 29.9349 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 60 | 1334033560 | Yes | EAST ORLEANS | FAIR | 251 | 2020-06-29 13:09 | 2020-06-29 14:54 | 2020-06-29 17:20 | 15060 | LFUS | 25734 | 4328950589 | 2214 | ENOI | 6 | 60 | EPRI | Equipment Failure - Primary Conductor | N | Failed lateral cable on "B" phase vlt 118 Sw. 25734 was carrying all of "B" phase at the time up to switch 25724 Crew made repairs | -97.0758 | 27.9067 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-29 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 134 | 1334033546 | Yes | ORLEANS | FAIR | 71 | 2020-06-29 13:10 | 2020-06-29 14:11 | 2020-06-29 14:21 | 9514 | LFUS | 27650 | 3977248967 | 1704 | ENOI | 1 | 134 | HCDC | Entergy Distribution Contractor (Describe in rema | N | entergy tree crew dropped branch on wires | -90.0769 | 30.0073 | Human Error | Line Fuse | Human Error | 2020-06-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 11 | 1334037216 | Yes | EAST ORLEANS | FAIR | 46 | 2020-06-29 13:45 | 2020-06-29 13:45 | 2020-06-29 14:31 | 506 | TFUS | 1258228 | 42956506322 | 2215 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | transfer secondary | -89.9755 | 30.0523 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-29 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 10 | 1334053395 | Yes | ORLEANS | FAIR | 25 | 2020-06-29 15:47 | 2020-06-29 15:47 | 2020-06-29 16:12 | 250 | TFUS | 613211 | 39853488253 | 1704 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | contractors working on pole have xfmr out | -90.0742 | 30.0036 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-06-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 13 | 1334095181 | Yes | EAST ORLEANS | FAIR | 404 | 2020-06-30 08:15 | 2020-06-30 08:15 | 2020-06-30 14:59 | 5252 | LFUS | 27847 | 4291250653 | 2215 | ENOI | 6 | 13 | SCHD | Scheduled Interruption | N |  | -89.977 | 30.0529 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-30 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 16 | 1334100790 | Yes | ORLEANS | FAIR | 205 | 2020-06-30 09:35 | 2020-06-30 10:05 | 2020-06-30 13:00 | 3280 | LFUS | F05707 | 3854546260 | 1926 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Derek Cain 504 444 6056 (18 Rosa Parks)...jcoo12 | -90.1166 | 29.9334 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-06-30 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 297 | 1334122667 | Yes | ORLEANS | FAIR | 79 | 2020-06-30 15:35 | 2020-06-30 16:45 | 2020-06-30 16:54 | 23463 | LFUS | 14694 | 38682495639 | 401 | ENOI | 1 | 297 | EPRI | Equipment Failure - Primary Conductor | N | UG primary splice blew up in manhole switched UG loop around to get everyone back in lights | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-30 | DLIN | D | Council District D | Jared Brossett | 70124 | 6
2020 | 7 | 1334126447 | Yes | EAST ORLEANS | FAIR | 163 | 2020-06-30 16:53 | 2020-06-30 17:35 | 2020-06-30 19:37 | 1141 | TFUS | 62245 | 42974505373 | 2215 | ENOI | 6 | 7 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -89.9752 | 30.0497 | Other | Transformer Fuse | Other | 2020-06-30 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 11 | 1334126825 | Yes | ORLEANS | FAIR | 279 | 2020-06-30 17:03 | 2020-06-30 19:25 | 2020-06-30 21:42 | 3069 | TFUS | 33479 | 38480492907 | 411 | ENOI | 1 | 11 | EARM | Equipment Failure - Crossarm | N | Bad crossarm repaired | -90.1174 | 30.0168 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-06-30 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 28 | 1334134211 | Yes | ORLEANS | FAIR | 31 | 2020-06-30 19:30 | 2020-06-30 19:50 | 2020-06-30 20:01 | 868 | LFUS | 33731 | 3954748313 | 1711 | ENOI | 1 | 28 | EARM | Equipment Failure - Crossarm | N | crew replace crossarm behind lateral | -90.0841 | 29.9894 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-30 | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 69 | 1334136458 | Yes | ORLEANS | FAIR | 29 | 2020-06-30 21:11 | 2020-06-30 21:33 | 2020-06-30 21:40 | 2001 | LFUS | 17782 | 3855249274 | 411 | ENOI | 1 | 69 | EARM | Equipment Failure - Crossarm | N |  | -90.115 | 30.0162 | Equipment Failure | Line Fuse | Equipment Failure | 2020-06-30 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 1 | 1334136582 | Yes | ORLEANS | FAIR | 79 | 2020-06-30 21:14 | 2020-06-30 21:14 | 2020-06-30 22:33 | 79 | SERV | METER | 39379462185 | 1924 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter burnt up capacitor for AC | -90.0903 | 29.9321 | Equipment Failure | Service Conductor | Equipment Failure | 2020-06-30 | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 7 | 1334147216 | Yes | ORLEANS | FAIR | 212 | 2020-07-01 07:05 | 2020-07-01 08:05 | 2020-07-01 10:37 | 1484 | TFUS | 65622 | 3869946665 | 1916 | ENOI | 1 | 7 | EFLK | Equipment Failure - Fuse Link | N | Refused transfo | -90.1114 | 29.9444 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-01 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 7
2020 | 36 | 1334150602 | Yes | EAST ORLEANS | FAIR | 441 | 2020-07-01 07:10 | 2020-07-01 14:02 | 2020-07-01 14:31 | 15876 | LFUS | 26002 | 42919501767 | 2216 | ENOI | 6 | 36 | EPRI | Equipment Failure - Primary Conductor | N | Crew repairing bad cable | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-01 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 26 | 1334147468 | Yes | ORLEANS | FAIR | 60 | 2020-07-01 07:21 | 2020-07-01 07:34 | 2020-07-01 08:21 | 1560 | LFUS | 17591 | 3835448690 | 410 | ENOI | 1 | 26 | SLAK | Slack Conductor / Loose Connection | N |  | -90.1217 | 30.0001 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-01 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 25 | 1334150773 | Yes | ORLEANS | THDR | 502 | 2020-07-01 08:23 | 2020-07-01 08:23 | 2020-07-01 16:46 | 12550 | TFUS | 69834 | 39284479809 | 912 | ENOI | 1 | 25 | SCHD | Scheduled Interruption | N |  | -90.0927 | 29.9804 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-01 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 69 | 1334152940 | Yes | EAST ORLEANS | FAIR | 70 | 2020-07-01 08:55 | 2020-07-01 09:59 | 2020-07-01 10:05 | 4830 | LFUS | 21771 | 4329649447 | 1611 | ENOI | 6 | 69 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Refused C phase at two one seven seven one due to balloon on line | -89.9652 | 30.0196 | Other | Line Fuse | Other | 2020-07-01 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 51 | 1334153762 | Yes | EAST ORLEANS | FAIR | 261 | 2020-07-01 09:10 | 2020-07-01 11:07 | 2020-07-01 13:31 | 13311 | LFUS | 65425 | 4106547707 | 611 | ENOI | 6 | 51 | SCHD | Scheduled Interruption | N |  | -90.0362 | 29.9724 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-01 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 28 | 1334154181 | Yes | EAST ORLEANS | FAIR | 261 | 2020-07-01 09:10 | 2020-07-01 13:03 | 2020-07-01 13:31 | 7308 | LFUS | 37094 | 4106547707 | 611 | ENOI | 6 | 28 | SCHD | Scheduled Interruption | N |  | -90.0362 | 29.9723 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-01 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 15 | 1334156836 | Yes | EAST ORLEANS | FAIR | 87 | 2020-07-01 10:33 | 2020-07-01 10:33 | 2020-07-01 12:00 | 1305 | TFUS | 1129379 | 40427478882 | 613 | ENOI | 6 | 15 | SCHD | Scheduled Interruption | N | ustomer back in | -90.0567 | 29.9777 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-01 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 2 | 1334160895 | Yes | EAST ORLEANS | FAIR | 176 | 2020-07-01 11:48 | 2020-07-01 11:50 | 2020-07-01 14:44 | 352 | LFUS | 79364 | 4114647245 | 622 | ENOI | 6 | 2 | UNKN | Inspected Unknown | N | Refused C phase at primary metering station | -90.0339 | 29.9597 | Other | Line Fuse | Other | 2020-07-01 | DLIN | C | Council District C | Kristin Palmer | 70117 | 7
2020 | 66 | 1334172870 | Yes | EAST ORLEANS | THDR | 144 | 2020-07-01 14:21 | 2020-07-01 14:35 | 2020-07-01 16:45 | 9504 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 66 | EABS | Equipment Failure - Air Break / Disconnect Switch | N | disconnect switch replaced | -89.959 | 30.0234 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-01 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 9 | 1334177005 | Yes | EAST ORLEANS | FAIR | 251 | 2020-07-01 15:08 | 2020-07-01 18:47 | 2020-07-01 19:19 | 2259 | TFUS | 73846 | 41781476604 | 2325 | ENOI | 6 | 9 | LGHT | Lightning | N | lightning hit arrestor; cleared arrestor and refused transforrmer | -90.0137 | 29.9709 | Lightning | Transformer Fuse | Lightning | 2020-07-01 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 63 | 1334181657 | Yes | EAST ORLEANS | THDR | 176 | 2020-07-01 15:44 | 2020-07-01 16:57 | 2020-07-01 18:40 | 11088 | LFUS | 93980 | 4218847703 | 2345 | ENOI | 6 | 63 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | high wind blew jumper off switch; reset jumper and closed switch back in | -90.0008 | 29.9719 | Other | Line Fuse | Other | 2020-07-01 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 2 | 1334184309 | Yes | EAST ORLEANS | THDR | 119 | 2020-07-01 16:24 | 2020-07-01 17:33 | 2020-07-01 18:23 | 238 | LFUS | 82569 | 4192847736 | 2347 | ENOI | 6 | 2 | LGHT | Lightning | N | refused c phase; lights on | -90.009 | 29.9728 | Lightning | Line Fuse | Lightning | 2020-07-01 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 17 | 1334190059 | Yes | EAST ORLEANS | FAIR | 123 | 2020-07-01 17:43 | 2020-07-01 18:12 | 2020-07-01 19:46 | 2091 | TFUS | 1155554 | 40524474979 | 2347 | ENOI | 6 | 17 | VOHL | Overhanging Limb | N | limb took out pot; removed limb and refused | -90.0535 | 29.9667 | Vegetation | Transformer Fuse | Vegetation | 2020-07-01 | DLIN | C | Council District C | Kristin Palmer | 70117 | 7
2020 | 110 | 1334196845 | Yes | EAST ORLEANS | FAIR | 44 | 2020-07-01 19:32 | 2020-07-01 20:12 | 2020-07-01 20:16 | 4840 | LFUS | 27864 | 4079547423 | 623 | ENOI | 6 | 110 | EARM | Equipment Failure - Crossarm | N | cleared arm off primary and closed switch back in | -90.0451 | 29.9648 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-01 | DLIN | C | Council District C | Kristin Palmer | 70117 | 7
2020 | 173 | 1334199547 | Yes | ORLEANS | FAIR | 94 | 2020-07-01 20:17 | 2020-07-01 21:19 | 2020-07-01 21:51 | 16262 | LFUS | 27737 | 4001847849 | 615 | ENOI | 1 | 173 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0694 | 29.9765 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-01 | DLIN | D | Council District D | Jared Brossett | 70119 | 7
2020 | 13 | 1334200245 | Yes | ORLEANS | FAIR | 102 | 2020-07-01 20:19 | 2020-07-01 21:27 | 2020-07-01 22:01 | 1326 | TFUS | 3007211 | 40195495557 | 503 | ENOI | 1 | 13 | EARR | Equipment Failure - Arrestor | N | cleared blown arrestor and down secondary | -90.0634 | 30.0233 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-01 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 197 | 1334231781 | Yes | ORLEANS | FAIR | 96 | 2020-07-02 11:19 | 2020-07-02 12:16 | 2020-07-02 12:55 | 18912 | LFUS | 27681 | 3889447598 | 2026 | ENOI | 1 | 197 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons | -90.1051 | 29.9701 | Other | Line Fuse | Other | 2020-07-02 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 22 | 1334434530 | Yes | EAST ORLEANS | FAIR | 94 | 2020-07-04 16:08 | 2020-07-04 16:25 | 2020-07-04 17:42 | 2068 | LFUS | 24886 | 4802151168 | 1204 | ENOI | 6 | 22 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | SWB hit underground cable took out lateral call crew brian garnett SWB NOT ON SENCE RELATED TO AMFM 1334461574 | -89.8154 | 30.0653 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-04 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 2 | 1334443195 | Yes | EAST ORLEANS | FAIR | 217 | 2020-07-04 18:23 | 2020-07-04 18:48 | 2020-07-04 22:00 | 434 | TFUS | 13140282 | 48045512476 | 1204 | ENOI | 6 | 2 | EPRI | Equipment Failure - Primary Conductor | N | repaired cable | -89.8145 | 30.0674 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-04 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 1 | 1334457650 | Yes | ORLEANS | FAIR | 36 | 2020-07-04 23:08 | 2020-07-04 23:08 | 2020-07-04 23:44 | 36 | SERV | METER | 39667488116 | 1704 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | AMI meter not working insatalled new meter | -90.0803 | 30.0031 | Other | Service Conductor | Other | 2020-07-04 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 63 | 1334460382 | Yes | EAST ORLEANS | FAIR | 176 | 2020-07-05 01:34 | 2020-07-05 04:11 | 2020-07-05 04:30 | 11088 | LFUS | 21760 | 4317949561 | 1611 | ENOI | 6 | 63 | EELB | Equipment Failure - Elbow | N | bad underground elbow in frt of 4835 Perrili Dr. | -89.9689 | 30.0228 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-05 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 17 | 1334465350 | Yes | EAST ORLEANS | FAIR | 455 | 2020-07-05 01:56 | 2020-07-05 08:19 | 2020-07-05 09:31 | 7735 | LFUS | 23737 | 4310049554 | 1611 | ENOI | 6 | 17 | ETRD | Equipment Failure - Transformer | N | repaired | -89.9713 | 30.0227 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-05 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 71 | 1334480470 | Yes | EAST ORLEANS | RAIN | 397 | 2020-07-05 11:32 | 2020-07-05 16:50 | 2020-07-05 18:09 | 28187 | XFMR | 1001 | 00000000000 | 1001 | ENOI | 6 | 71 | ETRD | Equipment Failure - Transformer | N | changed bad transformer |  |  | Equipment Failure | Transformer | Equipment Failure | 2020-07-05 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 241 | 1334495381 | Yes | ORLEANS | THDR | 209 | 2020-07-05 13:27 | 2020-07-05 16:48 | 2020-07-05 16:56 | 50369 | DIS | 23513 | 3804446036 | 2013 | ENOI | 1 | 241 | EARM | Equipment Failure - Crossarm | N | crossarm broken on lateral | -90.1206 | 29.9169 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-07-05 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 7
2020 | 2122 | 1334485587 | Yes | ORLEANS | THDR | 147 | 2020-07-05 13:28 | 2020-07-05 16:08 | 2020-07-05 15:54 | 311934 | SBKR | 2013 | 3847547389 | 2013 | ENOI | 1 | 2122 | EARM | Equipment Failure - Crossarm | N | at lateral location crossarm failure | -90.1183 | 29.9644 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-07-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 798 | 1334492158 | Yes | ORLEANS | FAIR | 10 | 2020-07-05 15:31 | 2020-07-05 15:40 | 2020-07-05 15:40 | 7980 | SBKR | 1912 | 3908945676 | 1912 | ENOI | 1 | 798 | EMER | Emergency Switching | N |  | -90.0995 | 29.9172 | Other | Substation Breaker | Emergency Switching | 2020-07-05 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 515 | 1334494607 | Yes | ORLEANS | THDR | 102 | 2020-07-05 15:41 | 2020-07-05 17:20 | 2020-07-05 17:23 | 52530 | DIS | 24530 | 3849745644 | 1912 | ENOI | 1 | 515 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burnt at location of Tchoupitoulas & Joesph Sts, | -90.1183 | 29.9164 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-07-05 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 7
2020 | 25 | 1334506820 | Yes | EAST ORLEANS | FAIR | 419 | 2020-07-05 20:34 | 2020-07-06 01:38 | 2020-07-06 03:33 | 10475 | LFUS | 26296 | 4381351016 | 2217 | ENOI | 6 | 25 | EPRI | Equipment Failure - Primary Conductor | N | bad cable bet vlt. 100 to vlt 59 | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-05 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 7
2020 | 48 | 1334519629 | Yes | ORLEANS | FAIR | 104 | 2020-07-06 07:55 | 2020-07-06 08:15 | 2020-07-06 09:39 | 4992 | LFUS | 91172 | 3963648824 | 1704 | ENOI | 1 | 48 | SCHD | Scheduled Interruption | N | back on | -90.0811 | 30.0034 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 11 | 1334529051 | Yes | ORLEANS | FAIR | 156 | 2020-07-06 07:55 | 2020-07-06 10:10 | 2020-07-06 10:31 | 1716 | TFUS | 1304784 | 39640487488 | 1704 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | back on | -90.0809 | 30.0014 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 9 | 1334521311 | Yes | ORLEANS | THDR | 100 | 2020-07-06 08:20 | 2020-07-06 08:20 | 2020-07-06 10:00 | 900 | TFUS | 75640 | 3888345706 | 1927 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | crew on site reli work | -90.1058 | 29.9178 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-06 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 239 | 1334521867 | Yes | EAST ORLEANS | FAIR | 14 | 2020-07-06 08:45 | 2020-07-06 08:55 | 2020-07-06 09:00 | 3346 | LFUS | 17998 | 4158049987 | 2212 | ENOI | 6 | 239 | EFSW | Equipment Failure - Fuse Switch | N | contractor had swicth burning, replaced | -90.0195 | 30.0348 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-06 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 17 | 1334530585 | Yes | EAST ORLEANS | FAIR | 66 | 2020-07-06 10:00 | 2020-07-06 10:42 | 2020-07-06 11:06 | 1122 | TFUS | 59932 | 41018477295 | 611 | ENOI | 6 | 17 | SCHD | Scheduled Interruption | N | contract crew on site reli work | -90.0376 | 29.9731 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-06 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 83 | 1334556432 | Yes | ORLEANS | FAIR | 190 | 2020-07-06 18:01 | 2020-07-06 20:28 | 2020-07-06 21:11 | 15770 | LFUS | 55730 | 3829946513 | 2014 | ENOI | 1 | 83 | VOHL | Overhanging Limb | N |  | -90.1243 | 29.9405 | Vegetation | Line Fuse | Vegetation | 2020-07-06 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 11 | 1334563500 | Yes | EAST ORLEANS | FAIR | 295 | 2020-07-07 00:35 | 2020-07-07 00:35 | 2020-07-07 05:30 | 3245 | TFUS | 495171 | 41448497423 | 1010 | ENOI | 6 | 11 | EPRI | Equipment Failure - Primary Conductor | N | repaired cable | -90.0235 | 30.0283 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-07 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 88 | 1334569351 | Yes | EAST ORLEANS | FAIR | 42 | 2020-07-07 08:19 | 2020-07-07 08:52 | 2020-07-07 09:01 | 3696 | LFUS | 32305 | 4164647339 | 2346 | ENOI | 6 | 88 | SCHD | Scheduled Interruption | N | back on | -90.0184 | 29.9622 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-07 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 213 | 1334569922 | Yes | EAST ORLEANS | FAIR | 333 | 2020-07-07 08:27 | 2020-07-07 13:05 | 2020-07-07 14:00 | 70929 | DIS | D01649 | 4107947703 | 611 | ENOI | 6 | 213 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0359 | 29.9722 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-07-07 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 48 | 1334574807 | Yes | ORLEANS | FAIR | 144 | 2020-07-07 09:20 | 2020-07-07 10:30 | 2020-07-07 11:44 | 6912 | LFUS | 37984 | 3942947766 | 912 | ENOI | 1 | 48 | SCHD | Scheduled Interruption | N | back on | -90.0882 | 29.9745 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-07 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 41 | 1334575594 | Yes | ORLEANS | FAIR | 66 | 2020-07-07 10:25 | 2020-07-07 10:45 | 2020-07-07 11:31 | 2706 | LFUS | 81769 | 3969048828 | 1704 | ENOI | 1 | 41 | EARM | Equipment Failure - Crossarm | N | crew repaired crossarm | -90.0795 | 30.0035 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-07 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 29 | 1334598970 | Yes | ORLEANS | THDR | 118 | 2020-07-07 13:39 | 2020-07-07 14:37 | 2020-07-07 15:37 | 3422 | TFUS | 1108924 | 3996446118 | 2132 | ENOI | 1 | 29 | LGHT | Lightning | N | , lightning arrestor blown, cleared and refused | -90.0718 | 29.9292 | Lightning | Transformer Fuse | Lightning | 2020-07-07 | DLIN | B | Council District B | Jay Banks | 70130 | 7
2020 | 12 | 1334599972 | Yes | ORLEANS | THDR | 105 | 2020-07-07 13:49 | 2020-07-07 14:38 | 2020-07-07 15:34 | 1260 | TFUS | 79696 | 38994459054 | 1917 | ENOI | 1 | 12 | EARR | Equipment Failure - Arrestor | N | refused | -90.1025 | 29.9236 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-07 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 9 | 1334619100 | Yes | EAST ORLEANS | RAIN | 65 | 2020-07-07 17:53 | 2020-07-07 17:53 | 2020-07-07 18:58 | 585 | TFUS | 500379 | 41595498988 | 2212 | ENOI | 6 | 9 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -90.019 | 30.0325 | Other | Transformer Fuse | Other | 2020-07-07 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 36 | 1334619462 | Yes | ORLEANS | THDR | 231 | 2020-07-07 18:09 | 2020-07-07 18:14 | 2020-07-07 22:00 | 8316 | LFUS | 21185 | 3807446657 | B0527 | ENOI | 1 | 36 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.131 | 29.9444 | Vegetation | Line Fuse | Vegetation | 2020-07-07 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 223 | 1334635963 | Yes | EAST ORLEANS | FAIR | 125 | 2020-07-08 02:34 | 2020-07-08 04:16 | 2020-07-08 04:39 | 27875 | SBKR | 2347 | 4216047802 | 2347 | ENOI | 6 | 223 | EPRI | Equipment Failure - Primary Conductor | N | Possible bad cable under Industrial Canal | -90.0018 | 29.9747 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-07-08 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 5 | 1334650216 | Yes | ORLEANS | FAIR | 127 | 2020-07-08 09:19 | 2020-07-08 09:22 | 2020-07-08 11:26 | 635 | XFMR | 50683 | 40249491891 | 503 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | changed bad transformer | -90.0618 | 30.0134 | Equipment Failure | Transformer | Equipment Failure | 2020-07-08 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 7 | 1334660245 | Yes | ORLEANS | FAIR | 137 | 2020-07-08 12:27 | 2020-07-08 12:31 | 2020-07-08 14:44 | 959 | TFUS | 500211 | 38084469992 | B0527 | ENOI | 1 | 7 | EFLK | Equipment Failure - Fuse Link | N | replaced | -90.1307 | 29.9538 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 596 | 1334687007 | Yes | ORLEANS | FAIR | 139 | 2020-07-08 14:52 | 2020-07-08 17:03 | 2020-07-08 17:11 | 82844 | DIS | 24938 | 3854047232 | 2015 | ENOI | 1 | 596 | EPRI | Equipment Failure - Primary Conductor | N | primary cvonducter fell, crew restore wire | -90.1162 | 29.96 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-07-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 798 | 1334686984 | Yes | ORLEANS | FAIR | 65 | 2020-07-08 14:53 | 2020-07-08 16:04 | 2020-07-08 15:58 | 51870 | RCLR | 24950 | 38402470587 | 2015 | ENOI | 1 | 798 | EPRI | Equipment Failure - Primary Conductor | N | phase down, switched around | -90.1208 | 29.9554 | Equipment Failure | Recloser | Equipment Failure | 2020-07-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 1 | 1334758757 | Yes | ORLEANS | FAIR | 132 | 2020-07-09 15:42 | 2020-07-09 15:42 | 2020-07-09 17:54 | 132 | SERV | SERVICE | 38539477613 | 2026 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed burned connections at weatherhead Burned ct metering bypassed to change connections Turned in pink ticket to office OC | -90.1161 | 29.9745 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 31 | 1334770656 | Yes | ORLEANS | FAIR | 298 | 2020-07-09 19:04 | 2020-07-09 20:22 | 2020-07-10 00:02 | 9238 | TFUS | 28528 | 39504480258 | 1711 | ENOI | 1 | 31 | ESEC | Secondary/Service Conductor | N | hot leg connections burning up changed out connections on bundle service feeding down verna ct in rear | -90.0856 | 29.9817 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-09 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 19 | 1334789202 | Yes | EAST ORLEANS | FAIR | 112 | 2020-07-10 07:51 | 2020-07-10 08:31 | 2020-07-10 09:43 | 2128 | LFUS | 27838 | 4195347461 | 2345 | ENOI | 6 | 19 | ASQL | Animal - Squirrel | N | squirrel took out latral refused back in | -90.0086 | 29.9653 | Animal | Line Fuse | Animal | 2020-07-10 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 1 | 1334791232 | Yes | EAST ORLEANS | FAIR | 112 | 2020-07-10 09:18 | 2020-07-10 09:18 | 2020-07-10 11:10 | 112 | TFUS | 1128201 | 41648487033 | 1608 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N |  | -90.0175 | 29.9996 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 1 | 1334791729 | Yes | ORLEANS | FAIR | 109 | 2020-07-10 09:23 | 2020-07-10 09:23 | 2020-07-10 11:12 | 109 | XFMR | 1429012 | 3800845885 | B0526 | ENOI | 1 | 1 | ETRD | Equipment Failure - Transformer | N | crew replaced transformer | -90.1336 | 29.9229 | Equipment Failure | Transformer | Equipment Failure | 2020-07-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 8 | 1334792719 | Yes | EAST ORLEANS | FAIR | 117 | 2020-07-10 09:53 | 2020-07-10 09:53 | 2020-07-10 11:50 | 936 | TFUS | 1599527 | 40855477822 | 622 | ENOI | 6 | 8 | SCHD | Scheduled Interruption | N | back on | -90.043 | 29.9746 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-10 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 29 | 1334792732 | Yes | EAST ORLEANS | FAIR | 115 | 2020-07-10 09:55 | 2020-07-10 11:21 | 2020-07-10 11:50 | 3335 | LFUS | 37150 | 40855477822 | 622 | ENOI | 6 | 29 | SCHD | Scheduled Interruption | N | back on | -90.0431 | 29.9746 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-10 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 31 | 1334820834 | Yes | ORLEANS | FAIR | 232 | 2020-07-10 18:18 | 2020-07-10 18:42 | 2020-07-10 22:10 | 7192 | TFUS | 28528 | 39504480258 | 1711 | ENOI | 1 | 31 | ESEC | Secondary/Service Conductor | N | secondary cable burning | -90.0856 | 29.9817 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-10 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 1 | 1334826665 | Yes | ORLEANS | FAIR | 199 | 2020-07-10 22:20 | 2020-07-10 22:20 | 2020-07-11 01:39 | 199 | SERV | SERVICE | 40307484209 | 1708 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | repired burned connections at pole | -90.06 | 29.9922 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-10 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 1 | 1334828203 | Yes | ORLEANS | FAIR | 142 | 2020-07-11 00:07 | 2020-07-11 00:07 | 2020-07-11 02:29 | 142 | LFUS | 33299 | 39102470307 | 1553 | ENOI | 1 | 1 | ETRD | Equipment Failure - Transformer | N | refused lateral taken out by bad transformer | -90.0988 | 29.9545 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-11 | DLIN | B | Council District B | Jay Banks | 70125 | 7
2020 | 138 | 1334840377 | Yes | EAST ORLEANS | FAIR | 242 | 2020-07-11 06:44 | 2020-07-11 10:39 | 2020-07-11 10:46 | 33396 | DIS | 23586 | 4196647238 | 2345 | ENOI | 6 | 138 | EMER | Emergency Switching | N |  | -90.008 | 29.9591 | Other | Disconnect Switch | Emergency Switching | 2020-07-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 7 | 1334840403 | Yes | EAST ORLEANS | FAIR | 268 | 2020-07-11 06:44 | 2020-07-11 06:44 | 2020-07-11 11:12 | 1876 | DIS | 25144 | 4164047961 | 2345 | ENOI | 6 | 7 | EMER | Emergency Switching | N | switching | -90.0181 | 29.9794 | Other | Disconnect Switch | Emergency Switching | 2020-07-11 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 499 | 1334835080 | Yes | EAST ORLEANS | FAIR | 206 | 2020-07-11 06:44 | 2020-07-11 09:52 | 2020-07-11 10:10 | 102794 | SBKR | 2345 | 4215647804 | 2345 | ENOI | 6 | 499 | EPRI | Equipment Failure - Primary Conductor | N | Failed UG cable 87' from TP on eastside of Industrial Canal | -90.0019 | 29.9747 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-07-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 21 | 1334834831 | Yes | EAST ORLEANS | FAIR | 318 | 2020-07-11 06:45 | 2020-07-11 07:29 | 2020-07-11 12:03 | 6678 | LFUS | 28002 | 4146247489 | 2347 | ENOI | 6 | 21 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | switched feeder back in and switched out under ground terminal pole theere gonna thump it today | -90.0241 | 29.9663 | Other | Line Fuse | Other | 2020-07-11 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 1 | 1334834936 | Yes | EAST ORLEANS | FAIR | 255 | 2020-07-11 06:57 | 2020-07-11 06:57 | 2020-07-11 11:13 | 255 | TFUS | 1075630 | 4159047990 | 612 | ENOI | 6 | 1 | EMER | Emergency Switching | N | feeder 2345 | -90.0197 | 29.98 | Other | Transformer Fuse | Emergency Switching | 2020-07-11 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 11 | 1334842152 | Yes | ORLEANS | FAIR | 338 | 2020-07-11 11:25 | 2020-07-11 11:30 | 2020-07-11 17:04 | 3718 | XFMR | 61841 | 39146477281 | 911 | ENOI | 1 | 11 | ETRD | Equipment Failure - Transformer | N | bad transformer changed out and upgraded | -90.097 | 29.9736 | Equipment Failure | Transformer | Equipment Failure | 2020-07-11 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 96 | 1334843550 | Yes | ORLEANS | FAIR | 348 | 2020-07-11 12:38 | 2020-07-11 17:55 | 2020-07-11 18:26 | 33408 | TFUS | 26651 | 39648495304 | 509 | ENOI | 1 | 96 | CFID | Cable Failure in duct | N | Bad cable between vaults trouble shot and switched out bad cable everyone back in lights | -90.0805 | 30.0229 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 77 | 1334850951 | Yes | EAST ORLEANS | FAIR | 111 | 2020-07-11 15:09 | 2020-07-11 16:06 | 2020-07-11 17:01 | 8547 | LFUS | 21024 | 4046347924 | 613 | ENOI | 6 | 77 | SCHD | Scheduled Interruption | N | back on | -90.0552 | 29.9787 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-11 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 25 | 1334859839 | Yes | EAST ORLEANS | FAIR | 232 | 2020-07-11 19:08 | 2020-07-11 22:57 | 2020-07-11 23:00 | 5800 | LFUS | 21427 | 4280249301 | 1604 | ENOI | 6 | 25 | ETRD | Equipment Failure - Transformer | N | replaced | -89.9811 | 30.0158 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-11 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 1709 | 1334861046 | NO | ORLEANS | FAIR | 89 | 2020-07-11 19:35 | 2020-07-11 21:00 | 2020-07-11 21:04 | 152101 | SUBN | 1921 | 3908745682 | 1921 | ENOI | 1 | 1709 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 | -90.0996 | 29.9173 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 2520 | 1334861314 | NO | ORLEANS | FAIR | 89 | 2020-07-11 19:35 | 2020-07-11 21:06 | 2020-07-11 21:04 | 224280 | SUBN | 1924 | 3909545682 | 1924 | ENOI | 1 | 2520 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 | -90.0994 | 29.9173 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 1799 | 1334861380 | NO | ORLEANS | FAIR | 89 | 2020-07-11 19:35 | 2020-07-11 21:14 | 2020-07-11 21:04 | 160111 | SUBN | 1923 | 3909045682 | 1923 | ENOI | 1 | 1799 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 | -90.0995 | 29.9173 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 1808 | 1334861624 | NO | ORLEANS | FAIR | 89 | 2020-07-11 19:35 | 2020-07-11 21:03 | 2020-07-11 21:04 | 160912 | SUBN | 1922 | 3908945682 | 1922 | ENOI | 1 | 1808 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 | -90.0995 | 29.9173 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 1325 | 1334861874 | NO | ORLEANS | FAIR | 89 | 2020-07-11 19:35 | 2020-07-11 21:04 | 2020-07-11 21:04 | 117925 | SUBN | 1927 | 3909945683 | 1927 | ENOI | 1 | 1325 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 | -90.0992 | 29.9173 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 949 | 1334861587 | NO | ORLEANS | FAIR | 205 | 2020-07-11 19:35 | 2020-07-11 22:59 | 2020-07-11 23:00 | 194545 | SUBN | 1926 | 3909745682 | 1926 | ENOI | 1 | 949 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 | -90.0993 | 29.9173 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 2259 | 1334861323 | NO | ORLEANS | FAIR | 240 | 2020-07-11 19:35 | 2020-07-11 23:32 | 2020-07-11 23:35 | 542160 | SUBN | 1925 | 3909645682 | 1925 | ENOI | 1 | 2259 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 | -90.0993 | 29.9173 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 1885 | 1334861582 | NO | ORLEANS | FAIR | 82 | 2020-07-11 20:55 | 2020-07-11 22:14 | 2020-07-11 22:18 | 154570 | SUBN | 1916 | 3909645677 | 1916 | ENOI | 1 | 1885 | BKRO | Breaker - Oil | N | Substation Breaker - Oil Breaker 1925 Failed damaging breakers 1916 & 1926 | -90.0993 | 29.9172 | Equipment Failure | Substation | Equipment Failure | 2020-07-11 | DSUB | B | Council District B | Jay Banks | 70115 | 7
2020 | 1211 | 1334871811 | Yes | ORLEANS | FAIR | 90 | 2020-07-11 22:26 | 2020-07-11 23:57 | 2020-07-11 23:56 | 108990 | DIS | 25097 | 3912245887 | 1923 | ENOI | 1 | 1211 | ECNS | Equipment Failure - Connector Sleeve | N | primary jumper broke, crew repaired | -90.0985 | 29.9231 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-07-11 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 74 | 1334882014 | Yes | EAST ORLEANS | FAIR | 285 | 2020-07-12 02:56 | 2020-07-12 04:14 | 2020-07-12 07:41 | 21090 | LFUS | 26117 | 4178549477 | 1610 | ENOI | 6 | 74 | EELB | Equipment Failure - Elbow | N | changed bad elbow | -90.013 | 30.0208 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-12 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 1 | 1334891699 | Yes | ORLEANS | FAIR | 130 | 2020-07-12 06:43 | 2020-07-12 06:56 | 2020-07-12 08:53 | 130 | SERV | SERVICE | 38095470254 | B0527 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed out connection voltage good | -90.1305 | 29.9545 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-12 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 135 | 1334900492 | Yes | ORLEANS | FAIR | 195 | 2020-07-12 08:00 | 2020-07-12 10:53 | 2020-07-12 11:16 | 26325 | LFUS | 21515 | 3900646470 | 1925 | ENOI | 1 | 135 | EMER | Emergency Switching | N | crew onsite making repairs | -90.1021 | 29.9391 | Other | Line Fuse | Emergency Switching | 2020-07-12 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 151 | 1334897037 | Yes | ORLEANS | FAIR | 78 | 2020-07-12 08:08 | 2020-07-12 08:08 | 2020-07-12 09:26 | 11778 | TFUS | 31060 | 4004746575 | 1826 | ENOI | 1 | 151 | SCHD | Scheduled Interruption | N | Contractors have lateral out | -90.0688 | 29.9417 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-12 | DLIN | B | Council District B | Jay Banks | 70130 | 7
2020 | 1 | 1334917893 | Yes | EAST ORLEANS | FAIR | 87 | 2020-07-12 17:11 | 2020-07-12 17:11 | 2020-07-12 18:38 | 87 | SERV | SERVICE | 40540485758 | 1710 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | hot leg burned off at connection fixed connection and got great voltage | -90.053 | 29.9965 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-12 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 41 | 1334935454 | Yes | EAST ORLEANS | FAIR | 229 | 2020-07-12 20:01 | 2020-07-12 23:26 | 2020-07-12 23:50 | 9389 | LFUS | 27150 | 4376051136 | 2217 | ENOI | 6 | 41 | ETRD | Equipment Failure - Transformer | N | replaced | -89.95 | 30.0658 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 7
2020 | 31 | 1334951511 | Yes | ORLEANS | HEAT | 150 | 2020-07-13 08:00 | 2020-07-13 09:31 | 2020-07-13 10:30 | 4650 | LFUS | 21670 | 3956148950 | 1704 | ENOI | 1 | 31 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0836 | 30.007 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-13 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 15 | 1334951124 | Yes | ORLEANS | FAIR | 360 | 2020-07-13 08:31 | 2020-07-13 10:14 | 2020-07-13 14:31 | 5400 | TFUS | 58661 | 40289476194 | 614 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.061 | 29.9704 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-13 | DLIN | C | Council District C | Kristin Palmer | 70116 | 7
2020 | 5 | 1334953136 | Yes | EAST ORLEANS | FAIR | 284 | 2020-07-13 09:16 | 2020-07-13 13:14 | 2020-07-13 14:00 | 1420 | XFMR | 58802 | 48464512640 | 1204 | ENOI | 6 | 5 | ETRD | Equipment Failure - Transformer | N | CHANGED OUT TRANSFORMER | -89.8012 | 30.0678 | Equipment Failure | Transformer | Equipment Failure | 2020-07-13 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 12 | 1334957775 | Yes | ORLEANS | FAIR | 154 | 2020-07-13 10:01 | 2020-07-13 10:01 | 2020-07-13 12:35 | 1848 | TFUS | 1304361 | 39815488381 | 1704 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0755 | 30.0037 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-13 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 8 | 1334958182 | Yes | EAST ORLEANS | FAIR | 34 | 2020-07-13 10:12 | 2020-07-13 10:12 | 2020-07-13 10:46 | 272 | TFUS | 1585507 | 41043492472 | 501 | ENOI | 6 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0365 | 30.0147 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-13 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 80 | 1334960128 | Yes | ORLEANS | THDR | 25 | 2020-07-13 11:00 | 2020-07-13 11:23 | 2020-07-13 11:25 | 2000 | SBKR | 1701 | 4024448723 | 1701 | ENOI | 1 | 80 | LGHT | Lightning | N | serviceman did not see any targets on breaker; doc gave order to close bkr | -90.062 | 30.0006 | Lightning | Substation Breaker | Lightning | 2020-07-13 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 89 | 1335004779 | Yes | ORLEANS | FAIR | 91 | 2020-07-13 18:34 | 2020-07-13 19:21 | 2020-07-13 20:05 | 8099 | LFUS | 21084 | 3850746102 | 1917 | ENOI | 1 | 89 | VLGL | Tree/Limb Growing Inside R.O.W. | N | tree limb | -90.1179 | 29.9291 | Vegetation | Line Fuse | Vegetation | 2020-07-13 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 7
2020 | 7 | 1335013293 | Yes | EAST ORLEANS | FAIR | 178 | 2020-07-14 00:45 | 2020-07-14 00:45 | 2020-07-14 03:43 | 1246 | TFUS | 593454 | 43354496091 | 1611 | ENOI | 6 | 7 | ECON | Equipment Failure - Connector / Sleeve | N | copper ove alum connection on transformer jumper to open wirre | -89.9635 | 30.0239 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-14 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 12 | 1335021095 | Yes | ORLEANS | HEAT | 52 | 2020-07-14 07:54 | 2020-07-14 07:54 | 2020-07-14 08:46 | 624 | TFUS | 73525 | 39734489159 | 1704 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0779 | 30.006 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-14 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 19 | 1335023843 | Yes | ORLEANS | FAIR | 30 | 2020-07-14 09:00 | 2020-07-14 09:00 | 2020-07-14 09:30 | 570 | TFUS | 73808 | 39742488049 | 1704 | ENOI | 1 | 19 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0777 | 30.0029 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-14 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 66 | 1335023633 | Yes | EAST ORLEANS | HEAT | 64 | 2020-07-14 09:04 | 2020-07-14 09:13 | 2020-07-14 10:08 | 4224 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 66 | ASQL | Animal - Squirrel | N | Scouted line saw squirrel and cleared refused lateral customers back in lights | -89.959 | 30.0234 | Animal | Line Fuse | Animal | 2020-07-14 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 14 | 1335029131 | Yes | ORLEANS | HEAT | 240 | 2020-07-14 09:30 | 2020-07-14 09:30 | 2020-07-14 13:31 | 3360 | TFUS | 68970 | 40347476240 | 614 | ENOI | 1 | 14 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0591 | 29.9704 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-14 | DLIN | C | Council District C | Kristin Palmer | 70116 | 7
2020 | 15 | 1335044639 | Yes | EAST ORLEANS | HEAT | 87 | 2020-07-14 13:44 | 2020-07-14 13:44 | 2020-07-14 15:11 | 1305 | TFUS | C71761 | 40666476392 | 622 | ENOI | 6 | 15 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0489 | 29.9708 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-14 | DLIN | C | Council District C | Kristin Palmer | 70117 | 7
2020 | 62 | 1335047210 | Yes | ORLEANS | THDR | 83 | 2020-07-14 14:55 | 2020-07-14 15:07 | 2020-07-14 16:18 | 5146 | LFUS | 21370 | 4003647425 | 1512 | ENOI | 1 | 62 | VLGL | Tree/Limb Growing Inside R.O.W. | N | B phase of lateral was blown do to tree limbs in right of way | -90.0691 | 29.9649 | Vegetation | Line Fuse | Vegetation | 2020-07-14 | DLIN | C | Council District C | Kristin Palmer | 70116 | 7
2020 | 403 | 1335055423 | Yes | ORLEANS | THDR | 177 | 2020-07-14 15:43 | 2020-07-14 18:34 | 2020-07-14 18:40 | 71331 | DIS | 23182 | 3814546744 | 2014 | ENOI | 1 | 403 | LGHT | Lightning | N | broke crossarm & primary down at intersection of short and jeannette | -90.1291 | 29.9468 | Lightning | Disconnect Switch | Lightning | 2020-07-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 1214 | 1335057202 | Yes | ORLEANS | THDR | 181 | 2020-07-14 15:43 | 2020-07-14 16:50 | 2020-07-14 18:44 | 87408 | RCLR | 91108 | 3819046694 | 2014 | ENOI | 1 | 1214 | LGHT | Lightning | N | broke crossarm & primary down at intersection of short and jeannette | -90.1276 | 29.9455 | Lightning | Recloser | Lightning | 2020-07-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 576 | 1335052417 | Yes | ORLEANS | THDR | 33 | 2020-07-14 15:43 | 2020-07-14 16:41 | 2020-07-14 16:16 | 19008 | SBKR | 2014 | 3847647389 | 2014 | ENOI | 1 | 576 | LGHT | Lightning | N | broke crossarm and primary down at intersection of jeannette and short st lightning burned down shield wire and two phases causing the crossarm to break | -90.1183 | 29.9644 | Lightning | Substation Breaker | Lightning | 2020-07-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 17 | 1335057716 | Yes | ORLEANS | THDR | 120 | 2020-07-14 16:40 | 2020-07-14 16:43 | 2020-07-14 18:41 | 2040 | LFUS | 36958 | 3820146837 | 2015 | ENOI | 1 | 17 | EMER | Emergency Switching | N | Taken out for safety to repair damaged primary & x-arms on fdr 2014 see that case | -90.1273 | 29.9493 | Other | Line Fuse | Emergency Switching | 2020-07-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 89 | 1335061616 | Yes | ORLEANS | FAIR | 30 | 2020-07-14 17:10 | 2020-07-14 17:38 | 2020-07-14 17:40 | 2670 | LFUS | 37943 | 3839445846 | 1914 | ENOI | 1 | 89 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1215 | 29.9221 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-14 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 7
2020 | 286 | 1335077290 | Yes | ORLEANS | FAIR | 226 | 2020-07-14 22:40 | 2020-07-15 01:58 | 2020-07-15 02:26 | 64636 | DIS | 22197 | 3994446276 | 2142 | ENOI | 1 | 286 | SCHD | Scheduled Interruption | N | back on | -90.0724 | 29.9333 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-07-14 | DLIN | B | Council District B | Jay Banks | 70130 | 7
2020 | 263 | 1335077305 | Yes | ORLEANS | FAIR | 226 | 2020-07-14 22:40 | 2020-07-15 01:50 | 2020-07-15 02:26 | 59438 | DIS | 15529 | 3995346355 | 2142 | ENOI | 1 | 263 | SCHD | Scheduled Interruption | N | back on | -90.0721 | 29.9357 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-07-14 | DLIN | B | Council District B | Jay Banks | 70130 | 7
2020 | 226 | 1335091577 | Yes | EAST ORLEANS | FAIR | 270 | 2020-07-15 07:00 | 2020-07-15 11:25 | 2020-07-15 11:30 | 61020 | LFUS | 81602 | 4113747634 | 611 | ENOI | 6 | 226 | SCHD | Scheduled Interruption | N | crew onsite | -90.034 | 29.9704 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 12 | 1335089896 | Yes | EAST ORLEANS | FAIR | 53 | 2020-07-15 07:57 | 2020-07-15 07:57 | 2020-07-15 08:50 | 636 | TFUS | 60528 | 41062476942 | 611 | ENOI | 6 | 12 | SCHD | Scheduled Interruption | N | crew on site | -90.0363 | 29.972 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 1 | 1335090150 | Yes | EAST ORLEANS | FAIR | 159 | 2020-07-15 08:13 | 2020-07-15 08:13 | 2020-07-15 10:52 | 159 | SERV | SERVICE | 44457501280 | 1205 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Crew install a dry cell | -89.9282 | 30.0378 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-15 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 4 | 1335114065 | Yes | ORLEANS | FAIR | 484 | 2020-07-15 09:26 | 2020-07-15 16:46 | 2020-07-15 17:31 | 1936 | XFMR | 646342 | 39188466117 | 2021 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | change transformer | -90.0961 | 29.943 | Equipment Failure | Transformer | Equipment Failure | 2020-07-15 | DLIN | B | Council District B | Jay Banks | 70125 | 7
2020 | 66 | 1335093184 | Yes | EAST ORLEANS | FAIR | 56 | 2020-07-15 09:27 | 2020-07-15 09:34 | 2020-07-15 10:23 | 3696 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 66 | ASQL | Animal - Squirrel | N | squirrel took out lateral refused it got good voltage turned in a ticket for animal gaurd on pole | -89.959 | 30.0234 | Animal | Line Fuse | Animal | 2020-07-15 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 11 | 1335094585 | Yes | ORLEANS | FAIR | 60 | 2020-07-15 10:00 | 2020-07-15 10:00 | 2020-07-15 11:00 | 660 | TFUS | 579268 | 39747487527 | 1704 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | crew onsite | -90.0776 | 30.0016 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 5 | 1335095325 | Yes | ORLEANS | FAIR | 8 | 2020-07-15 10:38 | 2020-07-15 10:38 | 2020-07-15 10:46 | 40 | TFUS | 73548 | 39746487658 | 1704 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | crew onsite | -90.0776 | 30.0019 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 1 | 1335109166 | Yes | ORLEANS | FAIR | 66 | 2020-07-15 15:41 | 2020-07-15 15:41 | 2020-07-15 16:47 | 66 | TFUS | 59843 | 39527466661 | 2021 | ENOI | 1 | 1 | EARR | Equipment Failure - Arrestor | N | failed arrestor | -90.0853 | 29.9442 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-15 | DLIN | B | Council District B | Jay Banks | 70113 | 7
2020 | 161 | 1335121353 | Yes | ORLEANS | THDR | 157 | 2020-07-15 19:24 | 2020-07-15 21:27 | 2020-07-15 22:01 | 25277 | LFUS | 50679 | 3863946745 | 2016 | ENOI | 1 | 161 | LGHT | Lightning | N | refused | -90.1135 | 29.9468 | Lightning | Line Fuse | Lightning | 2020-07-15 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 7
2020 | 77 | 1335129524 | Yes | ORLEANS | THDR | 202 | 2020-07-15 19:24 | 2020-07-15 20:58 | 2020-07-15 22:46 | 15554 | LFUS | 50314 | 3870546896 | 2016 | ENOI | 1 | 77 | LGHT | Lightning | N | refused back in | -90.1112 | 29.951 | Lightning | Line Fuse | Lightning | 2020-07-15 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 7
2020 | 865 | 1335121704 | Yes | ORLEANS | THDR | 91 | 2020-07-15 19:30 | 2020-07-15 20:55 | 2020-07-15 21:01 | 78715 | DIS | 24727 | 3985148457 | 1703 | ENOI | 1 | 865 | EPRI | Equipment Failure - Primary Conductor | N | c phase jumper burnt on switch, crew repaired, customers back on | -90.0746 | 29.9933 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-07-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 7 | 1335122771 | Yes | ORLEANS | THDR | 186 | 2020-07-15 20:08 | 2020-07-15 21:48 | 2020-07-15 23:14 | 1302 | TFUS | 22515 | 39642494508 | 509 | ENOI | 1 | 7 | ESEC | Secondary/Service Conductor | N | put spacers in open wire secondary, refused transformer | -90.0808 | 30.0207 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 40 | 1335123505 | Yes | EAST ORLEANS | THDR | 123 | 2020-07-15 20:21 | 2020-07-15 22:13 | 2020-07-15 22:24 | 4920 | LFUS | 24325 | 4440550114 | 1601 | ENOI | 6 | 40 | LGHT | Lightning | N | refused | -97.0758 | 27.9066 | Lightning | Line Fuse | Lightning | 2020-07-15 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 9 | 1335130008 | Yes | ORLEANS | THDR | 33 | 2020-07-15 22:28 | 2020-07-15 22:32 | 2020-07-15 23:01 | 297 | TFUS | 76534 | 38968475979 | 911 | ENOI | 1 | 9 | LGHT | Lightning | N | refused back on | -90.1028 | 29.9701 | Lightning | Transformer Fuse | Lightning | 2020-07-15 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 5 | 1335134443 | Yes | ORLEANS | FAIR | 622 | 2020-07-15 23:01 | 2020-07-16 07:08 | 2020-07-16 09:23 | 3110 | XFMR | 58413 | 38654469250 | 2016 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.1128 | 29.9516 | Equipment Failure | Transformer | Equipment Failure | 2020-07-15 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 7
2020 | 37 | 1335131112 | Yes | EAST ORLEANS | THDR | 197 | 2020-07-15 23:09 | 2020-07-15 23:40 | 2020-07-16 02:26 | 7289 | LFUS | 25734 | 4314750328 | 2214 | ENOI | 6 | 37 | EPRI | Equipment Failure - Primary Conductor | N | bad cable, switched around, all customers on | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-15 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 7
2020 | 3 | 1335137034 | Yes | EAST ORLEANS | FAIR | 309 | 2020-07-16 04:25 | 2020-07-16 07:46 | 2020-07-16 09:34 | 927 | LFUS | 21876 | 4132848611 | 616 | ENOI | 6 | 3 | EARM | Equipment Failure - Crossarm | N | replace arm | -90.0277 | 29.9971 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-16 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 225 | 1335135942 | Yes | EAST ORLEANS | FAIR | 95 | 2020-07-16 04:26 | 2020-07-16 05:14 | 2020-07-16 06:01 | 21375 | SBKR | 616 | 4081348421 | 616 | ENOI | 6 | 225 | EARM | Equipment Failure - Crossarm | N | crossarm broken at lateral 21876 | -90.0278 | 29.9971 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-07-16 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 11 | 1335137902 | Yes | EAST ORLEANS | THDR | 471 | 2020-07-16 07:00 | 2020-07-16 11:47 | 2020-07-16 14:51 | 5181 | XFMR | 73826 | 41744474016 | 2346 | ENOI | 6 | 11 | ETRD | Equipment Failure - Transformer | N | crew on site | -90.015 | 29.9638 | Equipment Failure | Transformer | Equipment Failure | 2020-07-16 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 2 | 1335138082 | Yes | EAST ORLEANS | THDR | 388 | 2020-07-16 07:07 | 2020-07-16 07:07 | 2020-07-16 13:35 | 776 | XFMR | 72229 | 42030474459 | 2345 | ENOI | 6 | 2 | LGHT | Lightning | N | TRANSFORMER HANGING FROM POLE OIL ON GROUND CALLED CREW TO WORK | -90.006 | 29.9648 | Lightning | Transformer | Lightning | 2020-07-16 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 12 | 1335138392 | Yes | ORLEANS | FAIR | 66 | 2020-07-16 07:25 | 2020-07-16 07:25 | 2020-07-16 08:31 | 792 | TFUS | 56390 | 39718488072 | 1704 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | crew onsite | -90.0787 | 30.003 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-16 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 89 | 1335147358 | Yes | EAST ORLEANS | FAIR | 103 | 2020-07-16 10:11 | 2020-07-16 10:44 | 2020-07-16 11:54 | 9167 | LFUS | 27755 | 4044648582 | 1710 | ENOI | 6 | 89 | VINE | Vine Growing into Line | N | Cleared vines from transformer and pole in the rear Was only able to clear portion near the primary bushing Also had to refuse c phase lateral switch Will need follow up with vegetation Back in lights | -90.0557 | 29.9965 | Vegetation | Line Fuse | Vegetation | 2020-07-16 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 22 | 1335147576 | Yes | ORLEANS | FAIR | 64 | 2020-07-16 10:16 | 2020-07-16 10:34 | 2020-07-16 11:20 | 1408 | LFUS | 17788 | 3893448852 | 413 | ENOI | 1 | 22 | LGHT | Lightning | N | weather | -90.1032 | 30.0044 | Lightning | Line Fuse | Lightning | 2020-07-16 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 165 | 1335148591 | Yes | EAST ORLEANS | FAIR | 394 | 2020-07-16 10:37 | 2020-07-16 16:06 | 2020-07-16 17:11 | 65010 | LFUS | 27658 | 4060848734 | 1710 | ENOI | 6 | 165 | EPRI | Equipment Failure - Primary Conductor | N |  | -90.0504 | 30.0009 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-16 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 78 | 1335154829 | Yes | ORLEANS | THDR | 35 | 2020-07-16 12:21 | 2020-07-16 12:24 | 2020-07-16 12:56 | 2730 | LFUS | 33243 | 3832347263 | 2016 | ENOI | 1 | 78 | LGHT | Lightning | N | Weather took out lateral refused ok | -90.1232 | 29.9609 | Lightning | Line Fuse | Lightning | 2020-07-16 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 29 | 1335155325 | Yes | EAST ORLEANS | THDR | 138 | 2020-07-16 12:32 | 2020-07-16 12:49 | 2020-07-16 14:50 | 4002 | LFUS | 32768 | 4172347319 | 2346 | ENOI | 6 | 29 | ETRD | Equipment Failure - Transformer | N |  | -90.0157 | 29.9615 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-16 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 49 | 1335157708 | Yes | ORLEANS | THDR | 126 | 2020-07-16 13:07 | 2020-07-16 13:24 | 2020-07-16 15:13 | 6174 | LFUS | 17699 | 3888449056 | 413 | ENOI | 1 | 49 | EARM | Equipment Failure - Crossarm | N | broken cross arm crew replaced | -90.1049 | 30.0102 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-16 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 10 | 1335198269 | Yes | ORLEANS | FAIR | 250 | 2020-07-17 06:09 | 2020-07-17 10:32 | 2020-07-17 10:19 | 2500 | XFMR | 497053 | 38210471126 | B0527 | ENOI | 1 | 10 | ETRD | Equipment Failure - Transformer | N | replaced transformer | -90.1269 | 29.9569 | Equipment Failure | Transformer | Equipment Failure | 2020-07-17 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 27 | 1335201014 | Yes | EAST ORLEANS | FAIR | 124 | 2020-07-17 07:33 | 2020-07-17 09:12 | 2020-07-17 09:37 | 3348 | LFUS | 25430 | 4440350119 | 1205 | ENOI | 6 | 27 | EFSW | Equipment Failure - Fuse Switch | N | refused c phase chris bowers will draw up job to have switch gear changed out flashed up | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-17 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 65 | 1335201114 | Yes | EAST ORLEANS | FAIR | 270 | 2020-07-17 08:00 | 2020-07-17 08:58 | 2020-07-17 12:30 | 17550 | LFUS | 28080 | 4099047734 | 611 | ENOI | 6 | 65 | SCHD | Scheduled Interruption | N | crew on site contractors | -90.0386 | 29.9732 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 13 | 1335202677 | Yes | ORLEANS | FAIR | 47 | 2020-07-17 08:53 | 2020-07-17 09:03 | 2020-07-17 09:40 | 611 | TFUS | 59448 | 39256457455 | 1922 | ENOI | 1 | 13 | VLGL | Tree/Limb Growing Inside R.O.W. | N | tree growing into transformer fuse trimmed | -90.0944 | 29.919 | Vegetation | Transformer Fuse | Vegetation | 2020-07-17 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 69 | 1335206839 | Yes | EAST ORLEANS | FAIR | 109 | 2020-07-17 10:03 | 2020-07-17 11:16 | 2020-07-17 11:52 | 7521 | LFUS | 65763 | 4216449199 | 1607 | ENOI | 6 | 69 | SCHD | Scheduled Interruption | N |  | -90.001 | 30.0132 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-17 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 128 | 1335214743 | Yes | ORLEANS | FAIR | 22 | 2020-07-17 13:02 | 2020-07-17 13:21 | 2020-07-17 13:24 | 2816 | LFUS | 17547 | 3899748565 | 403 | ENOI | 1 | 128 | SCHD | Scheduled Interruption | N | crew on site installing trip saver | -90.1013 | 29.9967 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-17 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 13 | 1335220977 | Yes | EAST ORLEANS | FAIR | 114 | 2020-07-17 15:59 | 2020-07-17 16:03 | 2020-07-17 17:53 | 1482 | TFUS | 666352 | 4270349847 | 1602 | ENOI | 6 | 13 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | changed UG secondary block | -89.9838 | 30.0306 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-17 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 1 | 1335221389 | Yes | ORLEANS | FAIR | 292 | 2020-07-17 16:16 | 2020-07-17 16:16 | 2020-07-17 21:08 | 292 | SERV | SERVICE | 39763496785 | 509 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | repaired | -90.0769 | 30.0268 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-17 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 119 | 1335226560 | Yes | ORLEANS | FAIR | 44 | 2020-07-17 19:29 | 2020-07-17 19:47 | 2020-07-17 20:13 | 5236 | LFUS | 21028 | 4025947660 | 614 | ENOI | 1 | 119 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | taken out by balloons refused ok | -90.0618 | 29.9713 | Other | Line Fuse | Other | 2020-07-17 | DLIN | C | Council District C | Kristin Palmer | 70116 | 7
2020 | 2 | 1335229756 | Yes | ORLEANS | FAIR | 813 | 2020-07-17 20:38 | 2020-07-17 20:38 | 2020-07-18 10:11 | 1626 | XFMR | 57042 | 40204486133 | 1704 | ENOI | 1 | 2 | ETRD | Equipment Failure - Transformer | N | Bad 5000 KV transformer, crew will change | -90.0633 | 29.9975 | Equipment Failure | Transformer | Equipment Failure | 2020-07-17 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 55 | 1335244399 | Yes | EAST ORLEANS | FAIR | 122 | 2020-07-18 08:27 | 2020-07-18 08:34 | 2020-07-18 10:30 | 6710 | LFUS | 65763 | 4216449199 | 1607 | ENOI | 6 | 55 | EFLK | Equipment Failure - Fuse Link | N | refused a phase latral | -90.001 | 30.0132 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 1 | 1335248133 | Yes | EAST ORLEANS | FAIR | 168 | 2020-07-18 12:13 | 2020-07-18 12:13 | 2020-07-18 15:01 | 168 | TFUS | 56152 | 41488473406 | 2346 | ENOI | 6 | 1 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.0234 | 29.9622 | Vegetation | Transformer Fuse | Vegetation | 2020-07-18 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 1 | 1335253539 | Yes | ORLEANS | FAIR | 66 | 2020-07-18 16:04 | 2020-07-18 16:04 | 2020-07-18 17:10 | 66 | SERV | SERVICE | 38470469687 | B0525 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad connection at house | -90.1187 | 29.9528 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-18 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 372 | 1335259605 | Yes | ORLEANS | FAIR | 123 | 2020-07-18 19:01 | 2020-07-18 20:55 | 2020-07-18 21:04 | 45756 | DIS | 14064 | 3886748786 | 405 | ENOI | 1 | 372 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | brace broken at memphis and french | -90.1055 | 30.0028 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-07-18 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 131 | 1335258065 | Yes | ORLEANS | FAIR | 53 | 2020-07-18 19:01 | 2020-07-18 19:52 | 2020-07-18 19:54 | 6943 | SBKR | 405 | 3847149119 | 405 | ENOI | 1 | 131 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | serviceman located broken brace at memphis and french | -90.1179 | 30.012 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-07-18 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 4 | 1335279152 | Yes | ORLEANS | FAIR | 44 | 2020-07-19 14:28 | 2020-07-19 14:28 | 2020-07-19 15:12 | 176 | TFUS | 61314 | 39234467756 | 2021 | ENOI | 1 | 4 | AOTH | Animal - Other (Describe in Remarks Field) | N | taken out by non reportable bird refused ok | -90.0947 | 29.9473 | Animal | Transformer Fuse | Animal | 2020-07-19 | DLIN | B | Council District B | Jay Banks | 70125 | 7
2020 | 2 | 1335279529 | Yes | ORLEANS | FAIR | 33 | 2020-07-19 15:08 | 2020-07-19 15:28 | 2020-07-19 15:41 | 66 | TFUS | 57324 | 39666475724 | 907 | ENOI | 1 | 2 | EARM | Equipment Failure - Crossarm | N |  | -90.0807 | 29.9692 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-19 | DLIN | D | Council District D | Jared Brossett | 70119 | 7
2020 | 51 | 1335303386 | Yes | ORLEANS | FAIR | 254 | 2020-07-20 07:40 | 2020-07-20 11:23 | 2020-07-20 11:54 | 12954 | LFUS | 21661 | 4026948923 | 1704 | ENOI | 1 | 51 | SCHD | Scheduled Interruption | N | back on | -90.0612 | 30.006 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-20 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 5 | 1335346466 | Yes | ORLEANS | FAIR | 20 | 2020-07-21 07:20 | 2020-07-21 07:20 | 2020-07-21 07:40 | 100 | TFUS | 56553 | 40159488619 | 1704 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N |  | -90.0645 | 30.0045 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 7 | 1335346574 | Yes | ORLEANS | FAIR | 20 | 2020-07-21 07:20 | 2020-07-21 07:20 | 2020-07-21 07:40 | 140 | TFUS | 1178018 | 40157488848 | 1704 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N |  | -90.0646 | 30.0051 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 42 | 1335348056 | Yes | ORLEANS | HEAT | 340 | 2020-07-21 08:15 | 2020-07-21 08:15 | 2020-07-21 13:55 | 14280 | OPEN | 3935147669 | 3935147669 | 1705 | ENOI | 1 | 42 | SCHD | Scheduled Interruption | N | scheduled outage for line maintenance | -90.0906 | 29.9719 | Scheduled Interruption | Open | Scheduled Interruption | 2020-07-21 | DLIN | B | Council District B | Jay Banks | 70119 | 7
2020 | 6 | 1335350219 | Yes | ORLEANS | FAIR | 21 | 2020-07-21 09:00 | 2020-07-21 09:00 | 2020-07-21 09:21 | 126 | TFUS | 1522955 | 40075489074 | 1704 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N |  | -90.0673 | 30.0056 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 8 | 1335351616 | Yes | ORLEANS | FAIR | 211 | 2020-07-21 09:15 | 2020-07-21 09:15 | 2020-07-21 12:46 | 1688 | TFUS | 62082 | 39061471011 | 1553 | ENOI | 1 | 8 | VHCL | Vehicle | N | placed transformer back on bolts | -90.1 | 29.9564 | Public Damage | Transformer Fuse | Public Damage | 2020-07-21 | DLIN | B | Council District B | Jay Banks | 70125 | 7
2020 | 1 | 1335362696 | Yes | EAST ORLEANS | FAIR | 138 | 2020-07-21 11:29 | 2020-07-21 11:29 | 2020-07-21 13:47 | 138 | SERV | SERVICE | 43472508023 | 2217 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | changed connection in hand hole | -89.9591 | 30.0568 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 7
2020 | 5 | 1335410217 | Yes | ORLEANS | FAIR | 64 | 2020-07-22 04:22 | 2020-07-22 04:25 | 2020-07-22 05:26 | 320 | TFUS | 495740 | 38052469024 | 2014 | ENOI | 1 | 5 | EARR | Equipment Failure - Arrestor | N | cleared lightning arrestor; refused transformer | -90.1319 | 29.9513 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-22 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 11 | 1335411689 | Yes | ORLEANS | FAIR | 68 | 2020-07-22 06:42 | 2020-07-22 07:12 | 2020-07-22 07:50 | 748 | TFUS | 64410 | 38421470399 | 2016 | ENOI | 1 | 11 | ASQL | Animal - Squirrel | N | refused | -90.12 | 29.9548 | Animal | Transformer Fuse | Animal | 2020-07-22 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 30 | 1335412959 | Yes | ORLEANS | FAIR | 169 | 2020-07-22 07:56 | 2020-07-22 08:12 | 2020-07-22 10:46 | 5070 | LFUS | 27878 | 3958948953 | 1704 | ENOI | 1 | 30 | SCHD | Scheduled Interruption | N | back on | -90.0825 | 30.007 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-22 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 11 | 1335456495 | Yes | ORLEANS | FAIR | 322 | 2020-07-22 18:36 | 2020-07-22 19:01 | 2020-07-22 23:58 | 3542 | TFUS | 75814 | 40205476550 | 614 | ENOI | 1 | 11 | ESEC | Secondary/Service Conductor | N |  | -90.0636 | 29.9711 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-22 | DLIN | C | Council District C | Kristin Palmer | 70116 | 7
2020 | 15 | 1335457038 | Yes | ORLEANS | FAIR | 533 | 2020-07-22 18:43 | 2020-07-22 23:43 | 2020-07-23 03:36 | 7995 | XFMR | 1078532 | 39644463133 | 2132 | ENOI | 1 | 15 | ETRD | Equipment Failure - Transformer | N |  | -90.0818 | 29.9346 | Equipment Failure | Transformer | Equipment Failure | 2020-07-22 | DLIN | B | Council District B | Jay Banks | 70130 | 7
2020 | 22 | 1335464694 | Yes | ORLEANS | FAIR | 73 | 2020-07-23 03:39 | 2020-07-23 03:39 | 2020-07-23 04:52 | 1606 | TFUS | 71020 | 40262476064 | 614 | ENOI | 1 | 22 | EARM | Equipment Failure - Crossarm | N |  | -90.0617 | 29.9699 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-23 | DLIN | C | Council District C | Kristin Palmer | 70116 | 7
2020 | 1 | 1335465528 | Yes | EAST ORLEANS | FAIR | 203 | 2020-07-23 05:14 | 2020-07-23 05:14 | 2020-07-23 08:37 | 203 | TFUS | 73128 | 43247507693 | 2223 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | cleared vines from primary refuse latral and transformer need to get tree crews to clear right of way | -89.9665 | 30.056 | Vegetation | Transformer Fuse | Vegetation | 2020-07-23 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 7
2020 | 85 | 1335467924 | Yes | ORLEANS | FAIR | 257 | 2020-07-23 07:14 | 2020-07-23 08:09 | 2020-07-23 11:31 | 21845 | LFUS | 21657 | 4012548949 | 1704 | ENOI | 1 | 85 | SCHD | Scheduled Interruption | N | plan outage | -90.0658 | 30.0067 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 1 | 1335468336 | Yes | ORLEANS | FAIR | 209 | 2020-07-23 07:23 | 2020-07-23 07:23 | 2020-07-23 10:52 | 209 | SERV | SERVICE | 38725484919 | 408 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | ran new service line | -90.1099 | 29.9946 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-23 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 21 | 1335468765 | Yes | ORLEANS | FAIR | 309 | 2020-07-23 07:51 | 2020-07-23 11:52 | 2020-07-23 13:00 | 6489 | DIS | 13439 | 4025249119 | 509 | ENOI | 1 | 21 | SCHD | Scheduled Interruption | N | Scheduled Interruption Crew on Site Working | -90.0615 | 30.0113 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 13 | 1335469427 | Yes | ORLEANS | FAIR | 51 | 2020-07-23 08:00 | 2020-07-23 08:00 | 2020-07-23 08:51 | 663 | LFUS | 21660 | 4015048980 | 1704 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N | complete | -90.0648 | 30.0077 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 31 | 1335469141 | Yes | ORLEANS | FAIR | 76 | 2020-07-23 08:00 | 2020-07-23 08:00 | 2020-07-23 09:16 | 2356 | LFUS | 21670 | 3956148950 | 1704 | ENOI | 1 | 31 | SCHD | Scheduled Interruption | N |  | -90.0836 | 30.007 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 20 | 1335469388 | Yes | ORLEANS | FAIR | 76 | 2020-07-23 08:00 | 2020-07-23 08:00 | 2020-07-23 09:16 | 1520 | LFUS | 38344 | 4023348883 | 1704 | ENOI | 1 | 20 | SCHD | Scheduled Interruption | N | CREW | -90.0622 | 30.0049 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 10 | 1335469132 | Yes | ORLEANS | FAIR | 240 | 2020-07-23 08:00 | 2020-07-23 08:00 | 2020-07-23 12:00 | 2400 | TFUS | 1186205 | 39737488816 | 1704 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N |  | -90.0778 | 30.005 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 52 | 1335471493 | Yes | EAST ORLEANS | FAIR | 12 | 2020-07-23 08:56 | 2020-07-23 09:01 | 2020-07-23 09:08 | 624 | LFUS | 21610 | 4056948968 | 1702 | ENOI | 6 | 52 | EARM | Equipment Failure - Crossarm | N | crew to make repairs | -90.0515 | 30.0072 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 41 | 1335474478 | Yes | EAST ORLEANS | FAIR | 29 | 2020-07-23 10:01 | 2020-07-23 10:10 | 2020-07-23 10:30 | 1189 | LFUS | 17858 | 4047049301 | 506 | ENOI | 6 | 41 | SCHD | Scheduled Interruption | N |  | -90.0548 | 30.0163 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 12 | 1335475460 | Yes | ORLEANS | FAIR | 122 | 2020-07-23 10:25 | 2020-07-23 10:25 | 2020-07-23 12:27 | 1464 | TFUS | 517221 | 38337458934 | 1914 | ENOI | 1 | 12 | VINE | Vine Growing into Line | N |  | -90.1231 | 29.9233 | Vegetation | Transformer Fuse | Vegetation | 2020-07-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 1 | 1335498832 | Yes | ORLEANS | FAIR | 99 | 2020-07-23 18:22 | 2020-07-23 18:22 | 2020-07-23 20:01 | 99 | TFUS | 66552 | 39252466199 | 2021 | ENOI | 1 | 1 | UNKN | Inspected Unknown | N |  | -90.094 | 29.943 | Other | Transformer Fuse | Other | 2020-07-23 | DLIN | B | Council District B | Jay Banks | 70125 | 7
2020 | 1 | 1335534292 | Yes | EAST ORLEANS | FAIR | 103 | 2020-07-24 16:58 | 2020-07-24 16:58 | 2020-07-24 18:41 | 103 | SERV | SERVICE | 44901501647 | 1205 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N |  | -89.9143 | 30.0386 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-24 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 4 | 1335535582 | Yes | EAST ORLEANS | FAIR | 298 | 2020-07-24 17:29 | 2020-07-24 17:35 | 2020-07-24 22:27 | 1192 | XFMR | 1573810 | 43158506354 | 2223 | ENOI | 6 | 4 | ETRD | Equipment Failure - Transformer | N |  | -89.9693 | 30.0522 | Equipment Failure | Transformer | Equipment Failure | 2020-07-24 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 7
2020 | 1 | 1335570202 | Yes | ORLEANS | FAIR | 103 | 2020-07-25 10:11 | 2020-07-25 10:16 | 2020-07-25 11:54 | 103 | SERV | SERVICE | 38931488210 | 413 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | repaired damaged service cable | -90.1033 | 30.0038 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-25 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 548 | 1335605892 | Yes | EAST ORLEANS | FAIR | 65 | 2020-07-26 07:36 | 2020-07-26 08:56 | 2020-07-26 08:41 | 35620 | RCLR | 24641 | 4090648904 | 617 | ENOI | 6 | 548 | LGHT | Lightning | N | Inspected all of feeder behind recloser Did not find any signs of structual damage to our equipment Inspected line behind storage facility The trees were in the clear at the time Arms Poles and Shield all in working order | -90.0409 | 30.0054 | Lightning | Recloser | Lightning | 2020-07-26 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 30 | 1335607435 | Yes | EAST ORLEANS | THDR | 94 | 2020-07-26 09:31 | 2020-07-26 10:41 | 2020-07-26 11:05 | 2820 | LFUS | 21104 | 4114949035 | 617 | ENOI | 6 | 30 | VLFL | Tree On Line Outside R.O.W | N | removed tree branch off pirmary | -90.0334 | 30.0088 | Vegetation | Line Fuse | Vegetation | 2020-07-26 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 29 | 1335607595 | Yes | EAST ORLEANS | THDR | 59 | 2020-07-26 09:39 | 2020-07-26 09:39 | 2020-07-26 10:38 | 1711 | LFUS | 27643 | 41086490698 | 617 | ENOI | 6 | 29 | LGHT | Lightning | N | Refused A Phase Lateral then transformer Customer back in lights Bad weather was in the area no signs of damage | -90.0354 | 30.0097 | Lightning | Line Fuse | Lightning | 2020-07-26 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 450 | 1335609103 | Yes | EAST ORLEANS | THDR | 51 | 2020-07-26 11:21 | 2020-07-26 12:20 | 2020-07-26 12:12 | 22950 | SBKR | 1605 | 4350949755 | 1605 | ENOI | 6 | 450 | ESWC | Switching Cabinet | N | found flash in cubicle 418 sw. # 21838 | -89.9585 | 30.0279 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-07-26 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 16 | 1335634129 | Yes | ORLEANS | FAIR | 80 | 2020-07-27 08:00 | 2020-07-27 08:00 | 2020-07-27 09:20 | 1280 | TFUS | 515796 | 38293466559 | 2013 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1244 | 29.9443 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-27 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 42 | 1335634120 | Yes | ORLEANS | FAIR | 150 | 2020-07-27 08:00 | 2020-07-27 08:00 | 2020-07-27 10:30 | 6300 | LFUS | 21673 | 3979448784 | 1704 | ENOI | 1 | 42 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0759 | 30.0023 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-27 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 8 | 1335644918 | Yes | ORLEANS | THDR | 137 | 2020-07-27 11:09 | 2020-07-27 12:41 | 2020-07-27 13:26 | 1096 | LFUS | 33961 | 3892747491 | 911 | ENOI | 1 | 8 | LGHT | Lightning | N | b phase blown on lateral and c phase blown on two pot bank; refused and lights back on | -90.1041 | 29.9668 | Lightning | Line Fuse | Lightning | 2020-07-27 | DLIN | B | Council District B | Jay Banks | 70119 | 7
2020 | 113 | 1335655346 | Yes | ORLEANS | RAIN | 29 | 2020-07-27 14:17 | 2020-07-27 14:26 | 2020-07-27 14:46 | 3277 | LFUS | 42795 | 4013748676 | 1704 | ENOI | 1 | 113 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0652 | 29.9994 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-27 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 579 | 1335668016 | Yes | ORLEANS | FAIR | 57 | 2020-07-27 20:16 | 2020-07-27 20:53 | 2020-07-27 21:13 | 33003 | RCLR | 71181 | 4025148173 | 1709 | ENOI | 1 | 579 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons at nineteen hundred n derbigny | -90.0617 | 29.9854 | Other | Recloser | Other | 2020-07-27 | DLIN | D | Council District D | Jared Brossett | 70119 | 7
2020 | 450 | 1335683301 | Yes | EAST ORLEANS | FAIR | 95 | 2020-07-28 07:34 | 2020-07-28 09:11 | 2020-07-28 09:09 | 42750 | SBKR | 1605 | 4350949755 | 1605 | ENOI | 6 | 450 | ESWC | Switching Cabinet | N | primary burning in Cub 418; isolated cubicle and closed recloser rl0738 | -89.9585 | 30.0279 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-07-28 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 334 | 1335685111 | Yes | ORLEANS | FAIR | 380 | 2020-07-28 08:28 | 2020-07-28 13:25 | 2020-07-28 14:48 | 126920 | OPEN | 3946445994 | 3946445994 | 1923 | ENOI | 1 | 334 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0876 | 29.9258 | Scheduled Interruption | Open | Scheduled Interruption | 2020-07-28 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 123 | 1335685570 | Yes | ORLEANS | FAIR | 380 | 2020-07-28 08:28 | 2020-07-28 14:40 | 2020-07-28 14:48 | 46740 | OPEN | 3946445995 | 3946445995 | 1923 | ENOI | 1 | 123 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0876 | 29.9258 | Scheduled Interruption | Open | Scheduled Interruption | 2020-07-28 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 155 | 1335688677 | Yes | EAST ORLEANS | RAIN | 25 | 2020-07-28 10:11 | 2020-07-28 10:29 | 2020-07-28 10:36 | 3875 | LFUS | 27850 | 4092947726 | 622 | ENOI | 6 | 155 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0407 | 29.973 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-28 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 13 | 1335689073 | Yes | ORLEANS | RAIN | 145 | 2020-07-28 10:26 | 2020-07-28 10:26 | 2020-07-28 12:51 | 1885 | TFUS | 64681 | 39294458990 | 1923 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0931 | 29.9233 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-28 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 138 | 1335689147 | Yes | ORLEANS | RAIN | 28 | 2020-07-28 10:32 | 2020-07-28 10:54 | 2020-07-28 11:00 | 3864 | LFUS | 33996 | 3944946396 | 2132 | ENOI | 1 | 138 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.088 | 29.9367 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-28 | DLIN | B | Council District B | Jay Banks | 70113 | 7
2020 | 3 | 1335701846 | Yes | EAST ORLEANS | FAIR | 1242 | 2020-07-28 14:42 | 2020-07-28 14:42 | 2020-07-29 11:24 | 3726 | XFMR | 29188 | 40925488096 | 625 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | crew changed out pot | -90.0404 | 30.0027 | Equipment Failure | Transformer | Equipment Failure | 2020-07-28 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 27 | 1335706682 | Yes | ORLEANS | FAIR | 225 | 2020-07-28 15:39 | 2020-07-28 15:55 | 2020-07-28 19:24 | 6075 | LFUS | 17694 | 3886848710 | 405 | ENOI | 1 | 27 | EARM | Equipment Failure - Crossarm | N | changed broken crossarm | -90.1054 | 30.0008 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-28 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 16 | 1335710161 | Yes | ORLEANS | FAIR | 156 | 2020-07-28 16:25 | 2020-07-28 18:53 | 2020-07-28 19:01 | 2496 | LFUS | 17565 | 3883848713 | 405 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1063 | 30.0008 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-28 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 11 | 1335715008 | Yes | ORLEANS | FAIR | 371 | 2020-07-28 18:14 | 2020-07-28 20:52 | 2020-07-29 00:25 | 4081 | XFMR | 75848 | 38892483286 | 904 | ENOI | 1 | 11 | ETRD | Equipment Failure - Transformer | N | changed bad xfmr | -90.1047 | 29.9902 | Equipment Failure | Transformer | Equipment Failure | 2020-07-28 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 7
2020 | 66 | 1335716653 | Yes | ORLEANS | FAIR | 187 | 2020-07-28 19:28 | 2020-07-28 21:17 | 2020-07-28 22:35 | 12342 | LFUS | 27945 | 3920748012 | 904 | ENOI | 1 | 66 | VLFL | Tree On Line Outside R.O.W | N | tree burnt down phase picked up down phase | -90.0951 | 29.9812 | Vegetation | Line Fuse | Vegetation | 2020-07-28 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 7
2020 | 17 | 1335719274 | Yes | ORLEANS | FAIR | 153 | 2020-07-28 20:51 | 2020-07-28 21:34 | 2020-07-28 23:24 | 14076 | LFUS | 28054 | 3942246645 | 1554 | ENOI | 1 | 17 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons took out b phase of lateral | -90.0888 | 29.9436 | Other | Line Fuse | Other | 2020-07-28 | DLIN | B | Council District B | Jay Banks | 70113 | 7
2020 | 263 | 1335729111 | Yes | ORLEANS | FAIR | 256 | 2020-07-29 04:55 | 2020-07-29 08:23 | 2020-07-29 09:11 | 67328 | DIS | 24877 | 3834645861 | 1914 | ENOI | 1 | 263 | SCHD | Scheduled Interruption | N | switched out to do work to move open point in the feeder | -90.1229 | 29.9226 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-07-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 116 | 1335730996 | Yes | EAST ORLEANS | FAIR | 216 | 2020-07-29 07:14 | 2020-07-29 08:55 | 2020-07-29 10:50 | 25056 | LFUS | 32647 | 4123847544 | 611 | ENOI | 6 | 116 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0309 | 29.9678 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-29 | DLIN | D | Council District D | Jared Brossett | 70117 | 7
2020 | 91 | 1335731121 | Yes | ORLEANS | FAIR | 114 | 2020-07-29 07:27 | 2020-07-29 08:33 | 2020-07-29 09:21 | 10374 | LFUS | 21656 | 4011448874 | 1704 | ENOI | 1 | 91 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.066 | 30.0046 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 22 | 1335731668 | Yes | ORLEANS | FAIR | 77 | 2020-07-29 07:58 | 2020-07-29 07:58 | 2020-07-29 09:15 | 1694 | LFUS | 35042 | 3805846338 | 2013 | ENOI | 1 | 22 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1316 | 29.9357 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-07-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 8 | 1335732860 | Yes | ORLEANS | FAIR | 141 | 2020-07-29 08:10 | 2020-07-29 08:10 | 2020-07-29 10:31 | 1128 | TFUS | 65895 | 40068487519 | 1704 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0674 | 30.0015 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-29 | DLIN | D | Council District D | Jared Brossett | 70122 | 7
2020 | 66 | 1335733370 | Yes | EAST ORLEANS | FAIR | 120 | 2020-07-29 08:22 | 2020-07-29 10:08 | 2020-07-29 10:22 | 7920 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 66 | ASQL | Animal - Squirrel | N | refused C phase at two seven eight eight five | -89.959 | 30.0234 | Animal | Line Fuse | Animal | 2020-07-29 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 7
2020 | 100 | 1335734789 | Yes | ORLEANS | FAIR | 157 | 2020-07-29 09:11 | 2020-07-29 11:42 | 2020-07-29 11:48 | 15700 | DIS | 27664 | 3842445837 | 1914 | ENOI | 1 | 100 | SCHD | Scheduled Interruption | N | crew on site | -90.1205 | 29.9219 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-07-29 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 7
2020 | 1 | 1335735070 | Yes | ORLEANS | FAIR | 414 | 2020-07-29 09:24 | 2020-07-29 15:34 | 2020-07-29 16:18 | 414 | SERV | SERVICE | 38689495179 | 401 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | bad stinger cable leaving manhole in front of 321 jewel | -90.1107 | 30.0229 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-29 | DLIN | D | Council District D | Jared Brossett | 70124 | 7
2020 | 2 | 1335748949 | Yes | EAST ORLEANS | FAIR | 457 | 2020-07-29 15:02 | 2020-07-29 15:02 | 2020-07-29 22:40 | 914 | TFUS | 1062335 | 4446350242 | 1205 | ENOI | 6 | 2 | EMER | Emergency Switching | N |  | -89.9281 | 30.0408 | Other | Transformer Fuse | Emergency Switching | 2020-07-29 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 7
2020 | 9 | 1335778488 | Yes | ORLEANS | FAIR | 131 | 2020-07-30 06:20 | 2020-07-30 06:20 | 2020-07-30 08:31 | 1179 | TFUS | 478819 | 38242470171 | 2013 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N |  | -90.1257 | 29.9542 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-07-30 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 1 | 1335780090 | Yes | EAST ORLEANS | FAIR | 102 | 2020-07-30 07:51 | 2020-07-30 07:51 | 2020-07-30 09:33 | 102 | TFUS | 504234 | 4221649508 | 1607 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | REFUSED TRANSFORMER CUSTOMER BACK IN LIGHTS | -89.9996 | 30.0216 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-30 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 7
2020 | 5 | 1335784660 | Yes | EAST ORLEANS | FAIR | 245 | 2020-07-30 09:28 | 2020-07-30 10:11 | 2020-07-30 13:33 | 1225 | XFMR | 77100 | 43439508497 | 2217 | ENOI | 6 | 5 | ETRD | Equipment Failure - Transformer | N |  | -89.9601 | 30.058 | Equipment Failure | Transformer | Equipment Failure | 2020-07-30 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 7
2020 | 4 | 1335864072 | NO | ORLEANS | FAIR | 99 | 2020-07-30 18:03 | 2020-07-30 18:03 | 2020-07-30 19:42 | 396 | SUBN | 1541 | 3950946993 | 1541 | ENOI | 1 | 4 | BKRO | Breaker - Oil | N | Fault on 1515 cause master breaker to trip | -90.0858 | 29.9532 | Equipment Failure | Substation | Equipment Failure | 2020-07-30 | DSUB | B | Council District B | Jay Banks | 70113 | 7
2020 | 29 | 1335864135 | NO | ORLEANS | FAIR | 99 | 2020-07-30 18:03 | 2020-07-30 18:03 | 2020-07-30 19:42 | 2871 | SUBN | 1543 | 3950446996 | 1543 | ENOI | 1 | 29 | BKRO | Breaker - Oil | N | Fault on 1515 cause master breaker to trip | -90.086 | 29.9533 | Equipment Failure | Substation | Equipment Failure | 2020-07-30 | DSUB | B | Council District B | Jay Banks | 70113 | 7
2020 | 12 | 1335864154 | NO | ORLEANS | FAIR | 99 | 2020-07-30 18:03 | 2020-07-30 18:03 | 2020-07-30 19:42 | 1188 | SUBN | 1510 | 3951546986 | 1510 | ENOI | 1 | 12 | BKRO | Breaker - Oil | N | Fault on 1515 cause master breaker to trip | -90.0856 | 29.953 | Equipment Failure | Substation | Equipment Failure | 2020-07-30 | DSUB | B | Council District B | Jay Banks | 70113 | 7
2020 | 11 | 1335864286 | NO | ORLEANS | FAIR | 99 | 2020-07-30 18:03 | 2020-07-30 18:03 | 2020-07-30 19:42 | 1089 | SUBN | 1542 | 3950646995 | 1542 | ENOI | 1 | 11 | BKRO | Breaker - Oil | N | Fault on 1515 cause master breaker to trip | -90.0859 | 29.9533 | Equipment Failure | Substation | Equipment Failure | 2020-07-30 | DSUB | B | Council District B | Jay Banks | 70113 | 7
2020 | 5 | 1335835062 | Yes | ORLEANS CBD | FAIR | 230 | 2020-07-30 18:10 | 2020-07-30 18:19 | 2020-07-30 22:00 | 1150 | TFUS | 31598 | 39690469829 | 1551 | ENOI | 4 | 5 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | on feeder 1515 switched in 1551 to pick up | -90.0799 | 29.953 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-07-30 | DLIN | B | Council District B | Jay Banks | 70112 | 7
2020 | 1 | 1335840052 | Yes | ORLEANS | FAIR | 62 | 2020-07-30 19:40 | 2020-07-30 19:40 | 2020-07-30 20:42 | 62 | SERV | SERVICE | 38146470228 | B0527 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | Meter was open internally | -90.1289 | 29.9545 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-30 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 6 | 1335840415 | Yes | ORLEANS | FAIR | 256 | 2020-07-30 19:51 | 2020-07-30 22:40 | 2020-07-31 00:07 | 1536 | XFMR | 64925 | 40233479668 | 627 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | changed bad xfmr | -90.0624 | 29.9798 | Equipment Failure | Transformer | Equipment Failure | 2020-07-30 | DLIN | D | Council District D | Jared Brossett | 70119 | 7
2020 | 42 | 1335842364 | Yes | EAST ORLEANS | FAIR | 432 | 2020-07-30 21:49 | 2020-07-31 03:17 | 2020-07-31 05:01 | 18144 | LFUS | 16057-F | 4167149321 | 1001 | ENOI | 6 | 42 | EELB | Equipment Failure - Elbow | N |  | -90.0168 | 30.0167 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-30 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 49 | 1335842396 | Yes | EAST ORLEANS | FAIR | 433 | 2020-07-30 21:50 | 2020-07-31 03:05 | 2020-07-31 05:03 | 21217 | LFUS | 16059-F | 4166549161 | 1001 | ENOI | 6 | 49 | EELB | Equipment Failure - Elbow | N |  | -90.017 | 30.0124 | Equipment Failure | Line Fuse | Equipment Failure | 2020-07-30 | DLIN | D | Council District D | Jared Brossett | 70126 | 7
2020 | 1 | 1335870351 | Yes | ORLEANS | FAIR | 76 | 2020-07-31 14:18 | 2020-07-31 14:18 | 2020-07-31 15:35 | 76 | SERV | METER | 38717462927 | 1927 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | Crossed meters | -90.1112 | 29.9342 | Other | Service Conductor | Other | 2020-07-31 | DLIN | B | Council District B | Jay Banks | 70115 | 7
2020 | 67 | 1335893223 | Yes | EAST ORLEANS | FAIR | 103 | 2020-07-31 21:07 | 2020-07-31 21:41 | 2020-07-31 22:50 | 6901 | LFUS | 97550 | 4154247589 | 2325 | ENOI | 6 | 67 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons on line | -90.0214 | 29.9689 | Other | Line Fuse | Other | 2020-07-31 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 7
2020 | 1 | 1335899898 | Yes | ORLEANS | FAIR | 69 | 2020-07-31 22:39 | 2020-07-31 22:39 | 2020-07-31 23:48 | 69 | SERV | SERVICE | 38013469200 | B0526 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | changed meter | -90.133 | 29.9517 | Equipment Failure | Service Conductor | Equipment Failure | 2020-07-31 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 7
2020 | 1 | 1335917659 | Yes | EAST ORLEANS | FAIR | 144 | 2020-08-01 09:00 | 2020-08-01 09:00 | 2020-08-01 11:25 | 144 | SERV | SERVICE | 42134497897 | 2211 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Hot leg burned up in URD submersible vault spliced good voltage | -90.002 | 30.0292 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-01 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 24 | 1335919613 | Yes | ORLEANS | FAIR | 155 | 2020-08-01 09:05 | 2020-08-01 10:21 | 2020-08-01 11:40 | 3720 | LFUS | 33989 | 3991345919 | 2147 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | ontract crew had planned outage on lateral to work on it | -90.0732 | 29.9237 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-01 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 7 | 1335933379 | Yes | ORLEANS | FAIR | 69 | 2020-08-01 19:03 | 2020-08-01 19:03 | 2020-08-01 20:12 | 483 | TFUS | 56303 | 39703477914 | 615 | ENOI | 1 | 7 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons took out both wing transformers refused ok | -90.0794 | 29.9752 | Other | Transformer Fuse | Other | 2020-08-01 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 46 | 1335947329 | Yes | ORLEANS | FAIR | 117 | 2020-08-02 08:00 | 2020-08-02 09:23 | 2020-08-02 09:57 | 5382 | LFUS | F05705 | 39486458513 | 2147 | ENOI | 1 | 46 | SCHD | Scheduled Interruption | N | back on | -90.087 | 29.9218 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-02 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 88 | 1335950626 | Yes | EAST ORLEANS | FAIR | 65 | 2020-08-02 11:00 | 2020-08-02 11:32 | 2020-08-02 12:05 | 5720 | LFUS | 17966 | 4172149327 | 1001 | ENOI | 6 | 88 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons in phases B and C of lateralcleared refused ok | -90.015 | 30.0169 | Other | Line Fuse | Other | 2020-08-02 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 195 | 1335955442 | Yes | ORLEANS | FAIR | 301 | 2020-08-02 13:59 | 2020-08-02 17:59 | 2020-08-02 19:00 | 58695 | RCLR | 82583 | 3862847085 | 2027 | ENOI | 1 | 195 | EPRI | Equipment Failure - Primary Conductor | N | picked up down wire | -90.1135 | 29.956 | Equipment Failure | Recloser | Equipment Failure | 2020-08-02 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 66 | 1335955410 | Yes | ORLEANS | THDR | 267 | 2020-08-02 14:00 | 2020-08-02 18:04 | 2020-08-02 18:27 | 17622 | LFUS | 33047 | 3876947824 | 2026 | ENOI | 1 | 66 | ETRD | Equipment Failure - Transformer | N | Bad transformer in front of fourty six eighteen palmyra | -90.109 | 29.9763 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-02 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 90 | 1335955446 | Yes | ORLEANS | FAIR | 614 | 2020-08-02 14:01 | 2020-08-03 00:08 | 2020-08-03 00:15 | 55260 | LFUS | 34120 | 38024468308 | 2014 | ENOI | 1 | 90 | EPOL | Equipment Failure - Pole | N | replaced broken pole | -90.1326 | 29.9492 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-02 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 55 | 1335955604 | Yes | ORLEANS | THDR | 196 | 2020-08-02 14:02 | 2020-08-02 17:21 | 2020-08-02 17:18 | 10780 | LFUS | 36623 | 3837045664 | 1912 | ENOI | 1 | 55 | VLGL | Tree/Limb Growing Inside R.O.W. | N | trees need to be trimmed away from lateral | -90.122 | 29.9171 | Vegetation | Line Fuse | Vegetation | 2020-08-02 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 8
2020 | 343 | 1336044086 | Yes | ORLEANS | THDR | 133 | 2020-08-02 14:07 | 2020-08-04 09:00 | 2020-08-02 16:20 | 45619 | DIS | 24403 | 3964845844 | 2147 | ENOI | 1 | 343 | LGHT | Lightning | N | created ticket for outage correction on 8/2/20 | -90.0819 | 29.9217 | Lightning | Disconnect Switch | Lightning | 2020-08-02 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 2444 | 1335956323 | Yes | ORLEANS | THDR | 117 | 2020-08-02 14:07 | 2020-08-02 16:15 | 2020-08-02 16:04 | 285948 | SBKR | 2147 | 4013146121 | 2147 | ENOI | 1 | 2444 | LGHT | Lightning | N | picked wire up and breaker back in | -90.0665 | 29.9291 | Lightning | Substation Breaker | Lightning | 2020-08-02 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 4 | 1335958601 | Yes | ORLEANS | THDR | 242 | 2020-08-02 14:54 | 2020-08-02 15:13 | 2020-08-02 18:56 | 968 | TFUS | 1630794 | 3987948654 | 1703 | ENOI | 1 | 4 | VINE | Vine Growing into Line | N | Vines took out transformer refused ok lateral was never out | -90.0736 | 29.9987 | Vegetation | Transformer Fuse | Vegetation | 2020-08-02 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 2 | 1335961489 | Yes | ORLEANS | THDR | 172 | 2020-08-02 15:46 | 2020-08-02 16:16 | 2020-08-02 18:38 | 344 | TFUS | 77954 | 38744459960 | 1921 | ENOI | 1 | 2 | VINE | Vine Growing into Line | N | refused transformer | -90.1103 | 29.9262 | Vegetation | Transformer Fuse | Vegetation | 2020-08-02 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 9 | 1335963138 | Yes | ORLEANS | FAIR | 327 | 2020-08-02 16:33 | 2020-08-02 21:22 | 2020-08-02 22:00 | 2943 | TFUS | 64012 | 39168458418 | 1923 | ENOI | 1 | 9 | VLFL | Tree On Line Outside R.O.W | N | remove tree limb refused | -90.0969 | 29.9217 | Vegetation | Transformer Fuse | Vegetation | 2020-08-02 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 7 | 1335966498 | Yes | ORLEANS | FAIR | 288 | 2020-08-02 17:41 | 2020-08-02 19:37 | 2020-08-02 22:30 | 2016 | TFUS | 548535 | 37969465758 | B0527 | ENOI | 1 | 7 | LGHT | Lightning | N | taken out by weather refused ok | -90.1347 | 29.9422 | Lightning | Transformer Fuse | Lightning | 2020-08-02 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 16 | 1335969168 | Yes | ORLEANS | FAIR | 114 | 2020-08-02 19:07 | 2020-08-02 19:07 | 2020-08-02 21:01 | 1824 | XFMR | 479218 | 38802478337 | 2026 | ENOI | 1 | 16 | ETRD | Equipment Failure - Transformer | N | bad transformer | -90.1078 | 29.9766 | Equipment Failure | Transformer | Equipment Failure | 2020-08-02 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 1 | 1335969265 | Yes | ORLEANS | FAIR | 251 | 2020-08-02 19:18 | 2020-08-02 19:18 | 2020-08-02 23:29 | 251 | SERV | SERVICE | 39565488818 | 1704 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed connections in man hole | -90.0833 | 30.005 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-02 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 132 | 1335970776 | Yes | EAST ORLEANS | FAIR | 149 | 2020-08-02 20:27 | 2020-08-02 21:47 | 2020-08-02 22:56 | 19668 | LFUS | 27886 | 4082247647 | 622 | ENOI | 6 | 132 | LGHT | Lightning | N | found c phase blown on sw three seven one two one refused found main lateral two seven eight eight six also blown refused verified all customers lights behind main lateral back on | -90.044 | 29.9708 | Lightning | Line Fuse | Lightning | 2020-08-02 | DLIN | C | Council District C | Kristin Palmer | 70117 | 8
2020 | 15 | 1335974219 | Yes | ORLEANS | FAIR | 288 | 2020-08-03 00:10 | 2020-08-03 00:10 | 2020-08-03 04:58 | 4320 | TFUS | 481540 | 38000468039 | 2014 | ENOI | 1 | 15 | EPOL | Equipment Failure - Pole | N | replacing broken pole | -90.1334 | 29.9485 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 41 | 1335974961 | Yes | ORLEANS | FAIR | 52 | 2020-08-03 01:38 | 2020-08-03 01:38 | 2020-08-03 02:30 | 2132 | TFUS | 652089 | 3927147812 | 904 | ENOI | 1 | 41 | EARM | Equipment Failure - Crossarm | N | Crossarm at the end of line took out lateral refused ok arm in the clear | -90.0931 | 29.9757 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 29 | 1335978997 | Yes | ORLEANS | FAIR | 292 | 2020-08-03 07:58 | 2020-08-03 10:46 | 2020-08-03 12:50 | 8468 | LFUS | 38498 | 38382466786 | 2013 | ENOI | 1 | 29 | SCHD | Scheduled Interruption | N | contract crew on site | -90.1216 | 29.9448 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 8 | 1335980410 | Yes | ORLEANS | FAIR | 264 | 2020-08-03 08:56 | 2020-08-03 08:56 | 2020-08-03 13:20 | 2112 | TFUS | 50183 | 40183490619 | 512 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N |  | -90.0637 | 30.0099 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-03 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 58 | 1335987630 | Yes | EAST ORLEANS | FAIR | 43 | 2020-08-03 12:39 | 2020-08-03 12:57 | 2020-08-03 13:22 | 2494 | LFUS | 21126 | 4120947834 | 621 | ENOI | 6 | 58 | SCHD | Scheduled Interruption | N |  | -90.0317 | 29.9757 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-03 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 16 | 1335987809 | Yes | EAST ORLEANS | FAIR | 36 | 2020-08-03 12:44 | 2020-08-03 12:44 | 2020-08-03 13:20 | 576 | TFUS | 1453099 | 4117847795 | 616 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N |  | -90.0327 | 29.9746 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-03 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 4 | 1335988418 | Yes | ORLEANS | FAIR | 150 | 2020-08-03 13:13 | 2020-08-03 15:26 | 2020-08-03 15:43 | 600 | XFMR | 56797 | 38652475805 | 2026 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N |  | -90.1127 | 29.9696 | Equipment Failure | Transformer | Equipment Failure | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 1 | 1336003161 | Yes | ORLEANS | FAIR | 282 | 2020-08-03 17:29 | 2020-08-03 19:02 | 2020-08-03 22:11 | 282 | SERV | METER | 39403477144 | 1513 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter opened remotely amoc closed changed out meter with new AMI meter see mtr change | -90.0891 | 29.973 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 170 | 1336005771 | Yes | ORLEANS | FAIR | 71 | 2020-08-03 19:13 | 2020-08-03 20:13 | 2020-08-03 20:24 | 12070 | LFUS | F05701 | 3822546662 | 2014 | ENOI | 1 | 170 | EFLK | Equipment Failure - Fuse Link | N | refused b phase on lateral | -90.1266 | 29.9446 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 1 | 1336007009 | Yes | ORLEANS | FAIR | 71 | 2020-08-03 20:22 | 2020-08-03 20:22 | 2020-08-03 21:33 | 71 | SERV | METER | 38029462860 | 2013 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter was opened remotely turn on was completed today but meter still open | -90.1327 | 29.9343 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 1 | 1336008845 | Yes | ORLEANS | FAIR | 85 | 2020-08-03 21:37 | 2020-08-03 21:37 | 2020-08-03 23:02 | 85 | SERV | METER | 39170480195 | 904 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter open remotely amoc closed changed out meter with new AMI meter see mtr change | -90.0963 | 29.9814 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-03 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 46 | 1336012500 | Yes | ORLEANS | FAIR | 65 | 2020-08-04 00:15 | 2020-08-04 00:46 | 2020-08-04 01:20 | 2990 | LFUS | 33130 | 3972746165 | 2135 | ENOI | 1 | 46 | EFLK | Equipment Failure - Fuse Link | N | refused b phase on lateral | -90.0791 | 29.9306 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-04 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 14 | 1336019569 | Yes | ORLEANS | FAIR | 230 | 2020-08-04 04:44 | 2020-08-04 07:55 | 2020-08-04 08:35 | 3121 | SBKR | 1510 | 3951546986 | 1510 | ENOI | 1 | 14 | VHCL | Vehicle | N | Vehicle struck down guy fuse sw. # 33133 & 26018 flashed over | -90.0856 | 29.953 | Public Damage | Substation Breaker | Public Damage | 2020-08-04 | DLIN | B | Council District B | Jay Banks | 70113 | 8
2020 | 1 | 1336019577 | Yes | EAST ORLEANS | FAIR | 435 | 2020-08-04 04:45 | 2020-08-04 04:45 | 2020-08-04 12:00 | 435 | SERV | SERVICE | 41773495486 | 1610 | ENOI | 6 | 1 | SECF | Secondary cable failure | N |  | -90.0133 | 30.0228 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-04 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 3 | 1336020803 | Yes | ORLEANS | FAIR | 150 | 2020-08-04 06:20 | 2020-08-04 06:57 | 2020-08-04 08:50 | 450 | TFUS | 1004935 | 39743461470 | 2135 | ENOI | 1 | 3 | EARR | Equipment Failure - Arrestor | N | arrestor on xfmr failed catastrophically cleared areestor refused xfmr | -90.0787 | 29.93 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-04 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 9 | 1336025659 | Yes | EAST ORLEANS | FAIR | 306 | 2020-08-04 08:52 | 2020-08-04 08:56 | 2020-08-04 13:58 | 2754 | TFUS | 73291 | 41908474631 | 2345 | ENOI | 6 | 9 | VHCL | Vehicle | N | car hit pole | -90.0097 | 29.9654 | Public Damage | Transformer Fuse | Public Damage | 2020-08-04 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 8
2020 | 14 | 1336041799 | Yes | ORLEANS | FAIR | 95 | 2020-08-04 14:10 | 2020-08-04 14:10 | 2020-08-04 15:45 | 1330 | XFMR | 63209 | 38849467501 | 1916 | ENOI | 1 | 14 | ETRD | Equipment Failure - Transformer | N |  | -90.1067 | 29.9468 | Equipment Failure | Transformer | Equipment Failure | 2020-08-04 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 1 | 1336042872 | Yes | EAST ORLEANS | FAIR | 45 | 2020-08-04 14:46 | 2020-08-04 14:46 | 2020-08-04 15:32 | 45 | SERV | SERVICE | 40978489487 | 617 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Hot leg burned off at pole reconnected good volatge | -90.0386 | 30.0065 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-04 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 20 | 1336043897 | Yes | EAST ORLEANS | FAIR | 265 | 2020-08-04 15:29 | 2020-08-04 19:22 | 2020-08-04 19:54 | 5300 | XFMR | 74451 | 42625504166 | 2215 | ENOI | 6 | 20 | ETRD | Equipment Failure - Transformer | N | change out xformer | -89.986 | 30.0465 | Equipment Failure | Transformer | Equipment Failure | 2020-08-04 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 8
2020 | 97 | 1336044165 | Yes | ORLEANS | FAIR | 48 | 2020-08-04 15:37 | 2020-08-04 16:08 | 2020-08-04 16:25 | 4656 | LFUS | 49262 | 3960449441 | 509 | ENOI | 1 | 97 | EFSW | Equipment Failure - Fuse Switch | N | c phase lateral switch was burning changed out lateral switch | -90.0821 | 30.0203 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-04 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 1 | 1336048073 | Yes | ORLEANS | FAIR | 181 | 2020-08-04 16:27 | 2020-08-04 16:27 | 2020-08-04 19:28 | 181 | SERV | SERVICE | 39311495818 | 404 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | stinger leg pulled out mold spliced out and put back in mold cust ac turned on | -90.0913 | 30.0246 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-04 | DLIN | D | Council District D | Jared Brossett | 70124 | 8
2020 | 118 | 1336082049 | Yes | ORLEANS | FAIR | 156 | 2020-08-05 08:08 | 2020-08-05 10:38 | 2020-08-05 10:44 | 18408 | OPEN | 3803846364 | 3803846364 | 2013 | ENOI | 1 | 118 | SCHD | Scheduled Interruption | N | contract crew on site | -90.1325 | 29.9364 | Scheduled Interruption | Open | Scheduled Interruption | 2020-08-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 11 | 1336080399 | Yes | EAST ORLEANS | FAIR | 97 | 2020-08-05 08:53 | 2020-08-05 08:53 | 2020-08-05 10:31 | 1067 | TFUS | 617924 | 41079478393 | 611 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N |  | -90.0359 | 29.9761 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-05 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 65 | 1336163432 | Yes | ORLEANS | FAIR | 56 | 2020-08-06 07:11 | 2020-08-06 07:45 | 2020-08-06 08:07 | 3640 | LFUS | 37780 | 3990648264 | 1709 | ENOI | 1 | 65 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0728 | 29.9879 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-06 | DLIN | D | Council District D | Jared Brossett | 70119 | 8
2020 | 11 | 1336164320 | Yes | ORLEANS | FAIR | 198 | 2020-08-06 07:43 | 2020-08-06 07:43 | 2020-08-06 11:01 | 2178 | TFUS | 56189 | 40199476023 | 614 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | opened for safety | -90.0639 | 29.9698 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-06 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 7 | 1336164936 | Yes | ORLEANS | FAIR | 144 | 2020-08-06 07:51 | 2020-08-06 07:51 | 2020-08-06 10:15 | 1008 | TFUS | 528672 | 38101464286 | 2013 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Crew on Site Working on Transformer Allen Slamans 228-731-5949 | -90.1305 | 29.9382 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-06 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 1 | 1336175823 | Yes | ORLEANS | FAIR | 61 | 2020-08-06 09:55 | 2020-08-06 09:55 | 2020-08-06 10:56 | 61 | TFUS | 1053406 | 38085460966 | 2013 | ENOI | 1 | 1 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1311 | 29.929 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-06 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 10 | 1336179858 | Yes | ORLEANS | FAIR | 145 | 2020-08-06 11:00 | 2020-08-06 11:00 | 2020-08-06 13:25 | 1450 | TFUS | 549768 | 38103461220 | 2013 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1306 | 29.9298 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-06 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 1 | 1336188624 | Yes | ORLEANS | FAIR | 293 | 2020-08-06 15:08 | 2020-08-06 15:08 | 2020-08-06 20:01 | 293 | TFUS | 29360 | 40012473665 | 614 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N |  | -90.0698 | 29.9634 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-06 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 39 | 1336221333 | Yes | ORLEANS | FAIR | 77 | 2020-08-07 07:44 | 2020-08-07 08:37 | 2020-08-07 09:01 | 3003 | LFUS | 21657 | 4012548949 | 1704 | ENOI | 1 | 39 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0658 | 30.0067 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-07 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 11 | 1336222526 | Yes | ORLEANS | FAIR | 115 | 2020-08-07 08:00 | 2020-08-07 08:00 | 2020-08-07 09:55 | 1265 | TFUS | 504710 | 38117464270 | 2013 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1299 | 29.9382 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-07 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 12 | 1336223210 | Yes | ORLEANS | FAIR | 342 | 2020-08-07 08:23 | 2020-08-07 08:23 | 2020-08-07 14:06 | 4104 | TFUS | 550093 | 38054460509 | 2013 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1321 | 29.9278 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-07 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 13 | 1336228526 | Yes | ORLEANS | FAIR | 211 | 2020-08-07 09:55 | 2020-08-07 09:55 | 2020-08-07 13:26 | 2743 | TFUS | 70654 | 40296476316 | 614 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0605 | 29.9707 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-07 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 10 | 1336234145 | Yes | ORLEANS | FAIR | 111 | 2020-08-07 12:00 | 2020-08-07 12:56 | 2020-08-07 13:51 | 1110 | LFUS | 27744 | 3810946395 | 2013 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1302 | 29.9371 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-07 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 11 | 1336238222 | Yes | ORLEANS | FAIR | 96 | 2020-08-07 14:24 | 2020-08-07 14:24 | 2020-08-07 16:01 | 1056 | TFUS | 58740 | 40324476221 | 614 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0598 | 29.9704 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-07 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 400 | 1336249745 | Yes | ORLEANS | FAIR | 73 | 2020-08-07 21:03 | 2020-08-07 22:14 | 2020-08-07 22:16 | 29200 | RCLR | 23490 | 3879348106 | 904 | ENOI | 1 | 400 | ECNS | Equipment Failure - Connector Sleeve | N | @ location lost B phase serviceman can isolate jumper repair safely and restore power | -90.1089 | 29.9831 | Equipment Failure | Recloser | Equipment Failure | 2020-08-07 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 27 | 1336257523 | Yes | ORLEANS | FAIR | 105 | 2020-08-08 07:15 | 2020-08-08 08:10 | 2020-08-08 09:00 | 2835 | LFUS | 33120 | 3842745641 | 1917 | ENOI | 1 | 27 | AOTH | Animal - Other (Describe in Remarks Field) | N | crow got across took out B/C laterial and B/C on tranformer refuse all back in. 8/8/20 | -90.1203 | 29.9164 | Animal | Line Fuse | Animal | 2020-08-08 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 8
2020 | 15 | 1336257898 | Yes | ORLEANS | FAIR | 278 | 2020-08-08 07:57 | 2020-08-08 07:57 | 2020-08-08 12:36 | 4170 | TFUS | 58661 | 40289476194 | 614 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.061 | 29.9704 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-08 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 17 | 1336259357 | Yes | ORLEANS | FAIR | 165 | 2020-08-08 09:05 | 2020-08-08 09:05 | 2020-08-08 11:50 | 2805 | TFUS | 548570 | 38021460622 | 2013 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1329 | 29.928 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 13 | 1336260913 | Yes | EAST ORLEANS | FAIR | 332 | 2020-08-08 10:38 | 2020-08-08 13:59 | 2020-08-08 16:10 | 4316 | TFUS | 1315333 | 43959513436 | 2217 | ENOI | 6 | 13 | ESEC | Secondary/Service Conductor | N | pull in new main amnd splice out primary cable | -89.9437 | 30.0714 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-08 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 8
2020 | 22 | 1336264412 | Yes | ORLEANS | FAIR | 172 | 2020-08-08 13:23 | 2020-08-08 14:23 | 2020-08-08 16:15 | 3784 | TFUS | 709025 | 38397469063 | 2015 | ENOI | 1 | 22 | VINE | Vine Growing into Line | N | vine got across the transformer. refuse back in 8/8/20 | -90.121 | 29.9512 | Vegetation | Transformer Fuse | Vegetation | 2020-08-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 133 | 1336264741 | Yes | ORLEANS | FAIR | 256 | 2020-08-08 13:34 | 2020-08-08 17:39 | 2020-08-08 17:50 | 34048 | LFUS | LFUS | 00000000000 | 2027 | ENOI | 1 | 133 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | radio tower from burned down building came down and fell across the primary causing it to blow the lateral fuse and burned wire down. Cut tower down and picked up wire |  |  | Other | Line Fuse | Other | 2020-08-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 8 | 1336291430 | Yes | ORLEANS | FAIR | 151 | 2020-08-09 08:14 | 2020-08-09 08:14 | 2020-08-09 10:45 | 1208 | TFUS | 65009 | 40282476979 | 614 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0611 | 29.9724 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-09 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 12 | 1336300440 | Yes | ORLEANS | FAIR | 163 | 2020-08-09 14:27 | 2020-08-09 14:30 | 2020-08-09 17:10 | 1956 | TFUS | 55737 | 40223487314 | 1704 | ENOI | 1 | 12 | VOHL | Overhanging Limb | N | refused tranformer and tested tranformer all good. 8/9/20 | -90.0627 | 30.0007 | Vegetation | Transformer Fuse | Vegetation | 2020-08-09 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 7 | 1336320377 | Yes | ORLEANS | THDR | 79 | 2020-08-09 21:16 | 2020-08-09 21:47 | 2020-08-09 22:35 | 553 | LFUS | 37536 | 39339465415 | 1915 | ENOI | 1 | 7 | EFLK | Equipment Failure - Fuse Link | N | single phase lateral switch blew, looks like lighting might have tagged line refused ok | -90.0913 | 29.9409 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-09 | DLIN | B | Council District B | Jay Banks | 70113 | 8
2020 | 84 | 1336321532 | Yes | EAST ORLEANS | FAIR | 104 | 2020-08-09 22:47 | 2020-08-10 00:05 | 2020-08-10 00:31 | 8736 | LFUS | 27669 | 4245950386 | 2215 | ENOI | 6 | 84 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Cleared balloons off line and refused A phase | -89.9913 | 30.0458 | Other | Line Fuse | Other | 2020-08-09 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 8
2020 | 13 | 1336329456 | Yes | ORLEANS | FAIR | 182 | 2020-08-10 08:42 | 2020-08-10 08:42 | 2020-08-10 11:44 | 2366 | TFUS | 1060986 | 40313475917 | 614 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N | completed | -90.0601 | 29.9693 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-10 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 9 | 1336329446 | Yes | ORLEANS | FAIR | 183 | 2020-08-10 08:42 | 2020-08-10 08:42 | 2020-08-10 11:45 | 1647 | TFUS | 58471 | 40291475891 | 614 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | work completed | -90.0609 | 29.9693 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-10 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 112 | 1336329411 | Yes | ORLEANS | FAIR | 253 | 2020-08-10 08:42 | 2020-08-10 08:42 | 2020-08-10 12:56 | 28336 | LFUS | 33186 | 3975145935 | 2147 | ENOI | 1 | 112 | SCHD | Scheduled Interruption | N |  | -90.0786 | 29.924 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-10 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 15 | 1336343249 | Yes | ORLEANS | FAIR | 117 | 2020-08-10 13:43 | 2020-08-10 13:43 | 2020-08-10 15:40 | 1755 | TFUS | 58661 | 40289476194 | 614 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | work completed | -90.061 | 29.9704 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-10 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 5 | 1336352672 | Yes | ORLEANS | FAIR | 104 | 2020-08-10 18:02 | 2020-08-10 18:02 | 2020-08-10 19:46 | 520 | TFUS | 1310372 | 37987457869 | B0526 | ENOI | 1 | 5 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | ballon on line | -90.1342 | 29.9205 | Other | Transformer Fuse | Other | 2020-08-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 4 | 1336363213 | Yes | EAST ORLEANS | FAIR | 198 | 2020-08-11 06:33 | 2020-08-11 06:33 | 2020-08-11 09:51 | 792 | TFUS | 1084113 | 41343478509 | 621 | ENOI | 6 | 4 | EARM | Equipment Failure - Crossarm | N | Crew is working on broken arm | -90.0275 | 29.9762 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-11 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 15 | 1336364680 | Yes | ORLEANS | FAIR | 180 | 2020-08-11 07:45 | 2020-08-11 07:45 | 2020-08-11 10:45 | 2700 | TFUS | 519248 | 38234466236 | 2014 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N |  | -90.1263 | 29.9436 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 1 | 1336364727 | Yes | EAST ORLEANS | FAIR | 166 | 2020-08-11 07:49 | 2020-08-11 07:49 | 2020-08-11 10:35 | 166 | TFUS | 1171242 | 4140347829 | 621 | ENOI | 6 | 1 | EARM | Equipment Failure - Crossarm | N | change out arm | -90.0252 | 29.9756 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-11 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 4 | 1336364857 | Yes | ORLEANS | FAIR | 145 | 2020-08-11 07:51 | 2020-08-11 07:51 | 2020-08-11 10:16 | 580 | TFUS | 1004972 | 39815466243 | 2137 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N |  | -90.0761 | 29.943 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-11 | DLIN | B | Council District B | Jay Banks | 70113 | 8
2020 | 4 | 1336366982 | Yes | ORLEANS | FAIR | 89 | 2020-08-11 08:56 | 2020-08-11 08:56 | 2020-08-11 10:25 | 356 | TFUS | 76268 | 40270477167 | 614 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N |  | -90.0615 | 29.973 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-11 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 7 | 1336369997 | Yes | EAST ORLEANS | FAIR | 39 | 2020-08-11 09:51 | 2020-08-11 09:51 | 2020-08-11 10:30 | 273 | LFUS | 27757 | 4126947853 | 621 | ENOI | 6 | 7 | EMER | Emergency Switching | N |  | -90.0297 | 29.9764 | Other | Line Fuse | Emergency Switching | 2020-08-11 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 5 | 1336383881 | Yes | ORLEANS | FAIR | 68 | 2020-08-11 14:07 | 2020-08-11 14:07 | 2020-08-11 15:15 | 340 | TFUS | 58911 | 40181477094 | 614 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N |  | -90.0643 | 29.9728 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-11 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 53 | 1336387428 | Yes | ORLEANS | THDR | 95 | 2020-08-11 14:26 | 2020-08-11 14:39 | 2020-08-11 16:01 | 5035 | LFUS | 27637 | 3917746081 | 1924 | ENOI | 1 | 53 | LGHT | Lightning | N |  | -90.0968 | 29.9283 | Lightning | Line Fuse | Lightning | 2020-08-11 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 33 | 1336387882 | Yes | ORLEANS | THDR | 275 | 2020-08-11 14:45 | 2020-08-11 18:06 | 2020-08-11 19:21 | 9075 | LFUS | 27762 | 38801470366 | 2027 | ENOI | 1 | 33 | EARM | Equipment Failure - Crossarm | N | x-arm braces in rear repaired | -90.1081 | 29.9547 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-11 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 66 | 1336390299 | Yes | ORLEANS | THDR | 94 | 2020-08-11 14:46 | 2020-08-11 15:16 | 2020-08-11 16:20 | 6204 | LFUS | 21998 | 3886346861 | 2027 | ENOI | 1 | 66 | LGHT | Lightning | N | made repairs to lat. | -90.1062 | 29.9499 | Lightning | Line Fuse | Lightning | 2020-08-11 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 8
2020 | 6 | 1336387947 | Yes | ORLEANS | THDR | 126 | 2020-08-11 14:49 | 2020-08-11 14:49 | 2020-08-11 16:55 | 756 | TFUS | 551074 | 38260457761 | 1914 | ENOI | 1 | 6 | LGHT | Lightning | N | refused | -90.1257 | 29.9202 | Lightning | Transformer Fuse | Lightning | 2020-08-11 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 59 | 1336388618 | Yes | ORLEANS | THDR | 241 | 2020-08-11 14:59 | 2020-08-11 18:23 | 2020-08-11 19:00 | 14219 | LFUS | 33661 | 3865245932 | 1917 | ENOI | 1 | 59 | EARM | Equipment Failure - Crossarm | N | repaired arm | -90.1132 | 29.9242 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-11 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 2787 | 1336389233 | Yes | ORLEANS | THDR | 11 | 2020-08-11 15:09 | 2020-08-11 15:39 | 2020-08-11 15:19 | 30657 | SBKR | 2147 | 4013146121 | 2147 | ENOI | 1 | 2787 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | molding got into feeder | -90.0665 | 29.9291 | Other | Substation Breaker | Other | 2020-08-11 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 2787 | 1336495346 | NO | ORLEANS | THDR | 19 | 2020-08-11 15:19 | 2020-08-11 15:19 | 2020-08-11 15:38 | 52953 | SBKR | 2147 | 4013146121 | 2147 | ENOI | 1 | 2787 | CCFA | Control Cable Failure | N | Ticket Generated to correct Substation outage time from 8/11; SWMS WR 2300024: found loose 48V supervisory control wire in the SCADA cabinet | -90.0665 | 29.9291 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-08-11 | DSUB | B | Council District B | Jay Banks | 70130 | 8
2020 | 21 | 1336398526 | Yes | ORLEANS | THDR | 129 | 2020-08-11 16:51 | 2020-08-11 18:27 | 2020-08-11 19:00 | 2709 | LFUS | 27624 | 38654459434 | 1917 | ENOI | 1 | 21 | EARM | Equipment Failure - Crossarm | N | replaced arm | -90.1131 | 29.9245 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-11 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 1440 | 1336410466 | Yes | ORLEANS | THDR | 7 | 2020-08-11 19:10 | 2020-08-11 19:16 | 2020-08-11 19:17 | 10080 | SBKR | 1554 | 3950246993 | 1554 | ENOI | 1 | 1440 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Crew found balloons at Clara St. & M.L. King Blvd. | -90.086 | 29.9532 | Other | Substation Breaker | Other | 2020-08-11 | DLIN | B | Council District B | Jay Banks | 70113 | 8
2020 | 1 | 1336423684 | Yes | EAST ORLEANS | THDR | 233 | 2020-08-11 21:07 | 2020-08-11 21:32 | 2020-08-12 01:00 | 233 | TFUS | 1003027 | 4195049339 | 1612 | ENOI | 6 | 1 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.0079 | 30.0168 | Vegetation | Transformer Fuse | Vegetation | 2020-08-11 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 6 | 1336438207 | Yes | ORLEANS | FAIR | 251 | 2020-08-12 08:05 | 2020-08-12 08:05 | 2020-08-12 12:16 | 1506 | TFUS | 504186 | 38071464292 | 2013 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N |  | -90.1314 | 29.9382 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 12 | 1336438575 | Yes | ORLEANS | FAIR | 117 | 2020-08-12 08:14 | 2020-08-12 09:26 | 2020-08-12 10:11 | 1404 | TFUS | 29461 | 40207476128 | 614 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N |  | -90.0636 | 29.9702 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-12 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 14 | 1336438626 | Yes | ORLEANS | FAIR | 494 | 2020-08-12 08:17 | 2020-08-12 08:17 | 2020-08-12 16:31 | 6916 | TFUS | 510680 | 38291464608 | 2013 | ENOI | 1 | 14 | LGHT | Lightning | N |  | -90.1244 | 29.9389 | Lightning | Transformer Fuse | Lightning | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 19 | 1336440009 | Yes | ORLEANS | FAIR | 206 | 2020-08-12 09:00 | 2020-08-12 09:12 | 2020-08-12 12:26 | 3914 | XFMR | 65709 | 38608469776 | 2016 | ENOI | 1 | 19 | ETRD | Equipment Failure - Transformer | N |  | -90.1143 | 29.9531 | Equipment Failure | Transformer | Equipment Failure | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 8
2020 | 27 | 1336441193 | Yes | ORLEANS | FAIR | 336 | 2020-08-12 09:00 | 2020-08-12 11:36 | 2020-08-12 14:36 | 9072 | LFUS | 33120 | 3842745641 | 1917 | ENOI | 1 | 27 | SCHD | Scheduled Interruption | N |  | -90.1203 | 29.9164 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 8
2020 | 51 | 1336450250 | Yes | ORLEANS | FAIR | 129 | 2020-08-12 11:42 | 2020-08-12 12:46 | 2020-08-12 13:51 | 6579 | LFUS | 21569 | 3903748059 | 904 | ENOI | 1 | 51 | EFSW | Equipment Failure - Fuse Switch | N |  | -90.1004 | 29.9827 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 15 | 1336451781 | Yes | ORLEANS | FAIR | 266 | 2020-08-12 12:35 | 2020-08-12 12:35 | 2020-08-12 17:01 | 3990 | TFUS | 67329 | 39228458983 | 1923 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N |  | -90.0952 | 29.9234 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 52 | 1336468491 | Yes | ORLEANS | THDR | 260 | 2020-08-12 13:55 | 2020-08-12 17:05 | 2020-08-12 18:15 | 13520 | DIS | 99670 | 3938345890 | 2147 | ENOI | 1 | 52 | EMER | Emergency Switching | N | Emergency Switching | -90.0903 | 29.923 | Other | Disconnect Switch | Emergency Switching | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 2737 | 1336459260 | Yes | ORLEANS | FAIR | 47 | 2020-08-12 13:55 | 2020-08-12 14:50 | 2020-08-12 14:42 | 128639 | SBKR | 2147 | 4013146121 | 2147 | ENOI | 1 | 2737 | EOSC | Equipment Failure - Shield Conductor | N |  | -90.0665 | 29.9291 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 949 | 1336459167 | Yes | ORLEANS | FAIR | 84 | 2020-08-12 13:55 | 2020-08-12 15:50 | 2020-08-12 15:19 | 97258 | SBKR | 1926 | 3909745682 | 1926 | ENOI | 1 | 949 | EOSC | Equipment Failure - Shield Conductor | N | lightning hit shielded conductor | -90.0993 | 29.9173 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 101 | 1336480868 | Yes | ORLEANS | THDR | 350 | 2020-08-12 13:56 | 2020-08-12 18:42 | 2020-08-12 19:46 | 30401 | OPEN | 3924145907 | 3924145907 | 1923 | ENOI | 1 | 101 | EOSC | Equipment Failure - Shield Conductor | N | Closed with recloser 24210 | -90.0947 | 29.9235 | Equipment Failure | Open | Equipment Failure | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 26 | 1336480800 | Yes | ORLEANS | THDR | 357 | 2020-08-12 13:56 | 2020-08-12 18:44 | 2020-08-12 19:53 | 7826 | OPEN | 3924045911 | 3924045911 | 1923 | ENOI | 1 | 26 | EOSC | Equipment Failure - Shield Conductor | N | Cleared with recloser 24210 | -90.0947 | 29.9236 | Equipment Failure | Open | Equipment Failure | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 466 | 1336460201 | Yes | ORLEANS | THDR | 214 | 2020-08-12 13:57 | 2020-08-12 17:13 | 2020-08-12 17:31 | 99724 | RCLR | 24210 | 3918445893 | 1923 | ENOI | 1 | 466 | EOSC | Equipment Failure - Shield Conductor | N |  | -90.0966 | 29.9233 | Equipment Failure | Recloser | Equipment Failure | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 375 | 1336473930 | Yes | ORLEANS | FAIR | 152 | 2020-08-12 13:57 | 2020-08-12 16:29 | 2020-08-12 16:29 | 57000 | DIS | 25070 | 3925445905 | 1923 | ENOI | 1 | 375 | LGHT | Lightning | N | lightning hit shielded conductor | -90.0943 | 29.9235 | Lightning | Disconnect Switch | Lightning | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 6 | 1336462050 | Yes | ORLEANS | THDR | 96 | 2020-08-12 14:16 | 2020-08-12 14:17 | 2020-08-12 15:52 | 576 | TFUS | 549276 | 38489459162 | 1914 | ENOI | 1 | 6 | VOHL | Overhanging Limb | N | found branch on top of tranformer refuse customer back in lights 8/12/20 | -90.1183 | 29.924 | Vegetation | Transformer Fuse | Vegetation | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 8
2020 | 24 | 1336464576 | Yes | ORLEANS | THDR | 142 | 2020-08-12 14:19 | 2020-08-12 14:46 | 2020-08-12 16:41 | 3408 | LFUS | 37033 | 3869045924 | 1917 | ENOI | 1 | 24 | LGHT | Lightning | N | colplete by 302 on 8/12/20 | -90.1121 | 29.9241 | Lightning | Line Fuse | Lightning | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 12 | 1336462363 | Yes | ORLEANS | THDR | 233 | 2020-08-12 14:22 | 2020-08-12 15:29 | 2020-08-12 18:16 | 2796 | TFUS | 73770 | 39177457608 | 1922 | ENOI | 1 | 12 | EARM | Equipment Failure - Crossarm | N | replaced wilson rack and made new connections | -90.0967 | 29.9195 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 43 | 1336462774 | Yes | ORLEANS | THDR | 128 | 2020-08-12 14:30 | 2020-08-12 15:59 | 2020-08-12 16:38 | 5504 | LFUS | 61361 | 3852345644 | 1912 | ENOI | 1 | 43 | VLGL | Tree/Limb Growing Inside R.O.W. | N | palm tree got into tranformer refuse barrel 8/12/20 | -90.1173 | 29.9165 | Vegetation | Line Fuse | Vegetation | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 8
2020 | 23 | 1336471447 | Yes | ORLEANS | FAIR | 141 | 2020-08-12 15:19 | 2020-08-12 17:02 | 2020-08-12 17:40 | 3243 | DIS | 24523 | 3903246207 | 2024 | ENOI | 1 | 23 | EMER | Emergency Switching | N |  | -90.1013 | 29.9318 | Other | Disconnect Switch | Emergency Switching | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 17 | 1336471434 | Yes | ORLEANS | FAIR | 110 | 2020-08-12 15:56 | 2020-08-12 15:58 | 2020-08-12 17:46 | 1870 | TFUS | 73663 | 39437459616 | 2147 | ENOI | 1 | 17 | EMER | Emergency Switching | N |  | -90.0885 | 29.9249 | Other | Transformer Fuse | Emergency Switching | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 9 | 1336472657 | Yes | ORLEANS | FAIR | 92 | 2020-08-12 16:13 | 2020-08-12 16:13 | 2020-08-12 17:45 | 828 | TFUS | 63013 | 39443460417 | 2147 | ENOI | 1 | 9 | EMER | Emergency Switching | N |  | -90.0883 | 29.9271 | Other | Transformer Fuse | Emergency Switching | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 289 | 1336474882 | Yes | ORLEANS | FAIR | 43 | 2020-08-12 16:47 | 2020-08-12 17:31 | 2020-08-12 17:30 | 12427 | LFUS | 38007 | 3980547500 | 907 | ENOI | 1 | 289 | ASQL | Animal - Squirrel | N | refused ok | -90.0763 | 29.9673 | Animal | Line Fuse | Animal | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70116 | 8
2020 | 1 | 1336479175 | Yes | ORLEANS | FAIR | 611 | 2020-08-12 17:59 | 2020-08-12 17:59 | 2020-08-13 04:10 | 611 | TFUS | 1028563 | 3824246306 | 2013 | ENOI | 1 | 1 | EPOL | Equipment Failure - Pole | N | t pole inside zoo replaced and transferred all facilities | -90.1261 | 29.9347 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-12 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 431 | 1336481256 | Yes | ORLEANS | THDR | 28 | 2020-08-12 18:57 | 2020-08-12 20:01 | 2020-08-12 19:25 | 12068 | RCLR | 24210 | 3918445893 | 1923 | ENOI | 1 | 431 | EMER | Emergency Switching | N | DOC opened recloser for crew to safely clear wire downed by lightning | -90.0966 | 29.9233 | Other | Recloser | Emergency Switching | 2020-08-12 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 184 | 1336483034 | Yes | EAST ORLEANS | FAIR | 144 | 2020-08-12 19:57 | 2020-08-12 21:29 | 2020-08-12 22:21 | 26496 | RCLR | 23282 | 4122747950 | 621 | ENOI | 6 | 184 | MALD | Malicious Damage | N | primary down at intersection of france and prieur: Public said that there were gun shots, them the lights went out. NO PID AROSE | -90.0312 | 29.9789 | Public Damage | Recloser | Public Damage | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 52 | 1336485595 | Yes | EAST ORLEANS | FAIR | 193 | 2020-08-12 19:57 | 2020-08-12 22:08 | 2020-08-12 23:10 | 10296 | DIS | 23316 | 4124747804 | 621 | ENOI | 6 | 52 | MALD | Malicious Damage | N | primary down at intersection of france and prieur: Public said that there were gun shots then the lights went out | -90.0306 | 29.975 | Public Damage | Disconnect Switch | Public Damage | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 79 | 1336486780 | Yes | EAST ORLEANS | FAIR | 248 | 2020-08-12 19:57 | 2020-08-13 00:09 | 2020-08-13 00:05 | 20540 | DIS | 25921 | 4123947698 | 621 | ENOI | 6 | 79 | MALD | Malicious Damage | N | primary down at intersection of france and prieur | -90.0307 | 29.9722 | Public Damage | Disconnect Switch | Public Damage | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 68 | 1336486063 | Yes | EAST ORLEANS | FAIR | 319 | 2020-08-12 19:57 | 2020-08-12 22:33 | 2020-08-13 01:16 | 21692 | DIS | 23061 | 4122747782 | 621 | ENOI | 6 | 68 | MALD | Malicious Damage | N | primary down at intersection of france and prieur | -90.0311 | 29.9746 | Public Damage | Disconnect Switch | Public Damage | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 37 | 1336483433 | Yes | EAST ORLEANS | FAIR | 323 | 2020-08-12 20:07 | 2020-08-13 00:35 | 2020-08-13 01:30 | 11951 | LFUS | 74488 | 4115847718 | 616 | ENOI | 6 | 37 | EMER | Emergency Switching | N | primary down at intersection of france and prieur | -90.0332 | 29.9728 | Other | Line Fuse | Emergency Switching | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 8 | 1336483444 | Yes | EAST ORLEANS | THDR | 502 | 2020-08-12 20:08 | 2020-08-12 21:30 | 2020-08-13 04:30 | 4016 | XFMR | 55984 | 41031480720 | 621 | ENOI | 6 | 8 | LGHT | Lightning | N | replaced 50kva transformer | -90.0372 | 29.9826 | Lightning | Transformer | Lightning | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 8 | 1336487412 | Yes | EAST ORLEANS | FAIR | 118 | 2020-08-12 23:25 | 2020-08-13 00:37 | 2020-08-13 01:23 | 944 | DIS | 23093 | 4124747804 | 616 | ENOI | 6 | 8 | EMER | Emergency Switching | N | primary down at intersection of france and prieur | -90.0306 | 29.975 | Other | Disconnect Switch | Emergency Switching | 2020-08-12 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 10 | 1336492338 | Yes | ORLEANS | FAIR | 86 | 2020-08-13 06:39 | 2020-08-13 06:48 | 2020-08-13 08:05 | 860 | TFUS | 502329 | 38022469736 | B0527 | ENOI | 1 | 10 | EARR | Equipment Failure - Arrestor | N | lightening arrestor blew on transformer, took out transformer and lateral, cleared arrestor and refused transformer and lateral | -90.1329 | 29.9532 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 9 | 1336493890 | Yes | ORLEANS | FAIR | 60 | 2020-08-13 06:55 | 2020-08-13 07:03 | 2020-08-13 07:55 | 540 | TFUS | 504692 | 38056463968 | 2013 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | back on | -90.1319 | 29.9372 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 22 | 1336499908 | Yes | ORLEANS | FAIR | 73 | 2020-08-13 08:25 | 2020-08-13 08:25 | 2020-08-13 09:38 | 1606 | LFUS | 61037 | 3953346410 | 2132 | ENOI | 1 | 22 | SCHD | Scheduled Interruption | N |  | -90.0852 | 29.9372 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-13 | DLIN | B | Council District B | Jay Banks | 70113 | 8
2020 | 28 | 1336502608 | Yes | ORLEANS | FAIR | 198 | 2020-08-13 08:42 | 2020-08-13 08:42 | 2020-08-13 12:00 | 5544 | LFUS | 38498 | 38382466786 | 2013 | ENOI | 1 | 28 | SCHD | Scheduled Interruption | N | crew onsite | -90.1216 | 29.9448 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 1 | 1336509911 | Yes | ORLEANS | FAIR | 114 | 2020-08-13 10:03 | 2020-08-13 10:45 | 2020-08-13 11:57 | 114 | SERV | METER | 38573465996 | 2024 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter opend remotely called amoc and reconnected meter | -90.1156 | 29.9427 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 27 | 1336523310 | Yes | ORLEANS | THDR | 162 | 2020-08-13 12:48 | 2020-08-13 13:56 | 2020-08-13 15:30 | 4374 | LFUS | 21069 | 3884346572 | 1916 | ENOI | 1 | 27 | LGHT | Lightning | N | weather back on | -90.1069 | 29.942 | Lightning | Line Fuse | Lightning | 2020-08-13 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 60 | 1336526642 | Yes | ORLEANS | THDR | 171 | 2020-08-13 12:55 | 2020-08-13 15:32 | 2020-08-13 15:46 | 10260 | LFUS | 21483 | 3920146088 | 1924 | ENOI | 1 | 60 | LGHT | Lightning | N | weather | -90.096 | 29.9285 | Lightning | Line Fuse | Lightning | 2020-08-13 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 111 | 1336526392 | Yes | ORLEANS | THDR | 121 | 2020-08-13 13:06 | 2020-08-13 13:46 | 2020-08-13 15:07 | 13320 | LFUS | 88209 | 3973246078 | 2132 | ENOI | 1 | 111 | LGHT | Lightning | N | Lightning | -90.0792 | 29.9281 | Lightning | Line Fuse | Lightning | 2020-08-13 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 534 | 1336530644 | Yes | ORLEANS | THDR | 51 | 2020-08-13 13:11 | 2020-08-13 14:02 | 2020-08-13 14:02 | 27234 | RCLR | 24944 | 3983048290 | 1711 | ENOI | 1 | 534 | VLFL | Tree On Line Outside R.O.W | N | crew found large limb fell into all 3 phases on Zachery Taylor, Wisner to Marconi | -90.0752 | 29.9887 | Vegetation | Recloser | Vegetation | 2020-08-13 | DLIN | D | Council District D | Jared Brossett | 70119 | 8
2020 | 1419 | 1336525912 | Yes | ORLEANS | THDR | 33 | 2020-08-13 13:12 | 2020-08-13 13:47 | 2020-08-13 13:45 | 46827 | SBKR | 1711 | 4024048726 | 1711 | ENOI | 1 | 1419 | EFER | Equipment Failure - Electronic Recloser | N | Recloser failed to isolate fault causing breaker to trip. Found issues with recloser : See recloser case | -90.0621 | 30.0007 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-08-13 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 1 | 1336536505 | Yes | EAST ORLEANS | THDR | 47 | 2020-08-13 14:54 | 2020-08-13 14:54 | 2020-08-13 15:41 | 47 | SERV | SERVICE | 40527485991 | 1710 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad connection at pole replaced connection got good voltage and customer is happy | -90.0534 | 29.9971 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-13 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 10 | 1336570939 | Yes | ORLEANS | FAIR | 121 | 2020-08-13 20:13 | 2020-08-13 20:56 | 2020-08-13 22:14 | 1210 | LFUS | 35103 | 38696473032 | 2011 | ENOI | 1 | 10 | VOHL | Overhanging Limb | N | branches got on primary and took out c phase | -90.1114 | 29.9619 | Vegetation | Line Fuse | Vegetation | 2020-08-13 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 4 | 1336608182 | Yes | ORLEANS | FAIR | 250 | 2020-08-14 08:50 | 2020-08-14 08:50 | 2020-08-14 13:00 | 1000 | TFUS | 550082 | 38138462485 | 2013 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1294 | 29.9333 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 4 | 1336637785 | Yes | ORLEANS | THDR | 230 | 2020-08-14 11:54 | 2020-08-14 11:54 | 2020-08-14 15:44 | 920 | XFMR | 1589627 | 39276466556 | 2021 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | Changed all three transformers, lightning | -90.0934 | 29.944 | Equipment Failure | Transformer | Equipment Failure | 2020-08-14 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 1 | 1336640583 | Yes | EAST ORLEANS | FAIR | 48 | 2020-08-14 14:35 | 2020-08-14 14:35 | 2020-08-14 15:23 | 48 | TFUS | C73738 | 46356498680 | 1202 | ENOI | 6 | 1 | LGHT | Lightning | N | lightning blew up some sewage and water board gear we opened switches for them so they can make there repaires and they will call back when they wanna energize it | -89.8686 | 30.0301 | Lightning | Transformer Fuse | Lightning | 2020-08-14 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 142 | 1336650485 | Yes | EAST ORLEANS | THDR | 162 | 2020-08-14 15:10 | 2020-08-14 16:41 | 2020-08-14 17:52 | 23004 | LFUS | 23527 | 4046947633 | 614 | ENOI | 6 | 142 | LGHT | Lightning | N | weather, refused | -90.0553 | 29.9708 | Lightning | Line Fuse | Lightning | 2020-08-14 | DLIN | C | Council District C | Kristin Palmer | 70117 | 8
2020 | 4 | 1336643791 | Yes | ORLEANS | THDR | 25 | 2020-08-14 15:16 | 2020-08-14 15:16 | 2020-08-14 15:41 | 100 | TFUS | 61142 | 39170468142 | 2021 | ENOI | 1 | 4 | LGHT | Lightning | N | weather, refused | -90.0966 | 29.9484 | Lightning | Transformer Fuse | Lightning | 2020-08-14 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 13 | 1336660963 | Yes | EAST ORLEANS | THDR | 126 | 2020-08-14 18:34 | 2020-08-14 19:39 | 2020-08-14 20:40 | 1638 | LFUS | 21733 | 4192049148 | 1607 | ENOI | 6 | 13 | LGHT | Lightning | N | lightning took out b & c phases; closed back in | -90.0089 | 30.0117 | Lightning | Line Fuse | Lightning | 2020-08-14 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 391 | 1336666061 | Yes | ORLEANS | FAIR | 90 | 2020-08-14 20:06 | 2020-08-14 21:26 | 2020-08-14 21:36 | 35190 | DIS | 14935 | 3952449376 | 404 | ENOI | 1 | 391 | EARM | Equipment Failure - Crossarm | N | broke crossarm at 14846 | -90.0846 | 30.0187 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-14 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 1 | 1336664905 | Yes | ORLEANS | FAIR | 110 | 2020-08-14 20:06 | 2020-08-14 20:54 | 2020-08-14 21:56 | 110 | RCLR | 14894 | 3910149108 | 404 | ENOI | 1 | 1 | EARM | Equipment Failure - Crossarm | N | broke crossarm at 14846 | -90.0979 | 30.0114 | Equipment Failure | Recloser | Equipment Failure | 2020-08-14 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 16 | 1336667610 | Yes | ORLEANS | FAIR | 259 | 2020-08-14 20:06 | 2020-08-14 20:06 | 2020-08-15 00:25 | 4144 | DIS | 14853 | 3949249280 | 509 | ENOI | 1 | 16 | EARM | Equipment Failure - Crossarm | N | broke crossarm on disc 14846 | -90.0854 | 30.0159 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-14 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 11 | 1336677639 | Yes | EAST ORLEANS | FAIR | 210 | 2020-08-15 09:31 | 2020-08-15 09:31 | 2020-08-15 13:01 | 2310 | XFMR | 59924 | 40992477427 | 611 | ENOI | 6 | 11 | LGHT | Lightning | N | changed transformer. Lights on | -90.0385 | 29.9734 | Lightning | Transformer | Lightning | 2020-08-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 63 | 1336688785 | Yes | EAST ORLEANS | FAIR | 339 | 2020-08-15 10:03 | 2020-08-15 13:25 | 2020-08-15 15:43 | 21357 | LFUS | 25217 | 4240450217 | 2216 | ENOI | 6 | 63 | ETRD | Equipment Failure - Transformer | N | replaced transformer | -89.9932 | 30.0411 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-15 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 8
2020 | 10 | 1336698487 | Yes | ORLEANS | FAIR | 168 | 2020-08-15 15:38 | 2020-08-15 15:38 | 2020-08-15 18:26 | 1680 | XFMR | 71312 | 39425458151 | 2147 | ENOI | 1 | 10 | LGHT | Lightning | N | CHANGED TRANSFORMER | -90.0888 | 29.9208 | Lightning | Transformer | Lightning | 2020-08-15 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 352 | 1336718763 | Yes | EAST ORLEANS | FAIR | 144 | 2020-08-16 01:04 | 2020-08-16 02:16 | 2020-08-16 03:28 | 50688 | RCLR | 65379 | 4407151142 | 2217 | ENOI | 6 | 352 | EREC | Equipment Failure - Recloser / Sectionalizer | N | Patrolled feeder behind recloser check indicators rest switch recloser on one shot as per doc | -89.9401 | 30.066 | Equipment Failure | Recloser | Equipment Failure | 2020-08-16 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 8
2020 | 5 | 1336722056 | Yes | ORLEANS | FAIR | 162 | 2020-08-16 05:59 | 2020-08-16 06:07 | 2020-08-16 08:41 | 810 | TFUS | 1003896 | 38911489462 | 413 | ENOI | 1 | 5 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Refused transformer trimmed tree | -90.1039 | 30.0071 | Vegetation | Transformer Fuse | Vegetation | 2020-08-16 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 17 | 1336723192 | Yes | ORLEANS | FAIR | 106 | 2020-08-16 07:00 | 2020-08-16 07:00 | 2020-08-16 08:46 | 1802 | LFUS | 37939 | 3839645882 | 1914 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | CREW OUTAGE | -90.1212 | 29.923 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-16 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 8
2020 | 3 | 1336728760 | Yes | ORLEANS | FAIR | 138 | 2020-08-16 10:22 | 2020-08-16 10:22 | 2020-08-16 12:40 | 414 | LFUS | 21303 | 3979847230 | 1512 | ENOI | 1 | 3 | SCHD | Scheduled Interruption | N | CREW OUTAGE | -90.0766 | 29.9597 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-16 | DLIN | B | Council District B | Jay Banks | 70112 | 8
2020 | 76 | 1336729167 | Yes | EAST ORLEANS | FAIR | 299 | 2020-08-16 10:42 | 2020-08-16 13:33 | 2020-08-16 15:41 | 22724 | LFUS | 27037 | 4394850834 | 2214 | ENOI | 6 | 76 | ETRD | Equipment Failure - Transformer | N | bad transformer | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-16 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 8
2020 | 1 | 1336731477 | Yes | ORLEANS | FAIR | 106 | 2020-08-16 12:59 | 2020-08-16 12:59 | 2020-08-16 14:45 | 106 | SERV | SERVICE | 39736482937 | 1711 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Spliced out burned service | -90.0782 | 29.9888 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-16 | DLIN | D | Council District D | Jared Brossett | 70119 | 8
2020 | 1 | 1336766246 | Yes | ORLEANS | FAIR | 51 | 2020-08-16 19:56 | 2020-08-16 19:56 | 2020-08-16 20:47 | 51 | SERV | SERVICE | 38387490977 | 409 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad connection at Wilson rack | -90.1204 | 30.0115 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-16 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 60 | 1336780572 | Yes | ORLEANS | THDR | 175 | 2020-08-16 21:40 | 2020-08-17 00:23 | 2020-08-17 00:35 | 10500 | LFUS | 17795 | 3976549020 | 512 | ENOI | 1 | 60 | LGHT | Lightning | N | all 3 fuses @ lateral switch 17795 taken out by lightning refused ok | -90.077 | 30.0089 | Lightning | Line Fuse | Lightning | 2020-08-16 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 44 | 1336782104 | Yes | ORLEANS | THDR | 100 | 2020-08-16 21:45 | 2020-08-16 22:38 | 2020-08-16 23:25 | 4400 | LFUS | 44646 | 3853148813 | 410 | ENOI | 1 | 44 | LGHT | Lightning | N | two phase lateral blown by 18th and pontchartrain by lightning refused ok | -90.1159 | 30.0035 | Lightning | Line Fuse | Lightning | 2020-08-16 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 5 | 1336781903 | Yes | ORLEANS | THDR | 124 | 2020-08-16 21:48 | 2020-08-16 22:55 | 2020-08-16 23:52 | 620 | TFUS | 1385289 | 39706489324 | 1704 | ENOI | 1 | 5 | LGHT | Lightning | N | taken out by lightning refused ok | -90.079 | 30.0064 | Lightning | Transformer Fuse | Lightning | 2020-08-16 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 37 | 1336786489 | Yes | EAST ORLEANS | THDR | 337 | 2020-08-16 22:00 | 2020-08-17 01:33 | 2020-08-17 03:37 | 12469 | LFUS | 74488 | 4115847718 | 616 | ENOI | 6 | 37 | ECNS | Equipment Failure - Connector Sleeve | N | re repaired jumper connection | -90.0332 | 29.9728 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-16 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 5 | 1336787282 | Yes | EAST ORLEANS | THDR | 264 | 2020-08-16 22:05 | 2020-08-16 22:05 | 2020-08-17 02:29 | 1320 | TFUS | C73284 | 42660504690 | 2215 | ENOI | 6 | 5 | EFLK | Equipment Failure - Fuse Link | N | REFUSED TRANSFORMER CUSTOMER BACK IN LIGHTS | -89.985 | 30.0479 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-16 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 8
2020 | 181 | 1336797530 | Yes | EAST ORLEANS | THDR | 224 | 2020-08-16 22:46 | 2020-08-16 23:24 | 2020-08-17 02:31 | 40544 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 181 | ECNS | Equipment Failure - Connector Sleeve | N | repaired jumper connection | -90.0335 | 29.9718 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-16 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 2 | 1336793739 | Yes | EAST ORLEANS | THDR | 281 | 2020-08-16 22:50 | 2020-08-16 22:50 | 2020-08-17 03:31 | 562 | TFUS | 1364684 | 41340480819 | 616 | ENOI | 6 | 2 | EPRI | Equipment Failure - Primary Conductor | N | repaired jumper | -90.0275 | 29.9827 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-16 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 4 | 1336796515 | Yes | ORLEANS | FAIR | 128 | 2020-08-16 23:12 | 2020-08-16 23:13 | 2020-08-17 01:20 | 512 | TFUS | 1530007 | 39358479184 | 912 | ENOI | 1 | 4 | ESEC | Secondary/Service Conductor | N |  | -90.0904 | 29.9787 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-16 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 4 | 1336808692 | Yes | ORLEANS | RAIN | 97 | 2020-08-17 00:53 | 2020-08-17 00:53 | 2020-08-17 02:31 | 388 | LFUS | 93676 | 3965447040 | 1504 | ENOI | 1 | 4 | VHCL | Vehicle | N | car hit pole RELATED TO TKT#1336808592, 1336803349 (A.STEWART) | -90.0813 | 29.9544 | Public Damage | Line Fuse | Public Damage | 2020-08-17 | DLIN | B | Council District B | Jay Banks | 70112 | 8
2020 | 30 | 1336803349 | Yes | ORLEANS | THDR | 67 | 2020-08-17 00:54 | 2020-08-17 01:26 | 2020-08-17 02:01 | 2010 | SBKR | 1504 | 3951046987 | 1504 | ENOI | 1 | 30 | VHCL | Vehicle | N | car hit pole RELATED TO TKT#1336808692, 1336808592 (A.STEWART) | -90.0858 | 29.9531 | Public Damage | Substation Breaker | Public Damage | 2020-08-17 | DLIN | B | Council District B | Jay Banks | 70113 | 8
2020 | 1 | 1336821897 | Yes | EAST ORLEANS | THDR | 686 | 2020-08-17 05:46 | 2020-08-17 05:53 | 2020-08-17 17:12 | 686 | TFUS | 4679051564 | 4679051564 | 1204 | ENOI | 6 | 1 | EPOL | Equipment Failure - Pole | N | broke pole | -89.8541 | 30.0767 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-17 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 45 | 1336828645 | Yes | EAST ORLEANS | THDR | 24 | 2020-08-17 07:32 | 2020-08-17 07:33 | 2020-08-17 07:56 | 1260 | DIS | 23084 | 4129547995 | 616 | ENOI | 6 | 45 | EPOL | Equipment Failure - Pole | N | crew replaced pole | -90.029 | 29.9803 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 9 | 1336828579 | Yes | EAST ORLEANS | FAIR | 396 | 2020-08-17 07:32 | 2020-08-17 07:32 | 2020-08-17 14:08 | 3564 | DIS | 80617 | 4136348208 | 616 | ENOI | 6 | 9 | EPOL | Equipment Failure - Pole | N | crew replaced pole | -90.0269 | 29.9863 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-17 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 26 | 1336831125 | Yes | ORLEANS | THDR | 65 | 2020-08-17 08:15 | 2020-08-17 09:06 | 2020-08-17 09:20 | 1690 | LFUS | 33410 | 3966347387 | 1512 | ENOI | 1 | 26 | EFLK | Equipment Failure - Fuse Link | N | B phase on lateral blown refused ok | -90.0807 | 29.964 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-17 | DLIN | B | Council District B | Jay Banks | 70119 | 8
2020 | 1 | 1336839260 | Yes | EAST ORLEANS | FAIR | 362 | 2020-08-17 09:59 | 2020-08-17 09:59 | 2020-08-17 16:01 | 362 | SERV | SERVICE | 48045512476 | 1204 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N |  | -89.8145 | 30.0674 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-17 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 128 | 1336847856 | Yes | EAST ORLEANS | FAIR | 125 | 2020-08-17 11:56 | 2020-08-17 12:24 | 2020-08-17 14:01 | 16000 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 128 | SCHD | Scheduled Interruption | N | all customers back in | -90.044 | 29.9708 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-17 | DLIN | C | Council District C | Kristin Palmer | 70117 | 8
2020 | 8 | 1336862554 | Yes | ORLEANS | FAIR | 261 | 2020-08-17 15:05 | 2020-08-17 15:05 | 2020-08-17 19:26 | 2088 | XFMR | 56858 | 40174477855 | 1712 | ENOI | 1 | 8 | ETRD | Equipment Failure - Transformer | N |  | -90.0644 | 29.9749 | Equipment Failure | Transformer | Equipment Failure | 2020-08-17 | DLIN | D | Council District D | Jared Brossett | 70116 | 8
2020 | 28 | 1336871675 | Yes | ORLEANS | FAIR | 255 | 2020-08-17 17:16 | 2020-08-17 18:28 | 2020-08-17 21:31 | 7140 | LFUS | 36819 | 3812046814 | 2014 | ENOI | 1 | 28 | ETRD | Equipment Failure - Transformer | N | Bad transformer, crew will change | -90.1299 | 29.9488 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-17 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 16 | 1336872310 | Yes | EAST ORLEANS | THDR | 224 | 2020-08-17 17:31 | 2020-08-17 19:38 | 2020-08-17 21:15 | 3584 | XFMR | 71737 | 40422489059 | 1702 | ENOI | 6 | 16 | ETRD | Equipment Failure - Transformer | N | Leaking transformer | -90.0562 | 30.0055 | Equipment Failure | Transformer | Equipment Failure | 2020-08-17 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 37 | 1336877333 | Yes | EAST ORLEANS | FAIR | 366 | 2020-08-17 19:37 | 2020-08-18 00:07 | 2020-08-18 01:43 | 13542 | LFUS | 26002 | 42919501767 | 2216 | ENOI | 6 | 37 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-17 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 8
2020 | 82 | 1336878042 | Yes | ORLEANS | FAIR | 84 | 2020-08-17 20:05 | 2020-08-17 20:40 | 2020-08-17 21:29 | 6888 | LFUS | 27715 | 3916545880 | 1923 | ENOI | 1 | 82 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.097 | 29.9228 | Vegetation | Line Fuse | Vegetation | 2020-08-17 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 56 | 1336885734 | Yes | ORLEANS | FAIR | 276 | 2020-08-18 05:25 | 2020-08-18 08:33 | 2020-08-18 10:01 | 15456 | LFUS | 21027 | 4017847648 | 614 | ENOI | 1 | 56 | SCHD | Scheduled Interruption | N | back on | -90.0645 | 29.9709 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-18 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 2 | 1336889566 | Yes | EAST ORLEANS | FAIR | 401 | 2020-08-18 08:35 | 2020-08-18 08:35 | 2020-08-18 15:16 | 804 | DIS | 25269 | 4417949194 | 1203 | ENOI | 6 | 2 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9375 | 30.0124 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-08-18 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 7 | 1336892832 | Yes | ORLEANS | FAIR | 165 | 2020-08-18 09:45 | 2020-08-18 09:50 | 2020-08-18 12:30 | 1155 | TFUS | 67513 | 39416460225 | 2147 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | back on | -90.089 | 29.9268 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-18 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 1 | 1336892881 | Yes | EAST ORLEANS | FAIR | 135 | 2020-08-18 09:47 | 2020-08-18 09:47 | 2020-08-18 12:02 | 135 | XFMR | 1355876 | 4140549054 | 1010 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | Hot leg bushing burned on transformer Was able to use a phase pot Customers back in lights | -90.0252 | 30.0093 | Equipment Failure | Transformer | Equipment Failure | 2020-08-18 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 8 | 1336892983 | Yes | ORLEANS | FAIR | 413 | 2020-08-18 09:50 | 2020-08-18 09:50 | 2020-08-18 16:43 | 3304 | DIS | 49955 | 3905145610 | 1927 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Crew Working on Site | -90.1008 | 29.9154 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-08-18 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 40 | 1336902130 | Yes | ORLEANS | FAIR | 107 | 2020-08-18 12:44 | 2020-08-18 12:45 | 2020-08-18 14:31 | 4280 | TFUS | 63332 | 39400460361 | 2147 | ENOI | 1 | 40 | SCHD | Scheduled Interruption | N | back on | -90.0895 | 29.9271 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-18 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 5 | 1336913000 | Yes | ORLEANS | FAIR | 611 | 2020-08-18 15:49 | 2020-08-18 15:52 | 2020-08-19 02:00 | 3055 | XFMR | 1381797 | 40111477488 | 613 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | changed bad transformer | -90.0664 | 29.9739 | Equipment Failure | Transformer | Equipment Failure | 2020-08-18 | DLIN | D | Council District D | Jared Brossett | 70116 | 8
2020 | 5 | 1336922663 | Yes | ORLEANS | FAIR | 149 | 2020-08-18 22:56 | 2020-08-18 23:00 | 2020-08-19 01:25 | 745 | TFUS | 66573 | 38304468352 | 2015 | ENOI | 1 | 5 | EFLK | Equipment Failure - Fuse Link | N | transformer refused ok | -90.124 | 29.9492 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-18 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 5 | 1336925424 | Yes | ORLEANS | FAIR | 178 | 2020-08-19 02:43 | 2020-08-19 02:43 | 2020-08-19 05:41 | 890 | XFMR | 66573 | 38304468352 | 2015 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N |  | -90.124 | 29.9492 | Equipment Failure | Transformer | Equipment Failure | 2020-08-19 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 33 | 1336928838 | Yes | ORLEANS | FAIR | 69 | 2020-08-19 07:21 | 2020-08-19 07:24 | 2020-08-19 08:30 | 2277 | TFUS | 67342 | 39388478514 | 912 | ENOI | 1 | 33 | VHCL | Vehicle | N | UPS truck pulled down messenger cable and shook pole caused fuse to blow. Refused OK. Cox cable wire down at location. HW | -90.0895 | 29.977 | Public Damage | Transformer Fuse | Public Damage | 2020-08-19 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 7 | 1336929014 | Yes | ORLEANS | FAIR | 104 | 2020-08-19 07:31 | 2020-08-19 07:45 | 2020-08-19 09:15 | 728 | TFUS | 527833 | 39880460086 | 2147 | ENOI | 1 | 7 | ASQL | Animal - Squirrel | N | Refused transformer taken out by squirrel | -90.0744 | 29.9262 | Animal | Transformer Fuse | Animal | 2020-08-19 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 124 | 1336929613 | Yes | ORLEANS | FAIR | 484 | 2020-08-19 07:57 | 2020-08-19 10:36 | 2020-08-19 16:01 | 60016 | LFUS | 38135 | 4029447662 | 614 | ENOI | 1 | 124 | SCHD | Scheduled Interruption | N | contract crew on site | -90.0606 | 29.9714 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-19 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 5 | 1336935321 | Yes | ORLEANS | FAIR | 66 | 2020-08-19 09:59 | 2020-08-19 09:59 | 2020-08-19 11:05 | 330 | TFUS | 67336 | 39408478769 | 912 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0888 | 29.9777 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-19 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 30 | 1336938313 | Yes | EAST ORLEANS | THDR | 200 | 2020-08-19 11:04 | 2020-08-19 13:44 | 2020-08-19 14:24 | 6000 | LFUS | 21106 | 4117549075 | 617 | ENOI | 6 | 30 | LGHT | Lightning | N | Lightning hit line causing fuses to blow Rdfused main and sub lateral | -90.0326 | 30.01 | Lightning | Line Fuse | Lightning | 2020-08-19 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 12 | 1336940005 | Yes | ORLEANS | FAIR | 437 | 2020-08-19 11:58 | 2020-08-19 16:37 | 2020-08-19 19:15 | 5244 | XFMR | 55737 | 40223487314 | 1704 | ENOI | 1 | 12 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.0627 | 30.0007 | Equipment Failure | Transformer | Equipment Failure | 2020-08-19 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 52 | 1336940046 | Yes | EAST ORLEANS | THDR | 125 | 2020-08-19 11:58 | 2020-08-19 13:20 | 2020-08-19 14:03 | 6500 | LFUS | 27686 | 4184247070 | 2346 | ENOI | 6 | 52 | LGHT | Lightning | N | Refused B and C phase at sw 27686 and 38435 due to lightning | -90.0122 | 29.9545 | Lightning | Line Fuse | Lightning | 2020-08-19 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 8
2020 | 281 | 1336943015 | Yes | EAST ORLEANS | THDR | 77 | 2020-08-19 11:59 | 2020-08-19 13:07 | 2020-08-19 13:16 | 21637 | DIS | 23500 | 4109848346 | 626 | ENOI | 6 | 281 | EOSC | Equipment Failure - Shield Conductor | N | shield wire down at the 2800 block of louisa | -90.0351 | 29.9898 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-19 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 180 | 1336941284 | Yes | EAST ORLEANS | FAIR | 152 | 2020-08-19 11:59 | 2020-08-19 14:07 | 2020-08-19 14:31 | 27360 | RCLR | 49556 | 4109448377 | 626 | ENOI | 6 | 180 | EOSC | Equipment Failure - Shield Conductor | N | shield wire down at the 2800 block of louisa | -90.0353 | 29.9907 | Equipment Failure | Recloser | Equipment Failure | 2020-08-19 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 17 | 1336941148 | Yes | EAST ORLEANS | THDR | 188 | 2020-08-19 12:22 | 2020-08-19 15:19 | 2020-08-19 15:30 | 3196 | LFUS | 62285 | 4180447921 | 612 | ENOI | 6 | 17 | EARM | Equipment Failure - Crossarm | N | crew repaired crossarm | -90.0131 | 29.9782 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-19 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 8
2020 | 72 | 1336949251 | Yes | EAST ORLEANS | FAIR | 183 | 2020-08-19 12:27 | 2020-08-19 15:28 | 2020-08-19 15:30 | 13176 | LFUS | 32497 | 4112647692 | 611 | ENOI | 6 | 72 | EARM | Equipment Failure - Crossarm | N | repaired broke crossarm | -90.0346 | 29.972 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-19 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 49 | 1336949360 | Yes | ORLEANS | FAIR | 115 | 2020-08-19 15:27 | 2020-08-19 15:37 | 2020-08-19 17:23 | 7475 | LFUS | 39776 | 3884846702 | 1916 | ENOI | 1 | 49 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.1067 | 29.9454 | Vegetation | Line Fuse | Vegetation | 2020-08-19 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 17 | 1336949443 | Yes | ORLEANS | FAIR | 12 | 2020-08-19 15:33 | 2020-08-19 15:44 | 2020-08-19 15:45 | 204 | TFUS | 1285647 | 38780459187 | 1916 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1092 | 29.9239 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-19 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 5 | 1336962570 | Yes | ORLEANS | FAIR | 356 | 2020-08-19 22:05 | 2020-08-19 22:26 | 2020-08-20 04:01 | 1780 | XFMR | 14571 | 38897493471 | 406 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | changed out bad transformer | -90.1042 | 30.018 | Equipment Failure | Transformer | Equipment Failure | 2020-08-19 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 9 | 1336962980 | Yes | ORLEANS | FAIR | 387 | 2020-08-19 22:34 | 2020-08-20 00:38 | 2020-08-20 05:01 | 3483 | XFMR | 26423 | 38943485527 | 403 | ENOI | 1 | 9 | ETRD | Equipment Failure - Transformer | N | change out transformer | -90.103 | 29.9963 | Equipment Failure | Transformer | Equipment Failure | 2020-08-19 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 2 | 1336970368 | Yes | EAST ORLEANS | FAIR | 87 | 2020-08-20 07:18 | 2020-08-20 07:19 | 2020-08-20 08:45 | 174 | TFUS | 57179 | 41902491321 | 1612 | ENOI | 6 | 2 | ASQL | Animal - Squirrel | N | Squirrel caused outage on the delta bank Customer and traffic light back on | -90.0095 | 30.0112 | Animal | Transformer Fuse | Animal | 2020-08-20 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 5 | 1336971569 | Yes | ORLEANS | FAIR | 332 | 2020-08-20 07:53 | 2020-08-20 07:53 | 2020-08-20 13:25 | 1660 | TFUS | 1635273 | 38214462846 | 2013 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.127 | 29.9342 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-20 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 12 | 1336972925 | Yes | ORLEANS | FAIR | 257 | 2020-08-20 08:13 | 2020-08-20 08:17 | 2020-08-20 12:30 | 3084 | TFUS | 29461 | 40207476128 | 614 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0636 | 29.9702 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-20 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 38 | 1336981062 | Yes | EAST ORLEANS | FAIR | 57 | 2020-08-20 11:33 | 2020-08-20 11:59 | 2020-08-20 12:31 | 2166 | LFUS | 21283 | 4312150644 | 2223 | ENOI | 6 | 38 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9705 | 30.0525 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-20 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 8
2020 | 9 | 1336983730 | Yes | ORLEANS | FAIR | 177 | 2020-08-20 12:54 | 2020-08-20 13:02 | 2020-08-20 15:51 | 1593 | XFMR | 64012 | 39168458418 | 1923 | ENOI | 1 | 9 | ETRD | Equipment Failure - Transformer | N | crew replaced transformer | -90.0969 | 29.9217 | Equipment Failure | Transformer | Equipment Failure | 2020-08-20 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 17 | 1337013059 | Yes | ORLEANS | FAIR | 62 | 2020-08-20 23:42 | 2020-08-20 23:43 | 2020-08-21 00:45 | 1054 | TFUS | 30610 | 40296480592 | 627 | ENOI | 1 | 17 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | transformer taken out by mylar balloons refused ok | -90.0604 | 29.9823 | Other | Transformer Fuse | Other | 2020-08-20 | DLIN | D | Council District D | Jared Brossett | 70119 | 8
2020 | 74 | 1337019101 | Yes | EAST ORLEANS | FAIR | 276 | 2020-08-21 04:42 | 2020-08-21 07:39 | 2020-08-21 09:18 | 20424 | DIS | 22751 | 4654451526 | 1202 | ENOI | 6 | 74 | EOSC | Equipment Failure - Shield Conductor | N | shield wire down RELATED TO TKT#1337017668, 1337019265 (A.STEWART) | -89.862 | 30.0753 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 1 | 1337017668 | Yes | EAST ORLEANS | FAIR | 126 | 2020-08-21 04:52 | 2020-08-21 04:52 | 2020-08-21 06:58 | 126 | RCLR | 27973 | 4555150350 | 1202 | ENOI | 6 | 1 | EOSC | Equipment Failure - Shield Conductor | N | shield wire down RELATED TO TKT#1337019265, 1337019101 (A.STEWART) | -89.8937 | 30.0438 | Equipment Failure | Recloser | Equipment Failure | 2020-08-21 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 32 | 1337021029 | Yes | ORLEANS | FAIR | 420 | 2020-08-21 08:00 | 2020-08-21 08:00 | 2020-08-21 15:00 | 13440 | LFUS | 21536 | 3934447910 | 912 | ENOI | 1 | 32 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0908 | 29.9785 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-21 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 7 | 1337020498 | Yes | ORLEANS | FAIR | 212 | 2020-08-21 08:11 | 2020-08-21 08:11 | 2020-08-21 11:43 | 1484 | TFUS | 1589927 | 39449479311 | 912 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0876 | 29.9791 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-21 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 12 | 1337026729 | Yes | ORLEANS | FAIR | 203 | 2020-08-21 10:12 | 2020-08-21 10:12 | 2020-08-21 13:35 | 2436 | XFMR | 53931 | 38768493138 | 411 | ENOI | 1 | 12 | ETRD | Equipment Failure - Transformer | N | CHANGED TRANSFORMER | -90.1083 | 30.0172 | Equipment Failure | Transformer | Equipment Failure | 2020-08-21 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 49 | 1337084435 | Yes | EAST ORLEANS | FAIR | 371 | 2020-08-22 17:03 | 2020-08-22 21:57 | 2020-08-22 23:14 | 18179 | LFUS | 27353 | 4438150319 | 1205 | ENOI | 6 | 49 | ETRD | Equipment Failure - Transformer | N | v 20 b phase padmount bad. leaking oil. call chad goulds to replace 167kva 120/240 padmount transformer | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-22 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 2 | 1337098107 | Yes | EAST ORLEANS | FAIR | 96 | 2020-08-23 10:39 | 2020-08-23 10:39 | 2020-08-23 12:16 | 192 | LFUS | 21056 | 41363483022 | 616 | ENOI | 6 | 2 | LGHT | Lightning | N | refused lateral 21056. rain/ lightning in area | -90.0263 | 29.9887 | Lightning | Line Fuse | Lightning | 2020-08-23 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 178 | 1337104509 | Yes | ORLEANS | FAIR | 61 | 2020-08-23 13:22 | 2020-08-23 14:18 | 2020-08-23 14:23 | 10858 | LFUS | 27626 | 3884847852 | 2026 | ENOI | 1 | 178 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -90.1064 | 29.977 | Other | Line Fuse | Other | 2020-08-23 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 1 | 1337104761 | Yes | ORLEANS | FAIR | 143 | 2020-08-23 13:39 | 2020-08-23 14:16 | 2020-08-23 16:02 | 143 | SERV | 79266 | 38745462998 | 1921 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.1103 | 29.9345 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-23 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 24 | 1337107942 | Yes | EAST ORLEANS | FAIR | 89 | 2020-08-23 16:00 | 2020-08-23 16:05 | 2020-08-23 17:29 | 2136 | TFUS | 665678 | 40630476580 | 622 | ENOI | 6 | 24 | VLGL | Tree/Limb Growing Inside R.O.W. | N | match ticket with 2465 n villere | -90.05 | 29.9712 | Vegetation | Transformer Fuse | Vegetation | 2020-08-23 | DLIN | C | Council District C | Kristin Palmer | 70117 | 8
2020 | 2 | 1337114437 | Yes | ORLEANS | FAIR | 294 | 2020-08-23 23:21 | 2020-08-23 23:25 | 2020-08-24 04:15 | 588 | XFMR | 24633 | 38864475156 | 911 | ENOI | 1 | 2 | ETRD | Equipment Failure - Transformer | N | crew changed out transformer bank | -90.1063 | 29.9679 | Equipment Failure | Transformer | Equipment Failure | 2020-08-23 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 8 | 1337115557 | Yes | ORLEANS | FAIR | 236 | 2020-08-24 00:20 | 2020-08-24 00:20 | 2020-08-24 04:16 | 1888 | LFUS | 33961 | 3892747491 | 911 | ENOI | 1 | 8 | ETRD | Equipment Failure - Transformer | N | crew changed out transformer bank | -90.1041 | 29.9668 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-24 | DLIN | B | Council District B | Jay Banks | 70119 | 8
2020 | 68 | 1337174756 | Yes | EAST ORLEANS | FAIR | 294 | 2020-08-24 03:01 | 2020-08-25 14:59 | 2020-08-24 07:55 | 68 | OPEN | 4161449854 | 4161449854 | 1001 | ENOI | 6 | 68 | EELB | Equipment Failure - Elbow | N | replaced bad elbow in vault 44, customers back on now - step restoration | -90.0183 | 30.0312 | Equipment Failure | Open | Equipment Failure | 2020-08-24 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 97 | 1337116696 | Yes | EAST ORLEANS | FAIR | 324 | 2020-08-24 03:01 | 2020-08-24 07:23 | 2020-08-24 08:25 | 31428 | LFUS | 15003-F | 4162549719 | 1001 | ENOI | 6 | 97 | EELB | Equipment Failure - Elbow | N | bad elbow in v-44 took out later; crew is making repairs - step restoration was performed | -90.018 | 30.0276 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-24 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 20 | 1337121094 | Yes | EAST ORLEANS | FAIR | 509 | 2020-08-24 03:01 | 2020-08-24 10:15 | 2020-08-24 11:30 | 10180 | TFUS | 1229207 | 41523497460 | 1001 | ENOI | 6 | 20 | EELB | Equipment Failure - Elbow | N | bad elbow in xfmr in v-44 | -90.0213 | 30.0283 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-24 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 12 | 1337124750 | Yes | EAST ORLEANS | FAIR | 62 | 2020-08-24 10:24 | 2020-08-24 10:24 | 2020-08-24 11:26 | 744 | LFUS | 21592 | 4191547283 | 2346 | ENOI | 6 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0098 | 29.9604 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-24 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 8
2020 | 8 | 1337128372 | Yes | ORLEANS | FAIR | 41 | 2020-08-24 11:04 | 2020-08-24 11:04 | 2020-08-24 11:45 | 328 | TFUS | 62982 | 39433460899 | 1923 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0884 | 29.9286 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-24 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 18 | 1337130843 | Yes | ORLEANS | FAIR | 17 | 2020-08-24 12:25 | 2020-08-24 12:25 | 2020-08-24 12:42 | 306 | DIS | 24030 | 3939848102 | 1711 | ENOI | 1 | 18 | EARM | Equipment Failure - Crossarm | N | crew replacing crossarm | -90.0889 | 29.9837 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-24 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 77 | 1337147704 | Yes | ORLEANS | FAIR | 22 | 2020-08-24 20:53 | 2020-08-24 21:30 | 2020-08-24 21:15 | 1694 | LFUS | 27965 | 3946447872 | 912 | ENOI | 1 | 77 | VLGL | Tree/Limb Growing Inside R.O.W. | N | trimming trees | -90.0871 | 29.9774 | Vegetation | Line Fuse | Vegetation | 2020-08-24 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 144 | 1337148135 | Yes | ORLEANS | FAIR | 31 | 2020-08-24 21:37 | 2020-08-24 21:50 | 2020-08-24 22:08 | 4464 | LFUS | 38134 | 40222476429 | 614 | ENOI | 1 | 144 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons took out lateral cleared refused ok | -90.0629 | 29.971 | Other | Line Fuse | Other | 2020-08-24 | DLIN | C | Council District C | Kristin Palmer | 70116 | 8
2020 | 10 | 1337159318 | Yes | ORLEANS | FAIR | 77 | 2020-08-25 10:13 | 2020-08-25 10:13 | 2020-08-25 11:31 | 770 | TFUS | 18507 | 38973492675 | 406 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1019 | 30.0158 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-25 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 27 | 1337161456 | Yes | ORLEANS | FAIR | 211 | 2020-08-25 11:15 | 2020-08-25 11:15 | 2020-08-25 14:46 | 5697 | LFUS | 45455 | 3934547712 | 912 | ENOI | 1 | 27 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0909 | 29.9731 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-08-25 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 6 | 1337164271 | Yes | ORLEANS | FAIR | 188 | 2020-08-25 12:12 | 2020-08-25 12:12 | 2020-08-25 15:20 | 1128 | TFUS | 511032 | 38160462631 | 2013 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1285 | 29.9336 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-25 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 7 | 1337165570 | Yes | ORLEANS | FAIR | 141 | 2020-08-25 12:19 | 2020-08-25 12:19 | 2020-08-25 14:40 | 987 | TFUS | 531488 | 38105461836 | 2013 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N |  | -90.1304 | 29.9313 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-25 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 8 | 1337174568 | Yes | ORLEANS | FAIR | 89 | 2020-08-25 14:51 | 2020-08-25 14:51 | 2020-08-25 16:20 | 712 | TFUS | 1032141 | 38493457602 | 1914 | ENOI | 1 | 8 | ESEC | Secondary/Service Conductor | N | Changed transformer lead | -90.1183 | 29.92 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-25 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 8
2020 | 11 | 1337205764 | Yes | ORLEANS | FAIR | 24 | 2020-08-26 09:26 | 2020-08-26 09:26 | 2020-08-26 09:50 | 264 | TFUS | 78697 | 38807463670 | 1921 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N |  | -90.1084 | 29.9363 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-26 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 76 | 1337218122 | Yes | EAST ORLEANS | WIND | 122 | 2020-08-26 12:34 | 2020-08-26 13:52 | 2020-08-26 14:36 | 9272 | LFUS | 27848 | 4181447129 | 2346 | ENOI | 6 | 76 | SLAK | Slack Conductor / Loose Connection | N | crew removed slack out of span; all customers restored | -90.0129 | 29.9562 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-26 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 8
2020 | 2797 | 1337235948 | Yes | ORLEANS | WIND | 6 | 2020-08-26 14:52 | 2020-08-26 14:59 | 2020-08-26 14:58 | 16782 | SBKR | 2132 | 4013446134 | 2132 | ENOI | 1 | 2797 | EMER | Emergency Switching | N | opened up breaker for servicman to remove tyvek home wrap tangled in feeder | -90.0664 | 29.9294 | Other | Substation Breaker | Emergency Switching | 2020-08-26 | DLIN | B | Council District B | Jay Banks | 70130 | 8
2020 | 1 | 1337255051 | Yes | ORLEANS | FAIR | 77 | 2020-08-26 17:39 | 2020-08-26 17:40 | 2020-08-26 18:56 | 77 | SERV | SERVICE | 39327466901 | 2021 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Bad connection at pole fixed ok | -90.0918 | 29.945 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-26 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 1653 | 1337456015 | Yes | EAST ORLEANS | THDR | 45 | 2020-08-27 03:12 | 2020-08-27 03:52 | 2020-08-27 03:57 | 74385 | VFI | 27422 | 4366350629 | 2213 | ENOI | 6 | 1653 | STRM | Storm | N | refused vfi Possible flash in cub 504 | -97.0758 | 27.9066 | Other | Vacuum Fault Interrupter | Other | 2020-08-27 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 8
2020 | 735 | 1337514451 | Yes | ORLEANS | THDR | 47 | 2020-08-27 06:46 | 2020-08-27 07:31 | 2020-08-27 07:33 | 34545 | RCLR | 56113 | 3924746012 | 1922 | ENOI | 1 | 735 | VOHL | Overhanging Limb | N | Overhanging Limb,Storm | -90.0946 | 29.9264 | Vegetation | Recloser | Vegetation | 2020-08-27 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 5 | 1337514413 | Yes | ORLEANS | THDR | 114 | 2020-08-27 06:46 | 2020-08-27 07:24 | 2020-08-27 08:41 | 570 | TFUS | 63260 | 39040457468 | 1923 | ENOI | 1 | 5 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Refused transformer and lateral c phase | -90.1012 | 29.9191 | Vegetation | Transformer Fuse | Vegetation | 2020-08-27 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 1 | 1337536038 | Yes | EAST ORLEANS | THDR | 83 | 2020-08-27 07:29 | 2020-08-27 07:29 | 2020-08-27 08:52 | 83 | LFUS | 17548 | 41320493904 | 1009 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | refused b phase lateral customer back on | -90.0276 | 30.0187 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-27 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 5 | 1337589713 | Yes | ORLEANS | THDR | 325 | 2020-08-27 08:19 | 2020-08-27 08:19 | 2020-08-27 13:44 | 1625 | TFUS | 1385289 | 39706489324 | 1704 | ENOI | 1 | 5 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Trimmed tree refused transformer | -90.079 | 30.0064 | Vegetation | Transformer Fuse | Vegetation | 2020-08-27 | DLIN | D | Council District D | Jared Brossett | 70122 | 8
2020 | 812 | 1337624971 | Yes | EAST ORLEANS | THDR | 186 | 2020-08-27 09:00 | 2020-08-27 11:37 | 2020-08-27 12:06 | 93756 | RCLR | 13897 | 4150649420 | 1010 | ENOI | 6 | 812 | VHCL | Vehicle | N | car hit pole | -90.022 | 30.0193 | Public Damage | Recloser | Public Damage | 2020-08-27 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 24 | 1337694827 | Yes | ORLEANS | THDR | 91 | 2020-08-27 10:26 | 2020-08-27 10:36 | 2020-08-27 11:57 | 2184 | LFUS | 17724 | 3858548405 | 407 | ENOI | 1 | 24 | VOHL | Overhanging Limb | N | vegatation (branch took out B&C phase). | -90.1146 | 29.9923 | Vegetation | Line Fuse | Vegetation | 2020-08-27 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 31 | 1337704750 | Yes | ORLEANS | THDR | 49 | 2020-08-27 10:41 | 2020-08-27 11:23 | 2020-08-27 11:30 | 1519 | LFUS | 38502 | 3822046761 | B0526 | ENOI | 1 | 31 | VOHL | Overhanging Limb | N | removed limb off primary | -90.1266 | 29.9474 | Vegetation | Line Fuse | Vegetation | 2020-08-27 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 108 | 1337773674 | Yes | ORLEANS | THDR | 40 | 2020-08-27 12:06 | 2020-08-27 12:47 | 2020-08-27 12:46 | 4320 | LFUS | 27871 | 3856346998 | 2016 | ENOI | 1 | 108 | VOHL | Overhanging Limb | N | A phase only blown refused ok | -90.1157 | 29.9536 | Vegetation | Line Fuse | Vegetation | 2020-08-27 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 8
2020 | 216 | 1337812312 | Yes | EAST ORLEANS | FAIR | 127 | 2020-08-27 12:29 | 2020-08-27 14:28 | 2020-08-27 14:36 | 27432 | LFUS | 27886 | 4087447744 | 622 | ENOI | 6 | 216 | EFLK | Equipment Failure - Fuse Link | N | Refused lateral b and c phase back on | -90.0424 | 29.9736 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-27 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 1 | 1337825550 | Yes | EAST ORLEANS | THDR | 127 | 2020-08-27 12:44 | 2020-08-27 12:44 | 2020-08-27 14:51 | 127 | TFUS | 74295 | 40717475927 | 622 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | a and b phase were blown refused ok | -90.0473 | 29.9693 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-27 | DLIN | C | Council District C | Kristin Palmer | 70117 | 8
2020 | 8 | 1337857298 | Yes | ORLEANS | FAIR | 111 | 2020-08-27 13:25 | 2020-08-27 13:25 | 2020-08-27 15:16 | 888 | TFUS | 58663 | 38930466122 | 1916 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1042 | 29.9431 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-27 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 8 | 1337899662 | Yes | ORLEANS | THDR | 39 | 2020-08-27 14:12 | 2020-08-27 14:15 | 2020-08-27 14:51 | 312 | TFUS | 56491 | 38469462981 | 1926 | ENOI | 1 | 8 | ESEC | Secondary/Service Conductor | N | Down open wire picked up | -90.119 | 29.9344 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-27 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 167 | 1337967310 | Yes | ORLEANS | FAIR | 113 | 2020-08-27 14:31 | 2020-08-27 15:39 | 2020-08-27 16:24 | 18871 | LFUS | 27894 | 3922646091 | 1924 | ENOI | 1 | 167 | ETRD | Equipment Failure - Transformer | N | bad transformer 63557 took out lateral | -90.0952 | 29.9286 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-27 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 116 | 1337943360 | Yes | EAST ORLEANS | THDR | 181 | 2020-08-27 14:45 | 2020-08-27 16:45 | 2020-08-27 17:46 | 20996 | LFUS | 32647 | 4123847544 | 611 | ENOI | 6 | 116 | EOSC | Equipment Failure - Shield Conductor | N | ran new shield conductor | -90.0309 | 29.9678 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-27 | DLIN | D | Council District D | Jared Brossett | 70117 | 8
2020 | 2 | 1338275445 | Yes | ORLEANS | FAIR | 237 | 2020-08-27 22:24 | 2020-08-27 22:24 | 2020-08-28 02:21 | 474 | TFUS | 31447 | 39610470812 | 1510 | ENOI | 1 | 2 | EARR | Equipment Failure - Arrestor | N | Blown lightning arrester A phase | -90.0826 | 29.9557 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-27 | DLIN | B | Council District B | Jay Banks | 70112 | 8
2020 | 7 | 1338352951 | Yes | EAST ORLEANS | FAIR | 122 | 2020-08-28 05:36 | 2020-08-28 05:50 | 2020-08-28 07:38 | 854 | TFUS | 27961 | 42245491903 | 1607 | ENOI | 6 | 7 | EFLK | Equipment Failure - Fuse Link | N | Refuse transformer customer back on lateral was in | -89.9987 | 30.0128 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-08-28 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 8
2020 | 1 | 1338369847 | Yes | EAST ORLEANS | FAIR | 116 | 2020-08-28 06:46 | 2020-08-28 06:46 | 2020-08-28 08:43 | 116 | SECO | SECN | 42997495325 | 1604 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Repaired secondary services on Wilson rack energized transformer back in lights | -89.9748 | 30.022 | Equipment Failure | Secondary Conductor | Equipment Failure | 2020-08-28 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 8
2020 | 1 | 1338379902 | Yes | EAST ORLEANS | FAIR | 289 | 2020-08-28 07:18 | 2020-08-28 07:18 | 2020-08-28 12:07 | 289 | XFMR | 32167 | 44367493516 | 1203 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | bad transformer | -89.9314 | 30.0167 | Equipment Failure | Transformer | Equipment Failure | 2020-08-28 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 1 | 1338429109 | Yes | ORLEANS | FAIR | 91 | 2020-08-28 09:17 | 2020-08-28 09:17 | 2020-08-28 10:48 | 91 | SERV | SECONDARY COND | 38794475957 | 2026 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | changed connections | -90.1083 | 29.9699 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-28 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 3038 | 1338513256 | Yes | ORLEANS | RAIN | 56 | 2020-08-28 13:16 | 2020-08-28 14:18 | 2020-08-28 14:12 | 182343 | DIS | 24274 | 3853847255 | 2015 | ENOI | 1 | 3038 | EMER | Emergency Switching | N | single phasing, open primary at fig and dante | -90.1164 | 29.9607 | Other | Disconnect Switch | Emergency Switching | 2020-08-28 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 58 | 1338509948 | Yes | ORLEANS | RAIN | 52 | 2020-08-28 13:20 | 2020-08-28 13:59 | 2020-08-28 14:12 | 3016 | LFUS | 35102 | 3887947088 | 2015 | ENOI | 1 | 58 | EPRI | Equipment Failure - Primary Conductor | N | single phasing c phase, fig st and dante | -90.1056 | 29.956 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-28 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 88 | 1338525043 | Yes | ORLEANS | RAIN | 16 | 2020-08-28 13:56 | 2020-08-28 14:11 | 2020-08-28 14:12 | 3168 | SBKR | 2015 | 3847647388 | 2015 | ENOI | 1 | 88 | ECNS | Equipment Failure - Connector Sleeve | N | single phasing c phase, fig st and dante | -90.1183 | 29.9644 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-08-28 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 103 | 1338523504 | Yes | ORLEANS | RAIN | 12 | 2020-08-28 14:00 | 2020-08-28 14:11 | 2020-08-28 14:12 | 1236 | LFUS | 33278 | 3865047100 | 2015 | ENOI | 1 | 103 | EPRI | Equipment Failure - Primary Conductor | N | single phasing c phase, fig st and dante | -90.1129 | 29.9566 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-28 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 7 | 1338606862 | Yes | ORLEANS | THDR | 89 | 2020-08-28 17:41 | 2020-08-28 17:41 | 2020-08-28 19:10 | 623 | TFUS | 59754 | 39641482471 | 1711 | ENOI | 1 | 7 | STRM | Storm | N | Transformer refused ok not sure what took it out | -90.0812 | 29.9878 | Other | Transformer Fuse | Other | 2020-08-28 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 1084 | 1338622571 | Yes | EAST ORLEANS | FAIR | 8 | 2020-08-28 18:17 | 2020-08-28 18:25 | 2020-08-28 18:25 | 8672 | SBKR | 1610 | 4351349757 | 1610 | ENOI | 6 | 1084 | VOHL | Overhanging Limb | N | tree burning at location had to dump not to burn feeders | -90.0179 | 30.0195 | Vegetation | Substation Breaker | Vegetation | 2020-08-28 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 9 | 1338622104 | Yes | EAST ORLEANS | FAIR | 247 | 2020-08-28 18:17 | 2020-08-28 19:38 | 2020-08-28 22:24 | 2223 | DIS | 27508 | 4174249463 | 1610 | ENOI | 6 | 9 | VOHL | Overhanging Limb | N | replaced broken cross arm caused by limb | -90.0146 | 30.0204 | Vegetation | Disconnect Switch | Vegetation | 2020-08-28 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 40 | 1338714572 | Yes | EAST ORLEANS | FAIR | 324 | 2020-08-29 04:05 | 2020-08-29 06:10 | 2020-08-29 09:29 | 12960 | DIS | 26285 | 4650151430 | 1202 | ENOI | 6 | 40 | ECNS | Equipment Failure - Connector Sleeve | N | b phase jumper open at 2700 tidgeway | -89.8633 | 30.0729 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-08-29 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 4 | 1338820249 | Yes | ORLEANS | FAIR | 38 | 2020-08-29 13:23 | 2020-08-29 13:23 | 2020-08-29 14:01 | 152 | TFUS | 59959 | 38844466152 | 1916 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N |  | -90.1061 | 29.9432 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-29 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 45 | 1338870302 | Yes | EAST ORLEANS | FAIR | 83 | 2020-08-29 15:56 | 2020-08-29 16:17 | 2020-08-29 17:19 | 3735 | LFUS | 17119-F | 4154449236 | 1010 | ENOI | 6 | 45 | EPRI | Equipment Failure - Primary Conductor | N | Replaced A phase riser at lateral switch 17119 | -90.0207 | 30.0144 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-29 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 23 | 1338924720 | Yes | ORLEANS | FAIR | 210 | 2020-08-29 19:31 | 2020-08-29 22:53 | 2020-08-29 23:01 | 4830 | XFMR | 58576 | 39078462013 | 1924 | ENOI | 1 | 23 | ETRD | Equipment Failure - Transformer | N | Burned lead on transformer fixed ok | -90.0997 | 29.9316 | Equipment Failure | Transformer | Equipment Failure | 2020-08-29 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 12 | 1339074681 | Yes | ORLEANS | FAIR | 216 | 2020-08-30 14:24 | 2020-08-30 15:17 | 2020-08-30 18:00 | 2592 | XFMR | 517221 | 38337458934 | 1914 | ENOI | 1 | 12 | ETRD | Equipment Failure - Transformer | N |  | -90.1231 | 29.9233 | Equipment Failure | Transformer | Equipment Failure | 2020-08-30 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 8
2020 | 6 | 1339086921 | Yes | ORLEANS | FAIR | 212 | 2020-08-30 15:31 | 2020-08-30 18:04 | 2020-08-30 19:03 | 1272 | XFMR | 63090 | 38616472343 | 2015 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | crew changed out bad transformer | -90.114 | 29.9601 | Equipment Failure | Transformer | Equipment Failure | 2020-08-30 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 1 | 1339179893 | Yes | EAST ORLEANS | FAIR | 169 | 2020-08-31 07:41 | 2020-08-31 07:41 | 2020-08-31 10:30 | 169 | SERV | SECN | 40855489657 | 617 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Replaced hot leg connection at pole | -90.0424 | 30.0072 | Equipment Failure | Service Conductor | Equipment Failure | 2020-08-31 | DLIN | D | Council District D | Jared Brossett | 70126 | 8
2020 | 18 | 1339187131 | Yes | ORLEANS | FAIR | 210 | 2020-08-31 08:29 | 2020-08-31 10:48 | 2020-08-31 11:59 | 3780 | LFUS | 33099 | 3904549248 | 406 | ENOI | 1 | 18 | VINE | Vine Growing into Line | N | Removed vines and re fused ok | -90.0996 | 30.0153 | Vegetation | Line Fuse | Vegetation | 2020-08-31 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 14 | 1339236059 | Yes | ORLEANS | FAIR | 76 | 2020-08-31 12:14 | 2020-08-31 13:22 | 2020-08-31 13:30 | 1064 | TFUS | 63579 | 38875466390 | 1916 | ENOI | 1 | 14 | SCHD | Scheduled Interruption | N |  | -90.106 | 29.9439 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-31 | DLIN | B | Council District B | Jay Banks | 70125 | 8
2020 | 167 | 1339244760 | Yes | ORLEANS | FAIR | 78 | 2020-08-31 13:00 | 2020-08-31 14:17 | 2020-08-31 14:18 | 13026 | LFUS | 33917 | 3889947659 | 2026 | ENOI | 1 | 167 | EINS | Equipment Failure - Insulator | N |  | -90.1048 | 29.9717 | Equipment Failure | Line Fuse | Equipment Failure | 2020-08-31 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 8
2020 | 13 | 1339249087 | Yes | ORLEANS | FAIR | 75 | 2020-08-31 13:16 | 2020-08-31 13:29 | 2020-08-31 14:31 | 975 | TFUS | 69947 | 39080460691 | 1924 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N |  | -90.0999 | 29.928 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-08-31 | DLIN | B | Council District B | Jay Banks | 70115 | 8
2020 | 1 | 1339257305 | Yes | EAST ORLEANS | THDR | 161 | 2020-08-31 13:50 | 2020-08-31 13:50 | 2020-08-31 16:31 | 161 | TFUS | 1375078 | 4846251288 | 1204 | ENOI | 6 | 1 | LGHT | Lightning | N | Refused B phase taken out by lightning--needs sw # on pole | -89.8013 | 30.0683 | Lightning | Transformer Fuse | Lightning | 2020-08-31 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 8
2020 | 10 | 1339285065 | Yes | ORLEANS | FAIR | 179 | 2020-08-31 14:59 | 2020-08-31 15:25 | 2020-08-31 17:58 | 1790 | XFMR | 1278094 | 38947483806 | 904 | ENOI | 1 | 10 | ETRD | Equipment Failure - Transformer | N | bad 50 KVA transformer changed out cust back in | -90.1029 | 29.9915 | Equipment Failure | Transformer | Equipment Failure | 2020-08-31 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 8 | 1339302126 | Yes | ORLEANS | FAIR | 204 | 2020-08-31 15:45 | 2020-08-31 15:56 | 2020-08-31 19:09 | 1632 | XFMR | 1589083 | 38440491626 | 409 | ENOI | 1 | 8 | ETRD | Equipment Failure - Transformer | N | bad transfomer changed out 50 kva transfomer | -90.1188 | 30.0133 | Equipment Failure | Transformer | Equipment Failure | 2020-08-31 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 8
2020 | 7 | 1339393634 | Yes | ORLEANS | FAIR | 27 | 2020-09-01 08:33 | 2020-09-01 08:33 | 2020-09-01 09:00 | 189 | TFUS | 61927 | 38920467049 | 1916 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N |  | -90.1046 | 29.9457 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-01 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 12 | 1339393659 | Yes | ORLEANS | FAIR | 147 | 2020-09-01 08:33 | 2020-09-01 10:13 | 2020-09-01 11:00 | 1764 | TFUS | 61138 | 38900466914 | 1916 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N |  | -90.1053 | 29.9452 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-01 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 64 | 1339460045 | Yes | EAST ORLEANS | FAIR | 6 | 2020-09-01 11:54 | 2020-09-01 12:03 | 2020-09-01 12:00 | 384 | SWIT | 21950 | 4394850834 | 2213 | ENOI | 6 | 64 | EMER | Emergency Switching | N | crew could not get switch 21952 in Cubicle #210 opened, contingency switching was preformed to minumize outage | -97.0758 | 27.9066 | Other | Switch | Emergency Switching | 2020-09-01 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 160 | 1339695382 | Yes | EAST ORLEANS | FAIR | 40 | 2020-09-01 22:06 | 2020-09-01 22:42 | 2020-09-01 22:46 | 6400 | LFUS | 14680 | 4040249576 | 505 | ENOI | 6 | 160 | EFLK | Equipment Failure - Fuse Link | N | refused | -90.0566 | 30.0239 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-01 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 69 | 1339698629 | Yes | EAST ORLEANS | FAIR | 32 | 2020-09-01 23:28 | 2020-09-01 23:28 | 2020-09-02 | 2208 | LFUS | 28080 | 4099047734 | 611 | ENOI | 6 | 69 | EFSW | Equipment Failure - Fuse Switch | N | crew replacing switch | -90.0386 | 29.9732 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-01 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 3 | 1339704127 | Yes | EAST ORLEANS | FAIR | 161 | 2020-09-02 02:29 | 2020-09-02 02:29 | 2020-09-02 05:10 | 483 | TFUS | 26167 | 40318496447 | 505 | ENOI | 6 | 3 | AOTH | Animal - Other (Describe in Remarks Field) | N | RAT GOT ACROSS PHASES | -90.0593 | 30.0258 | Animal | Transformer Fuse | Animal | 2020-09-02 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 32 | 1339727895 | Yes | ORLEANS | FAIR | 294 | 2020-09-02 09:20 | 2020-09-02 09:20 | 2020-09-02 14:14 | 9408 | LFUS | 33871 | 3992546274 | 2142 | ENOI | 1 | 32 | EARM | Equipment Failure - Crossarm | N |  | -90.0729 | 29.9335 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-02 | DLIN | B | Council District B | Jay Banks | 70130 | 9
2020 | 13 | 1339819393 | Yes | EAST ORLEANS | FAIR | 126 | 2020-09-02 14:57 | 2020-09-02 14:59 | 2020-09-02 17:03 | 1638 | XFMR | 56716 | 40640488752 | 1702 | ENOI | 6 | 13 | ETRD | Equipment Failure - Transformer | N | change out xformer | -90.0493 | 30.0047 | Equipment Failure | Transformer | Equipment Failure | 2020-09-02 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 712 | 1339905951 | Yes | EAST ORLEANS | FAIR | 38 | 2020-09-02 18:15 | 2020-09-02 18:50 | 2020-09-02 18:52 | 27056 | SBKR | 626 | 4081248423 | 626 | ENOI | 6 | 712 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | lateral fell into the feeder due to balloons | -90.0442 | 29.9922 | Other | Substation Breaker | Other | 2020-09-02 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 1 | 1339932680 | Yes | ORLEANS | HEAT | 68 | 2020-09-02 22:03 | 2020-09-02 22:03 | 2020-09-02 23:11 | 68 | SERV | SERVICE | 38183457791 | 1912 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | changed out meter put new info to office | -90.128 | 29.9203 | Other | Service Conductor | Other | 2020-09-02 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 1 | 1340006947 | Yes | ORLEANS | FAIR | 82 | 2020-09-03 18:47 | 2020-09-03 18:49 | 2020-09-03 20:09 | 82 | SERV | SERVICE | 39122465013 | 1925 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | conector burned up on pole changed conector | -90.0984 | 29.9399 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-03 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 1 | 1340041161 | Yes | ORLEANS | FAIR | 74 | 2020-09-04 08:29 | 2020-09-04 08:29 | 2020-09-04 09:43 | 74 | SERV | SERVICE | 40349473997 | 614 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | Ami opened meter | -90.0591 | 29.9643 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-04 | DLIN | C | Council District C | Kristin Palmer | 70116 | 9
2020 | 2 | 1340139797 | Yes | ORLEANS CBD | FAIR | 180 | 2020-09-04 22:33 | 2020-09-04 22:33 | 2020-09-05 01:34 | 360 | SBKR | 288 | 4019546896 | 288 | ENOI | 4 | 2 | EMER | Emergency Switching | N | Dropped out for safety to work on fdr 259 | -90.0642 | 29.9504 | Other | Substation Breaker | Emergency Switching | 2020-09-04 | DLIN | C | Council District C | Kristin Palmer | 70130 | 9
2020 | 1 | 1340245019 | Yes | ORLEANS | FAIR | 1314 | 2020-09-05 18:00 | 2020-09-05 18:00 | 2020-09-06 15:54 | 1314 | SBKR | 1515 | 3951946983 | 1515 | ENOI | 1 | 1 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | underground splice in manhole at Poydras & Loyola Sts. | -90.0855 | 29.953 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-09-05 | DLIN | B | Council District B | Jay Banks | 70113 | 9
2020 | 110 | 1340217818 | Yes | ORLEANS | FAIR | 115 | 2020-09-05 23:12 | 2020-09-06 01:03 | 2020-09-06 01:07 | 12650 | LFUS | 27949 | 3986347312 | 1512 | ENOI | 1 | 110 | UNKN | Inspected Unknown | N | outage un known a phase of lateral blown | -90.0745 | 29.962 | Other | Line Fuse | Other | 2020-09-05 | DLIN | C | Council District C | Kristin Palmer | 70112 | 9
2020 | 21 | 1340219153 | Yes | ORLEANS | FAIR | 100 | 2020-09-06 00:48 | 2020-09-06 00:48 | 2020-09-06 02:28 | 2100 | TFUS | 63749 | 39177465017 | 1915 | ENOI | 1 | 21 | VHCL | Vehicle | N | car hit pole blowing lateral no damage to pole and lateral refused HW | -90.0965 | 29.9399 | Public Damage | Transformer Fuse | Public Damage | 2020-09-06 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 60 | 1340227967 | Yes | ORLEANS | FAIR | 214 | 2020-09-06 07:54 | 2020-09-06 11:33 | 2020-09-06 11:28 | 12840 | LFUS | 50314 | 3870546896 | 1926 | ENOI | 1 | 60 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Caused by mylar balloons | -90.1112 | 29.951 | Other | Line Fuse | Other | 2020-09-06 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 9
2020 | 6 | 1340255498 | Yes | ORLEANS | FAIR | 243 | 2020-09-06 14:05 | 2020-09-06 14:05 | 2020-09-06 18:08 | 1458 | TFUS | 60878 | 38691469848 | 1926 | ENOI | 1 | 6 | VLFL | Tree On Line Outside R.O.W | N |  | -90.1116 | 29.9532 | Vegetation | Transformer Fuse | Vegetation | 2020-09-06 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 6 | 1340269428 | Yes | EAST ORLEANS | FAIR | 87 | 2020-09-06 20:24 | 2020-09-06 20:24 | 2020-09-06 21:51 | 522 | TFUS | 67689 | 42534494530 | 1607 | ENOI | 6 | 6 | EFLK | Equipment Failure - Fuse Link | N | Equipment Failure - Fuse Link | -89.9895 | 30.02 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-06 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 9
2020 | 1 | 1340305618 | Yes | ORLEANS | FAIR | 112 | 2020-09-07 19:15 | 2020-09-07 19:15 | 2020-09-07 21:07 | 112 | SERV | SERVICE | 38534461198 | 1914 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad connection at pole | -90.1168 | 29.9295 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-07 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 9
2020 | 41 | 1340322583 | Yes | ORLEANS | FAIR | 253 | 2020-09-08 08:13 | 2020-09-08 08:13 | 2020-09-08 12:26 | 10373 | LFUS | 21996 | 3941647749 | 912 | ENOI | 1 | 41 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0887 | 29.974 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-08 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 9
2020 | 16 | 1340326115 | Yes | ORLEANS | FAIR | 27 | 2020-09-08 09:34 | 2020-09-08 09:43 | 2020-09-08 10:01 | 432 | LFUS | 17565 | 3883848713 | 405 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1063 | 30.0008 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-08 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 52 | 1340380378 | Yes | EAST ORLEANS | FAIR | 268 | 2020-09-09 04:03 | 2020-09-09 06:59 | 2020-09-09 08:31 | 13936 | LFUS | 25441 | 4438550872 | 1609 | ENOI | 6 | 52 | EPRI | Equipment Failure - Primary Conductor | N | Bad cable between v32 and v33 | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-09 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 9
2020 | 127 | 1340386086 | Yes | ORLEANS | FAIR | 233 | 2020-09-09 06:38 | 2020-09-09 09:19 | 2020-09-09 10:31 | 29591 | LFUS | 36821 | 3815246634 | 2014 | ENOI | 1 | 127 | VLGL | Tree/Limb Growing Inside R.O.W. | N | wire down | -90.1287 | 29.944 | Vegetation | Line Fuse | Vegetation | 2020-09-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 71 | 1340382435 | Yes | ORLEANS | FAIR | 125 | 2020-09-09 06:40 | 2020-09-09 08:12 | 2020-09-09 08:45 | 8875 | LFUS | 27622 | 3816646701 | 2014 | ENOI | 1 | 71 | VLGL | Tree/Limb Growing Inside R.O.W. | N | refused A phase on main lateral, taken out by sub lateral tree fell and pulled wire down | -90.1281 | 29.9459 | Vegetation | Line Fuse | Vegetation | 2020-09-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 76 | 1340385023 | Yes | ORLEANS | FAIR | 154 | 2020-09-09 08:17 | 2020-09-09 08:58 | 2020-09-09 10:51 | 11704 | LFUS | 33406 | 3930647930 | 912 | ENOI | 1 | 76 | SCHD | Scheduled Interruption | N | 228-282-2735; corey bennett | -90.092 | 29.979 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-09 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 9
2020 | 22 | 1340406301 | Yes | EAST ORLEANS | FAIR | 108 | 2020-09-09 15:47 | 2020-09-09 16:46 | 2020-09-09 17:35 | 2376 | LFUS | 25398 | 42902502309 | 2216 | ENOI | 6 | 22 | ETRD | Equipment Failure - Transformer | N | Crew replaced failed submersible transformer in front of 10320 Chevy Chase Dr. | -89.9774 | 30.0413 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-09 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 9
2020 | 35 | 1340434124 | Yes | ORLEANS | FAIR | 215 | 2020-09-10 07:30 | 2020-09-10 09:28 | 2020-09-10 11:05 | 7525 | LFUS | 27897 | 3940347980 | 912 | ENOI | 1 | 35 | SCHD | Scheduled Interruption | N |  | -90.0888 | 29.9804 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-10 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 9
2020 | 18 | 1340438402 | Yes | ORLEANS | FAIR | 195 | 2020-09-10 08:45 | 2020-09-10 08:52 | 2020-09-10 12:00 | 3510 | TFUS | 1351141 | 38950461752 | 1925 | ENOI | 1 | 18 | SCHD | Scheduled Interruption | N | back on | -90.1038 | 29.9311 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-10 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 1 | 1340482915 | Yes | EAST ORLEANS | FAIR | 202 | 2020-09-11 02:59 | 2020-09-11 02:59 | 2020-09-11 06:21 | 202 | TFUS | C62036 | 44463498506 | 1601 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | Transformer fuse blown taken out by vines | -89.9283 | 30.0302 | Vegetation | Transformer Fuse | Vegetation | 2020-09-11 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 9
2020 | 39 | 1340519317 | Yes | ORLEANS | FAIR | 120 | 2020-09-11 12:58 | 2020-09-11 13:03 | 2020-09-11 14:58 | 4680 | OPEN | 3992249188 | 3992249188 | 510 | ENOI | 1 | 39 | EARM | Equipment Failure - Crossarm | N |  | -90.072 | 30.0135 | Equipment Failure | Open | Equipment Failure | 2020-09-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 39 | 1340509890 | Yes | ORLEANS | FAIR | 116 | 2020-09-11 13:03 | 2020-09-11 13:03 | 2020-09-11 14:59 | 4524 | LFUS | 17675 | 3989349266 | 510 | ENOI | 1 | 39 | EARM | Equipment Failure - Crossarm | N | changed broken lateral arm | -90.0731 | 30.0154 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 38 | 1340539195 | Yes | ORLEANS | FAIR | 64 | 2020-09-11 22:37 | 2020-09-11 22:37 | 2020-09-11 23:41 | 2432 | TFUS | 652089 | 3927147812 | 904 | ENOI | 1 | 38 | LGHT | Lightning | N | Blown lateral fuse on A phase only. Blown lightning arrestor. | -90.0931 | 29.9757 | Lightning | Transformer Fuse | Lightning | 2020-09-11 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 9
2020 | 2254 | 1340572004 | Yes | EAST ORLEANS | FAIR | 62 | 2020-09-12 17:08 | 2020-09-12 18:03 | 2020-09-12 18:10 | 139748 | SBKR | 2216 | 4334450774 | 2216 | ENOI | 6 | 2254 | EARM | Equipment Failure - Crossarm | N | crossarm broke, back on | -89.9633 | 30.056 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-09-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 35 | 1340572037 | Yes | EAST ORLEANS | FAIR | 235 | 2020-09-12 17:11 | 2020-09-12 20:26 | 2020-09-12 21:06 | 8225 | LFUS | 37102 | 4308850547 | 2223 | ENOI | 6 | 35 | EARM | Equipment Failure - Crossarm | N | Fdr 2216 x-arm above lateral failed and caused lateral primary to burn down | -89.9715 | 30.0497 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-12 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 648 | 1340574673 | Yes | EAST ORLEANS | FAIR | 127 | 2020-09-12 17:18 | 2020-09-12 19:20 | 2020-09-12 19:25 | 82296 | DIS | 25189 | 4697851574 | 1204 | ENOI | 6 | 648 | EPOL | Equipment Failure - Pole | N | broke pole, crew on site | -89.8481 | 30.0769 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-09-12 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 9
2020 | 18 | 1340577404 | Yes | EAST ORLEANS | FAIR | 280 | 2020-09-12 17:51 | 2020-09-12 18:59 | 2020-09-12 22:31 | 5040 | LFUS | 21216 | 4109648387 | 626 | ENOI | 6 | 18 | EARM | Equipment Failure - Crossarm | N | bad crossarm | -90.0352 | 29.991 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-12 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 331 | 1340620132 | Yes | ORLEANS | FAIR | 209 | 2020-09-13 06:11 | 2020-09-13 09:10 | 2020-09-13 09:40 | 69179 | DIS | 25494 | 3882647318 | 2011 | ENOI | 1 | 331 | VINE | Vine Growing into Line | N | repaired | -90.1071 | 29.9625 | Vegetation | Disconnect Switch | Vegetation | 2020-09-13 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 16 | 1340615851 | Yes | ORLEANS | FAIR | 107 | 2020-09-13 06:11 | 2020-09-13 07:07 | 2020-09-13 07:59 | 1712 | SBKR | 2011 | 3847547393 | 2011 | ENOI | 1 | 16 | EARM | Equipment Failure - Crossarm | N | broken cross arm, still retoring feeder | -90.1183 | 29.9645 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-09-13 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 46 | 1340616570 | Yes | ORLEANS | FAIR | 115 | 2020-09-13 06:35 | 2020-09-13 08:17 | 2020-09-13 08:30 | 5290 | LFUS | F05720 | 3894747329 | 2017 | ENOI | 1 | 46 | EARM | Equipment Failure - Crossarm | N | broke crossarm, repaired | -90.1036 | 29.9627 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-13 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 2523 | 1340628775 | Yes | ORLEANS | FAIR | 6 | 2020-09-13 11:11 | 2020-09-13 11:17 | 2020-09-13 11:18 | 15138 | SBKR | 1924 | 3909545682 | 1924 | ENOI | 1 | 2523 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | guy wire came lose and hit phase at deadend of feeder, clear now | -90.0994 | 29.9173 | Other | Substation Breaker | Other | 2020-09-13 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 17 | 1340633471 | Yes | EAST ORLEANS | FAIR | 84 | 2020-09-13 12:52 | 2020-09-13 13:02 | 2020-09-13 14:16 | 1428 | TFUS | 1155554 | 40524474979 | 2347 | ENOI | 6 | 17 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Palm tree took out transformer trimmed tree and refused ok. Cust back on | -90.0535 | 29.9667 | Vegetation | Transformer Fuse | Vegetation | 2020-09-13 | DLIN | C | Council District C | Kristin Palmer | 70117 | 9
2020 | 2 | 1340646356 | Yes | ORLEANS | FAIR | 1344 | 2020-09-13 17:57 | 2020-09-13 17:57 | 2020-09-14 16:20 | 2688 | SBKR | 1500 | 3951846979 | 1500 | ENOI | 1 | 2 | EPRI | Equipment Failure - Primary Conductor | N | bad cable in duct MH 1-1552 to 2-1552 | -90.0855 | 29.9529 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-09-13 | DLIN | B | Council District B | Jay Banks | 70113 | 9
2020 | 89 | 1340647059 | Yes | ORLEANS | FAIR | 85 | 2020-09-13 18:27 | 2020-09-13 18:58 | 2020-09-13 19:52 | 7565 | LFUS | 28053 | 3943846624 | 1915 | ENOI | 1 | 89 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons across lines. | -90.0884 | 29.9432 | Other | Line Fuse | Other | 2020-09-13 | DLIN | B | Council District B | Jay Banks | 70113 | 9
2020 | 1 | 1340650026 | Yes | ORLEANS | FAIR | 130 | 2020-09-13 19:50 | 2020-09-13 19:51 | 2020-09-13 22:00 | 130 | SERV | SERVICE | 39343457555 | 1922 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Connector bad at pole. Changed. | -90.0916 | 29.9192 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-13 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 1 | 1340650892 | Yes | EAST ORLEANS | FAIR | 218 | 2020-09-13 20:29 | 2020-09-13 20:29 | 2020-09-14 00:07 | 218 | SERV | SERVICE | 44504510646 | 1609 | ENOI | 6 | 1 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | Service burned up in pan AMI electrician replaced guts spliced out service good volatge | -89.9265 | 30.0637 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-13 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 9
2020 | 3 | 1340661128 | Yes | ORLEANS | FAIR | 78 | 2020-09-14 02:47 | 2020-09-14 02:51 | 2020-09-14 04:05 | 234 | TFUS | 1000592 | 39657461330 | 2146 | ENOI | 1 | 3 | VINE | Vine Growing into Line | N | vines growing on transformer refused ok | -90.0815 | 29.9296 | Vegetation | Transformer Fuse | Vegetation | 2020-09-14 | DLIN | B | Council District B | Jay Banks | 70130 | 9
2020 | 115 | 1340678231 | Yes | ORLEANS | FAIR | 251 | 2020-09-14 08:10 | 2020-09-14 10:20 | 2020-09-14 12:21 | 28865 | LFUS | F05219 | 3960746184 | 2146 | ENOI | 1 | 115 | EARM | Equipment Failure - Crossarm | N | x arm | -90.0829 | 29.9309 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-14 | DLIN | B | Council District B | Jay Banks | 70130 | 9
2020 | 115 | 1340673504 | Yes | ORLEANS | FAIR | 204 | 2020-09-14 08:17 | 2020-09-14 08:17 | 2020-09-14 11:41 | 23460 | LFUS | F05219 | 3960746184 | 2146 | ENOI | 1 | 115 | SCHD | Scheduled Interruption | N |  | -90.0829 | 29.9309 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-14 | DLIN | B | Council District B | Jay Banks | 70130 | 9
2020 | 56 | 1340669430 | Yes | ORLEANS | FAIR | 220 | 2020-09-14 08:40 | 2020-09-14 11:28 | 2020-09-14 12:20 | 12320 | LFUS | 27806 | 3884646637 | 1916 | ENOI | 1 | 56 | SCHD | Scheduled Interruption | N |  | -90.1067 | 29.9438 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-14 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 79 | 1340683041 | Yes | EAST ORLEANS | FAIR | 124 | 2020-09-14 13:37 | 2020-09-14 15:41 | 2020-09-14 15:41 | 9796 | LFUS | 50003 | 4068547762 | 622 | ENOI | 6 | 79 | EONC | Equipment Failure - Neutral Conductor | N | repaired | -90.0485 | 29.974 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-14 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 8 | 1340683046 | Yes | ORLEANS | FAIR | 73 | 2020-09-14 13:38 | 2020-09-14 14:18 | 2020-09-14 14:51 | 584 | TFUS | 67898 | 38325469598 | 2015 | ENOI | 1 | 8 | VLFL | Tree On Line Outside R.O.W | N | trimmed palm tree transformwer re fused good | -90.1232 | 29.9526 | Vegetation | Transformer Fuse | Vegetation | 2020-09-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 10 | 1340685223 | Yes | ORLEANS | FAIR | 91 | 2020-09-14 14:27 | 2020-09-14 14:38 | 2020-09-14 15:58 | 910 | TFUS | 578417 | 38939468951 | 2015 | ENOI | 1 | 10 | ASQL | Animal - Squirrel | N | squirrel took out the lateral refused good | -90.1038 | 29.9508 | Animal | Transformer Fuse | Animal | 2020-09-14 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 55 | 1340691677 | Yes | ORLEANS | FAIR | 68 | 2020-09-14 15:34 | 2020-09-14 15:44 | 2020-09-14 16:42 | 3740 | LFUS | 37273 | 3823546899 | 2013 | ENOI | 1 | 55 | ECNS | Equipment Failure - Connector Sleeve | N | jumper at carrolton and jeannette on one phase burnt open, open transformers and made jumper back up reenergized transformers | -90.1261 | 29.9509 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-14 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 1 | 1340703995 | Yes | ORLEANS | FAIR | 76 | 2020-09-14 19:53 | 2020-09-14 20:15 | 2020-09-14 21:09 | 76 | SERV | SERVICE | 39062475004 | 2025 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | changed burnt service | -90.0996 | 29.9673 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-14 | DLIN | B | Council District B | Jay Banks | 70119 | 9
2020 | 3 | 1340736969 | Yes | ORLEANS | FAIR | 220 | 2020-09-15 09:36 | 2020-09-15 09:36 | 2020-09-15 13:16 | 660 | TFUS | 74376 | 39740471145 | 1543 | ENOI | 1 | 3 | SCHD | Scheduled Interruption | N |  | -90.0785 | 29.9566 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-15 | DLIN | B | Council District B | Jay Banks | 70112 | 9
2020 | 17 | 1340738355 | Yes | EAST ORLEANS | FAIR | 53 | 2020-09-15 10:06 | 2020-09-15 10:19 | 2020-09-15 10:59 | 901 | TFUS | 1413872 | 4117148004 | 621 | ENOI | 6 | 17 | ETRD | Equipment Failure - Transformer | N | REFUSED TRANSFORMER CUSTOMER BACK IN LIGHTS | -90.0329 | 29.9804 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 1 | 1340745446 | Yes | EAST ORLEANS | FAIR | 24 | 2020-09-15 11:18 | 2020-09-15 11:18 | 2020-09-15 11:42 | 24 | TFUS | 660413 | 4127548922 | 625 | ENOI | 6 | 1 | SCHD | Scheduled Interruption | N |  | -90.0292 | 30.0058 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-15 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 1 | 1340772862 | Yes | ORLEANS | FAIR | 63 | 2020-09-15 20:55 | 2020-09-15 20:59 | 2020-09-15 21:58 | 63 | SERV | SERVICE | 39528465656 | 1554 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | spliced burnt service | -90.0855 | 29.9415 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-15 | DLIN | B | Council District B | Jay Banks | 70113 | 9
2020 | 1 | 1340775615 | Yes | ORLEANS | FAIR | 96 | 2020-09-15 21:30 | 2020-09-15 21:30 | 2020-09-15 23:06 | 96 | SERV | SERVICE | 39534488257 | 1703 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | reworked UG handhole | -90.0843 | 30.0035 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-15 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 10 | 1340777676 | Yes | ORLEANS | FAIR | 1479 | 2020-09-16 00:24 | 2020-09-16 00:24 | 2020-09-17 01:03 | 14790 | SBKR | 1501 | 3951646982 | 1501 | ENOI | 1 | 10 | ECNS | Equipment Failure - Connector Sleeve | N | breaker relayed out | -90.0856 | 29.9529 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-09-16 | DLIN | B | Council District B | Jay Banks | 70113 | 9
2020 | 357 | 1340778633 | Yes | ORLEANS | FAIR | 22 | 2020-09-16 02:12 | 2020-09-16 02:46 | 2020-09-16 02:34 | 7854 | SBKR | 2011 | 3847547393 | 2011 | ENOI | 1 | 357 | VHCL | Vehicle | N | car hit pole RELATED TO TKT#1340779201 (A.STEWART) | -90.1183 | 29.9645 | Public Damage | Substation Breaker | Public Damage | 2020-09-16 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 330 | 1340779201 | Yes | ORLEANS | FAIR | 38 | 2020-09-16 02:32 | 2020-09-16 03:15 | 2020-09-16 03:10 | 15510 | DIS | 25494 | 3882647318 | 2011 | ENOI | 1 | 330 | VHCL | Vehicle | N | pole hit at broadway and stroelitz RELATED TO TKT#1340778633 (A.STEWART) | -90.1071 | 29.9625 | Public Damage | Disconnect Switch | Public Damage | 2020-09-16 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 4 | 1340780787 | Yes | EAST ORLEANS | FAIR | 148 | 2020-09-16 05:56 | 2020-09-16 05:56 | 2020-09-16 08:25 | 592 | TFUS | 1084113 | 41343478509 | 621 | ENOI | 6 | 4 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | Ground broke off pole fell on B phase blew lateral cleared refused | -90.0275 | 29.9762 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-16 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 18 | 1340788927 | Yes | ORLEANS | FAIR | 161 | 2020-09-16 10:10 | 2020-09-16 10:10 | 2020-09-16 12:51 | 2898 | TFUS | 76492 | 39743476043 | 907 | ENOI | 1 | 18 | SCHD | Scheduled Interruption | N |  | -90.0782 | 29.9698 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-16 | DLIN | D | Council District D | Jared Brossett | 70119 | 9
2020 | 111 | 1340795144 | Yes | ORLEANS | FAIR | 36 | 2020-09-16 10:55 | 2020-09-16 10:55 | 2020-09-16 11:31 | 3996 | LFUS | 37784 | 3981748046 | 1709 | ENOI | 1 | 111 | EARM | Equipment Failure - Crossarm | N | broken x arm | -90.0757 | 29.9822 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-16 | DLIN | D | Council District D | Jared Brossett | 70119 | 9
2020 | 7 | 1340837913 | Yes | EAST ORLEANS | FAIR | 98 | 2020-09-17 07:37 | 2020-09-17 07:37 | 2020-09-17 09:15 | 686 | TFUS | 3007471 | 4094448142 | 621 | ENOI | 6 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0401 | 29.9845 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 8 | 1340838777 | Yes | ORLEANS | FAIR | 37 | 2020-09-17 07:59 | 2020-09-17 07:59 | 2020-09-17 08:36 | 296 | TFUS | 59768 | 38937465460 | 1916 | ENOI | 1 | 8 | ESEC | Secondary/Service Conductor | N | transformer lead | -90.1041 | 29.9413 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-17 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 1 | 1340839886 | Yes | EAST ORLEANS | FAIR | 354 | 2020-09-17 08:23 | 2020-09-17 08:23 | 2020-09-17 14:17 | 354 | XFMR | 1498421 | 4028049471 | 503 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | replace xformer | -90.0607 | 30.021 | Equipment Failure | Transformer | Equipment Failure | 2020-09-17 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 1 | 1340855058 | Yes | EAST ORLEANS | FAIR | 206 | 2020-09-17 13:34 | 2020-09-17 13:34 | 2020-09-17 17:00 | 206 | TFUS | 57916 | 40911481010 | 621 | ENOI | 6 | 1 | SCHD | Scheduled Interruption | N |  | -90.041 | 29.9834 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-17 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 3 | 1340882019 | Yes | EAST ORLEANS | FAIR | 73 | 2020-09-18 08:53 | 2020-09-18 08:53 | 2020-09-18 10:06 | 219 | TFUS | 1304360 | 4102648115 | 621 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0375 | 29.9837 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-18 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 16 | 1340889439 | Yes | EAST ORLEANS | FAIR | 7 | 2020-09-18 11:19 | 2020-09-18 11:19 | 2020-09-18 11:26 | 112 | LFUS | 32640 | 4176847139 | 2346 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0143 | 29.9565 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-18 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 9
2020 | 1 | 1340913742 | Yes | EAST ORLEANS | FAIR | 165 | 2020-09-18 15:59 | 2020-09-18 15:59 | 2020-09-18 18:44 | 165 | SERV | SERVICE | 50474544797 | 1204 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | replaced service | -89.7364 | 30.1556 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-18 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 9
2020 | 85 | 1340919767 | Yes | EAST ORLEANS | FAIR | 169 | 2020-09-18 17:08 | 2020-09-18 19:30 | 2020-09-18 19:57 | 14365 | LFUS | 28074 | 4101347706 | 611 | ENOI | 6 | 85 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons caused fuses to blow in front of 3417 Urquhart St | -90.0378 | 29.9724 | Other | Line Fuse | Other | 2020-09-18 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 36 | 1340942278 | Yes | ORLEANS | RAIN | 485 | 2020-09-19 10:35 | 2020-09-19 14:41 | 2020-09-19 18:40 | 17460 | LFUS | 17893 | 3986449263 | 510 | ENOI | 1 | 36 | VLGL | Tree/Limb Growing Inside R.O.W. | N | refused b phase | -90.074 | 30.0154 | Vegetation | Line Fuse | Vegetation | 2020-09-19 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 236 | 1340942769 | Yes | ORLEANS | RAIN | 221 | 2020-09-19 10:44 | 2020-09-19 14:11 | 2020-09-19 14:25 | 52156 | LFUS | 38003 | 3986247643 | 907 | ENOI | 1 | 236 | EARR | Equipment Failure - Arrestor | N | found failed arrestor and flashed over insulator on corner structure at dorgenios & gov nicholls | -90.0742 | 29.971 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-19 | DLIN | D | Council District D | Jared Brossett | 70116 | 9
2020 | 21 | 1340949696 | Yes | ORLEANS | RAIN | 304 | 2020-09-19 11:26 | 2020-09-19 12:00 | 2020-09-19 16:30 | 6384 | DIS | 24676 | 3836546670 | 2013 | ENOI | 1 | 21 | VLGL | Tree/Limb Growing Inside R.O.W. | N | span of primary down at willow and broadway | -90.1221 | 29.9448 | Vegetation | Disconnect Switch | Vegetation | 2020-09-19 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 104 | 1340946772 | Yes | EAST ORLEANS | FAIR | 140 | 2020-09-19 11:57 | 2020-09-19 13:13 | 2020-09-19 14:17 | 14560 | LFUS | 17967 | 4174249329 | 1001 | ENOI | 6 | 104 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Had to clear balloon off line customer back in | -90.0143 | 30.017 | Other | Line Fuse | Other | 2020-09-19 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 2359 | 1340946935 | Yes | ORLEANS | FAIR | 50 | 2020-09-19 12:00 | 2020-09-19 12:52 | 2020-09-19 12:51 | 117950 | SBKR | 2013 | 3847547389 | 2013 | ENOI | 1 | 2359 | VLGL | Tree/Limb Growing Inside R.O.W. | N | span of primary down at willow and broadway | -90.1183 | 29.9644 | Vegetation | Substation Breaker | Vegetation | 2020-09-19 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 64 | 1340953564 | Yes | ORLEANS | RAIN | 173 | 2020-09-19 13:36 | 2020-09-19 15:38 | 2020-09-19 16:29 | 11072 | DIS | 24078 | 3833446658 | B0525 | ENOI | 1 | 64 | EMER | Emergency Switching | N | Taken out for safety to pickup 1 span of primary down at willow and broadway off of fdr 2013 | -90.1229 | 29.9445 | Other | Disconnect Switch | Emergency Switching | 2020-09-19 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 49 | 1340975816 | Yes | ORLEANS | FAIR | 89 | 2020-09-19 23:00 | 2020-09-19 23:16 | 2020-09-20 00:29 | 4361 | LFUS | 21377 | 3902646822 | 1553 | ENOI | 1 | 49 | EARM | Equipment Failure - Crossarm | N | Replaced broken braces | -90.1013 | 29.9488 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-19 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 50 | 1341008492 | Yes | EAST ORLEANS | RAIN | 58 | 2020-09-20 11:08 | 2020-09-20 11:22 | 2020-09-20 12:06 | 2900 | LFUS | 27235 | 4326450737 | 2223 | ENOI | 6 | 50 | VINE | Vine Growing into Line | N | Clear vines and refused latera | -89.966 | 30.055 | Vegetation | Line Fuse | Vegetation | 2020-09-20 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 40 | 1341015432 | Yes | ORLEANS | FAIR | 317 | 2020-09-20 11:24 | 2020-09-20 12:50 | 2020-09-20 16:41 | 12680 | LFUS | 33410 | 3966347387 | 1512 | ENOI | 1 | 40 | EARM | Equipment Failure - Crossarm | N | REPAIRED CROSSARM | -90.0807 | 29.964 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-20 | DLIN | B | Council District B | Jay Banks | 70119 | 9
2020 | 1294 | 1341010751 | Yes | EAST ORLEANS | FAIR | 56 | 2020-09-20 11:49 | 2020-09-20 12:42 | 2020-09-20 12:45 | 72464 | SBKR | 1601 | 4351549746 | 1601 | ENOI | 6 | 1294 | EINS | Equipment Failure - Insulator | N | phase came off of insulator | -89.9583 | 30.0277 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-09-20 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 9
2020 | 13 | 1341010642 | Yes | ORLEANS | FAIR | 325 | 2020-09-20 11:54 | 2020-09-20 16:06 | 2020-09-20 17:19 | 4225 | TFUS | 59448 | 39256457455 | 1922 | ENOI | 1 | 13 | VLGL | Tree/Limb Growing Inside R.O.W. | N | crew refused transformer | -90.0944 | 29.919 | Vegetation | Transformer Fuse | Vegetation | 2020-09-20 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 87 | 1341015981 | Yes | EAST ORLEANS | FAIR | 35 | 2020-09-20 12:56 | 2020-09-20 13:15 | 2020-09-20 13:32 | 3045 | RCLR | 85894 | 4420549751 | 1601 | ENOI | 6 | 87 | EMER | Emergency Switching | N | recloser opened when closing in feeder; gave order to close | -89.9365 | 30.0278 | Other | Recloser | Emergency Switching | 2020-09-20 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 9
2020 | 10 | 1341038669 | Yes | ORLEANS | FAIR | 421 | 2020-09-20 16:47 | 2020-09-20 18:17 | 2020-09-20 23:48 | 4210 | TFUS | 64920 | 38718467292 | 1916 | ENOI | 1 | 10 | LGHT | Lightning | N | weather | -90.1108 | 29.9462 | Lightning | Transformer Fuse | Lightning | 2020-09-20 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 9
2020 | 109 | 1341042823 | Yes | EAST ORLEANS | FAIR | 195 | 2020-09-20 17:41 | 2020-09-20 19:49 | 2020-09-20 20:56 | 21255 | LFUS | 27777 | 4085447421 | 623 | ENOI | 6 | 109 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Molding for pole ground fell on phase--Removed molding with long stick and refused B phase at 27777 | -90.0432 | 29.9647 | Other | Line Fuse | Other | 2020-09-20 | DLIN | C | Council District C | Kristin Palmer | 70117 | 9
2020 | 3 | 1341044705 | Yes | ORLEANS | FAIR | 338 | 2020-09-20 18:23 | 2020-09-20 18:23 | 2020-09-21 00:01 | 1014 | TFUS | 69197 | 38575457279 | 1913 | ENOI | 1 | 3 | VINE | Vine Growing into Line | N | Cleared vibes from transformer | -90.1156 | 29.9188 | Vegetation | Transformer Fuse | Vegetation | 2020-09-20 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 9
2020 | 1 | 1341063083 | Yes | ORLEANS | FAIR | 87 | 2020-09-21 01:21 | 2020-09-21 01:21 | 2020-09-21 02:48 | 87 | SERV | SERVICE | 38718467292 | 1916 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | repaired bad hot leg at transformer. | -90.1108 | 29.9462 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-21 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 9
2020 | 30 | 1341065463 | Yes | ORLEANS | RAIN | 309 | 2020-09-21 03:44 | 2020-09-21 08:20 | 2020-09-21 08:53 | 9270 | LFUS | 28016 | 3959645842 | 2147 | ENOI | 1 | 30 | EARR | Equipment Failure - Arrestor | N | c phase taken out by bad arrestor in line cleared all arrestors and reenergized line | -90.0832 | 29.9216 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-21 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 85 | 1341065468 | Yes | ORLEANS | FAIR | 130 | 2020-09-21 03:44 | 2020-09-21 04:50 | 2020-09-21 05:54 | 11050 | LFUS | 21407 | 3857446521 | 1554 | ENOI | 1 | 85 | VLGL | Tree/Limb Growing Inside R.O.W. | N | tree | -90.1157 | 29.9407 | Vegetation | Line Fuse | Vegetation | 2020-09-21 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 22 | 1341068232 | Yes | ORLEANS | RAIN | 373 | 2020-09-21 03:49 | 2020-09-21 06:20 | 2020-09-21 10:02 | 8206 | LFUS | 21194 | 4024648351 | 627 | ENOI | 1 | 22 | VLGL | Tree/Limb Growing Inside R.O.W. | N | tree branch took out one phase of lateral | -90.0622 | 29.9903 | Vegetation | Line Fuse | Vegetation | 2020-09-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 94 | 1341065716 | Yes | EAST ORLEANS | FAIR | 521 | 2020-09-21 04:10 | 2020-09-21 09:50 | 2020-09-21 12:51 | 48974 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 94 | EARM | Equipment Failure - Crossarm | N | Refused C phase at 37121 and 27886--Inspected lateral unknown | -90.044 | 29.9708 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-21 | DLIN | C | Council District C | Kristin Palmer | 70117 | 9
2020 | 10 | 1341070216 | Yes | ORLEANS CBD | FAIR | 255 | 2020-09-21 06:54 | 2020-09-21 07:19 | 2020-09-21 11:09 | 2550 | TFUS | 1638453 | 40177464932 | 1826 | ENOI | 4 | 10 | ESEC | Secondary/Service Conductor | N | Open wire secondary getting together took slack out and refused transformers | -90.0648 | 29.9393 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-21 | DLIN | B | Council District B | Jay Banks | 70130 | 9
2020 | 24 | 1341078348 | Yes | EAST ORLEANS | WIND | 118 | 2020-09-21 08:23 | 2020-09-21 08:47 | 2020-09-21 10:21 | 2832 | LFUS | 27946 | 4250149384 | 1607 | ENOI | 6 | 24 | UNKN | Inspected Unknown | N | Refused C phase at 27946 | -89.9906 | 30.0181 | Other | Line Fuse | Other | 2020-09-21 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 9
2020 | 8 | 1341078212 | Yes | EAST ORLEANS | RAIN | 122 | 2020-09-21 08:28 | 2020-09-21 08:28 | 2020-09-21 10:30 | 976 | TFUS | 67435 | 42513493732 | 1607 | ENOI | 6 | 8 | EFLK | Equipment Failure - Fuse Link | N | Jeff Vickner Inspected line and refused lateral. Customer back in lights | -89.99 | 30.0177 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-21 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 9
2020 | 6 | 1341079872 | Yes | ORLEANS | RAIN | 744 | 2020-09-21 08:55 | 2020-09-21 08:55 | 2020-09-21 21:19 | 4464 | DIS | 14456 | 3854349047 | 408 | ENOI | 1 | 6 | EPOL | Equipment Failure - Pole | N | broke pole at pont xway and lane | -90.1155 | 30.0099 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-09-21 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 54 | 1341082283 | Yes | ORLEANS | RAIN | 723 | 2020-09-21 09:10 | 2020-09-21 20:29 | 2020-09-21 21:13 | 39042 | LFUS | 17771 | 3855249253 | 411 | ENOI | 1 | 54 | EPOL | Equipment Failure - Pole | N | broke pole at pont xway and lane | -90.115 | 30.0157 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-21 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 62 | 1341082408 | Yes | ORLEANS | RAIN | 723 | 2020-09-21 09:11 | 2020-09-21 21:00 | 2020-09-21 21:14 | 44826 | LFUS | 17596 | 3846648986 | 410 | ENOI | 1 | 62 | EPOL | Equipment Failure - Pole | N | broke pole at pont xway and lane | -90.1181 | 30.0082 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-21 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 155 | 1341134359 | Yes | ORLEANS | FAIR | 126 | 2020-09-22 00:25 | 2020-09-22 01:24 | 2020-09-22 02:31 | 19530 | LFUS | 27721 | 3942846301 | 1924 | ENOI | 1 | 155 | EARM | Equipment Failure - Crossarm | N | crew repaired broken crossarm | -90.0885 | 29.9342 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-22 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 75 | 1341137921 | Yes | EAST ORLEANS | FAIR | 99 | 2020-09-22 02:56 | 2020-09-22 04:37 | 2020-09-22 04:35 | 7425 | LFUS | 24738 | 4346351051 | 2223 | ENOI | 6 | 75 | UNKN | Inspected Unknown | N |  | -89.9595 | 30.0636 | Other | Line Fuse | Other | 2020-09-22 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 119 | 1341142295 | Yes | ORLEANS | RAIN | 130 | 2020-09-22 07:10 | 2020-09-22 07:10 | 2020-09-22 09:21 | 15470 | LFUS | 21028 | 4025947660 | 614 | ENOI | 1 | 119 | SCHD | Scheduled Interruption | N |  | -90.0618 | 29.9713 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-22 | DLIN | C | Council District C | Kristin Palmer | 70116 | 9
2020 | 7 | 1341147545 | Yes | EAST ORLEANS | RAIN | 14 | 2020-09-22 08:51 | 2020-09-22 08:51 | 2020-09-22 09:05 | 98 | TFUS | 1537915 | 42675493938 | 1604 | ENOI | 6 | 7 | EMER | Emergency Switching | N |  | -89.985 | 30.0183 | Other | Transformer Fuse | Emergency Switching | 2020-09-22 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 9
2020 | 58 | 1341153722 | Yes | EAST ORLEANS | RAIN | 217 | 2020-09-22 10:37 | 2020-09-22 13:13 | 2020-09-22 14:14 | 12586 | LFUS | 32292 | 4065548592 | 1710 | ENOI | 6 | 58 | ASQL | Animal - Squirrel | N | Squirrel caused outage. Refused b phase customers back in lights | -90.0491 | 29.997 | Animal | Line Fuse | Animal | 2020-09-22 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 3 | 1341158050 | Yes | EAST ORLEANS | RAIN | 51 | 2020-09-22 11:54 | 2020-09-22 11:54 | 2020-09-22 12:46 | 153 | TFUS | 57974 | 41070486961 | 616 | ENOI | 6 | 3 | EARM | Equipment Failure - Crossarm | N |  | -90.0359 | 29.9996 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-22 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 1 | 1341179046 | Yes | ORLEANS | FAIR | 127 | 2020-09-22 15:54 | 2020-09-22 15:54 | 2020-09-22 18:01 | 127 | SERV | SERVICE | 38802462232 | 1927 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | changed out service | -90.1085 | 29.9324 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-22 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 6 | 1341177347 | Yes | EAST ORLEANS | FAIR | 160 | 2020-09-22 16:31 | 2020-09-22 16:31 | 2020-09-22 19:11 | 960 | TFUS | 1451615 | 40604473641 | 623 | ENOI | 6 | 6 | UNKN | Inspected Unknown | N |  | -90.0509 | 29.9632 | Other | Transformer Fuse | Other | 2020-09-22 | DLIN | C | Council District C | Kristin Palmer | 70117 | 9
2020 | 70 | 1341177818 | Yes | EAST ORLEANS | FAIR | 190 | 2020-09-22 16:40 | 2020-09-22 19:05 | 2020-09-22 19:50 | 13300 | LFUS | 34334 | 4282950600 | 2215 | ENOI | 6 | 70 | EFLK | Equipment Failure - Fuse Link | N | Refused lateral fuse customer back on | -89.9797 | 30.0515 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-22 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 9
2020 | 110 | 1341178536 | Yes | EAST ORLEANS | FAIR | 107 | 2020-09-22 17:00 | 2020-09-22 18:31 | 2020-09-22 18:47 | 11770 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 110 | VOHL | Overhanging Limb | N | refused | -90.044 | 29.9708 | Vegetation | Line Fuse | Vegetation | 2020-09-22 | DLIN | C | Council District C | Kristin Palmer | 70117 | 9
2020 | 58 | 1341178781 | Yes | EAST ORLEANS | FAIR | 69 | 2020-09-22 17:04 | 2020-09-22 18:06 | 2020-09-22 18:13 | 4002 | LFUS | 32292 | 4065548592 | 1710 | ENOI | 6 | 58 | UNKN | Inspected Unknown | N |  | -90.0491 | 29.997 | Other | Line Fuse | Other | 2020-09-22 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 110 | 1341183098 | Yes | EAST ORLEANS | FAIR | 102 | 2020-09-22 19:09 | 2020-09-22 20:17 | 2020-09-22 20:51 | 11220 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 110 | UNKN | Inspected Unknown | N |  | -90.044 | 29.9708 | Other | Line Fuse | Other | 2020-09-22 | DLIN | C | Council District C | Kristin Palmer | 70117 | 9
2020 | 20 | 1341188719 | Yes | ORLEANS | FAIR | 168 | 2020-09-22 21:42 | 2020-09-22 23:08 | 2020-09-23 00:30 | 3360 | LFUS | 22096 | 3895547006 | 2015 | ENOI | 1 | 20 | EFSW | Equipment Failure - Fuse Switch | N | replaced 2 switches | -90.1033 | 29.9536 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-22 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 40 | 1341188097 | Yes | EAST ORLEANS | FAIR | 42 | 2020-09-22 22:20 | 2020-09-22 22:25 | 2020-09-22 23:03 | 1680 | LFUS | 17119-F | 4154449236 | 1010 | ENOI | 6 | 40 | UNKN | Inspected Unknown | N |  | -90.0207 | 30.0144 | Other | Line Fuse | Other | 2020-09-22 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 1 | 1341188142 | Yes | ORLEANS | FAIR | 82 | 2020-09-22 22:22 | 2020-09-22 22:22 | 2020-09-22 23:44 | 82 | TFUS | 1051894 | 38603471406 | 2015 | ENOI | 1 | 1 | EFSW | Equipment Failure - Fuse Switch | N | Refused blown switch. Tracking | -90.1144 | 29.9577 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-22 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 2 | 1341204338 | Yes | EAST ORLEANS | FAIR | 125 | 2020-09-23 06:11 | 2020-09-23 06:11 | 2020-09-23 08:16 | 250 | LFUS | LFUS | 4341249109 | 1612 | ENOI | 6 | 2 | ASQL | Animal - Squirrel | N |  | -89.9619 | 30.0102 | Animal | Line Fuse | Animal | 2020-09-23 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 9
2020 | 121 | 1341208684 | Yes | ORLEANS | FAIR | 407 | 2020-09-23 07:38 | 2020-09-23 11:59 | 2020-09-23 14:25 | 49247 | LFUS | 38136 | 4032947665 | 614 | ENOI | 1 | 121 | SCHD | Scheduled Interruption | N |  | -90.0595 | 29.9714 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-23 | DLIN | C | Council District C | Kristin Palmer | 70116 | 9
2020 | 54 | 1341210114 | Yes | ORLEANS | FAIR | 184 | 2020-09-23 07:55 | 2020-09-23 07:58 | 2020-09-23 10:59 | 9936 | LFUS | 21068 | 3885546539 | 1916 | ENOI | 1 | 54 | SCHD | Scheduled Interruption | N |  | -90.1067 | 29.9411 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-23 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 18 | 1341211257 | Yes | ORLEANS | FAIR | 189 | 2020-09-23 08:11 | 2020-09-23 08:11 | 2020-09-23 11:20 | 3402 | LFUS | 37688 | 3825845872 | 2013 | ENOI | 1 | 18 | SCHD | Scheduled Interruption | N |  | -90.1259 | 29.9228 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 3 | 1341211334 | Yes | EAST ORLEANS | RAIN | 375 | 2020-09-23 08:16 | 2020-09-23 08:16 | 2020-09-23 14:31 | 1125 | TFUS | 569576 | 43384505392 | 2214 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N |  | -89.962 | 30.0495 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-23 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 2 | 1341213065 | Yes | ORLEANS | RAIN | 119 | 2020-09-23 08:46 | 2020-09-23 08:46 | 2020-09-23 10:45 | 238 | TFUS | 1138914 | 38420496027 | 409 | ENOI | 1 | 2 | ECON | Equipment Failure - Connector / Sleeve | N | riser came out top of transformer | -90.1191 | 30.0251 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-23 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 12 | 1341217836 | Yes | ORLEANS | RAIN | 82 | 2020-09-23 09:58 | 2020-09-23 09:58 | 2020-09-23 11:20 | 984 | TFUS | 72502 | 38772480789 | 903 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N |  | -90.1088 | 29.9834 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-23 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 1 | 1341219649 | Yes | EAST ORLEANS | RAIN | 61 | 2020-09-23 10:29 | 2020-09-23 10:29 | 2020-09-23 11:30 | 61 | LFUS | 21989 | 4069547843 | 623 | ENOI | 6 | 1 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | repairs made ballons on wires | -90.048 | 29.9761 | Other | Line Fuse | Other | 2020-09-23 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 336 | 1341223311 | Yes | ORLEANS | RAIN | 139 | 2020-09-23 11:11 | 2020-09-23 12:13 | 2020-09-23 13:30 | 46704 | LFUS | 93123 | 3826846870 | 2015 | ENOI | 1 | 336 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Limb fell across t former switch blowing all the laterals repaired riser | -90.1251 | 29.9501 | Vegetation | Line Fuse | Vegetation | 2020-09-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 84 | 1341240056 | Yes | ORLEANS | THDR | 234 | 2020-09-23 11:28 | 2020-09-23 14:52 | 2020-09-23 15:23 | 19656 | LFUS | 21407 | 3857446521 | 1554 | ENOI | 1 | 84 | LGHT | Lightning | N | broken crossarm insulator tracking on arrestor bracket | -90.1157 | 29.9407 | Lightning | Line Fuse | Lightning | 2020-09-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 21 | 1341229031 | Yes | EAST ORLEANS | FAIR | 150 | 2020-09-23 12:10 | 2020-09-23 12:19 | 2020-09-23 14:40 | 3150 | LFUS | 27844 | 4360949602 | 1601 | ENOI | 6 | 21 | EARR | Equipment Failure - Arrestor | N |  | -89.9554 | 30.0237 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-23 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 7 | 1341230590 | Yes | ORLEANS | RAIN | 65 | 2020-09-23 12:55 | 2020-09-23 12:55 | 2020-09-23 14:00 | 455 | TFUS | 72360 | 38961484300 | 904 | ENOI | 1 | 7 | ESEC | Secondary/Service Conductor | N | secondary down | -90.1027 | 29.993 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-23 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 11 | 1341234611 | Yes | ORLEANS | FAIR | 66 | 2020-09-23 13:19 | 2020-09-23 13:19 | 2020-09-23 14:25 | 726 | TFUS | 55909 | 39085464704 | 1916 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | work completed | -90.0996 | 29.939 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-23 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 12 | 1341262882 | Yes | ORLEANS | FAIR | 68 | 2020-09-23 20:37 | 2020-09-23 21:08 | 2020-09-23 21:45 | 816 | TFUS | 500014 | 38013469200 | B0526 | ENOI | 1 | 12 | EFLK | Equipment Failure - Fuse Link | N | palm took out transformer trimmed tree and refused ok | -90.133 | 29.9517 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-23 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 15 | 1341269726 | Yes | ORLEANS | FAIR | 50 | 2020-09-24 00:25 | 2020-09-24 00:44 | 2020-09-24 01:15 | 750 | TFUS | 64986 | 38766468898 | 1916 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1092 | 29.9506 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-24 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 9
2020 | 11 | 1341272246 | Yes | ORLEANS | RAIN | 71 | 2020-09-24 01:44 | 2020-09-24 02:14 | 2020-09-24 02:55 | 781 | TFUS | 1001044 | 4003746396 | 2137 | ENOI | 1 | 11 | EFLK | Equipment Failure - Fuse Link | N | refused ok taken out by guy wire | -90.0692 | 29.9367 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-24 | DLIN | B | Council District B | Jay Banks | 70130 | 9
2020 | 38 | 1341287299 | Yes | EAST ORLEANS | FAIR | 60 | 2020-09-24 09:17 | 2020-09-24 09:56 | 2020-09-24 10:17 | 2280 | LFUS | 27874 | 4169347325 | 2346 | ENOI | 6 | 38 | ASQL | Animal - Squirrel | N | Had to refuse B and C phase due to squirrel | -90.0167 | 29.9617 | Animal | Line Fuse | Animal | 2020-09-24 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 9
2020 | 19 | 1341291928 | Yes | ORLEANS | FAIR | 221 | 2020-09-24 10:20 | 2020-09-24 10:20 | 2020-09-24 14:01 | 4199 | TFUS | 31261 | 38380466917 | 2013 | ENOI | 1 | 19 | SCHD | Scheduled Interruption | N | crew making repairs | -90.1217 | 29.9454 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-09-24 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 1 | 1341297794 | Yes | ORLEANS | FAIR | 102 | 2020-09-24 12:25 | 2020-09-24 12:25 | 2020-09-24 14:07 | 102 | TFUS | 18908 | 38425495018 | 409 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | repaired connections at transformer advised customer | -90.1192 | 30.0225 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-24 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 9
2020 | 1 | 1341327687 | Yes | ORLEANS | FAIR | 132 | 2020-09-25 06:34 | 2020-09-25 06:42 | 2020-09-25 08:46 | 132 | SERV | SERVICE | 40178487855 | 1704 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | Meter open | -90.0641 | 30.0023 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-25 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 1 | 1341334509 | Yes | ORLEANS | FAIR | 216 | 2020-09-25 09:23 | 2020-09-25 09:23 | 2020-09-25 12:59 | 216 | SERV | SERVICE | 38485458234 | 1926 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad connection at weatherhead | -90.1185 | 29.9215 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-25 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 9
2020 | 14 | 1341351573 | Yes | ORLEANS | FAIR | 86 | 2020-09-25 14:42 | 2020-09-25 14:42 | 2020-09-25 16:08 | 1204 | TFUS | 63426 | 39379463749 | 1924 | ENOI | 1 | 14 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons in feeder removed refused tf | -90.0901 | 29.9364 | Other | Transformer Fuse | Other | 2020-09-25 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 52 | 1341364270 | Yes | EAST ORLEANS | FAIR | 66 | 2020-09-25 23:00 | 2020-09-25 23:34 | 2020-09-26 00:06 | 3432 | LFUS | 27893 | 4082548786 | 625 | ENOI | 6 | 52 | EARR | Equipment Failure - Arrestor | N | cleared arrestor at the end of tap and closed in b phase lateral | -90.0435 | 30.0021 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-25 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 5 | 1341372112 | Yes | EAST ORLEANS | FAIR | 75 | 2020-09-26 07:26 | 2020-09-26 07:35 | 2020-09-26 08:41 | 375 | TFUS | 3010824 | 40848487656 | 625 | ENOI | 6 | 5 | EFLK | Equipment Failure - Fuse Link | N | Refused pot, may have blown due to weather. Lights back on | -90.0429 | 30.0017 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-26 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 1 | 1341372166 | Yes | ORLEANS | FAIR | 98 | 2020-09-26 07:31 | 2020-09-26 07:35 | 2020-09-26 09:09 | 98 | SERV | SERVICE | 39528458748 | 1911 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | Replaced burned servuce | -90.0856 | 29.9225 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-26 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 160 | 1341374539 | Yes | EAST ORLEANS | RAIN | 185 | 2020-09-26 07:55 | 2020-09-26 10:51 | 2020-09-26 11:00 | 29600 | LFUS | 36451 | 4342550013 | 1605 | ENOI | 6 | 160 | EARM | Equipment Failure - Crossarm | N | Crossarm broken on dwyer. C. S (612) has the information | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-26 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 9
2020 | 11 | 1341373113 | Yes | EAST ORLEANS | FAIR | 92 | 2020-09-26 07:59 | 2020-09-26 08:05 | 2020-09-26 09:31 | 1012 | TFUS | 1493239 | 40739478928 | 622 | ENOI | 6 | 11 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | Had to refuse b phase on lateral due to pole guard contacting a jumper. Customers back in lights | -90.0464 | 29.9776 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-09-26 | DLIN | D | Council District D | Jared Brossett | 70117 | 9
2020 | 137 | 1341392461 | Yes | ORLEANS | FAIR | 241 | 2020-09-26 10:00 | 2020-09-26 14:44 | 2020-09-26 14:01 | 33017 | LFUS | 21455 | 3935745789 | 1922 | ENOI | 1 | 137 | SCHD | Scheduled Interruption | N | crew replacing pole | -90.0909 | 29.9201 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-26 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 10 | 1341414251 | Yes | ORLEANS | FAIR | 125 | 2020-09-26 16:38 | 2020-09-26 16:39 | 2020-09-26 18:43 | 1250 | XFMR | 528713 | 38395460487 | 1926 | ENOI | 1 | 10 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.1212 | 29.9276 | Equipment Failure | Transformer | Equipment Failure | 2020-09-26 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 44 | 1341419774 | Yes | ORLEANS | FAIR | 97 | 2020-09-26 18:55 | 2020-09-26 19:57 | 2020-09-26 20:32 | 4268 | LFUS | 21524 | 3899847894 | 911 | ENOI | 1 | 44 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned open everyone back in lights | -90.1016 | 29.9781 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-26 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 9
2020 | 1 | 1341421456 | Yes | EAST ORLEANS | FAIR | 116 | 2020-09-26 21:02 | 2020-09-26 21:08 | 2020-09-26 22:59 | 116 | SERV | SERVICE | 42409493034 | 1607 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N |  | -89.9933 | 30.0159 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-26 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 9
2020 | 1 | 1341430243 | Yes | ORLEANS | FAIR | 175 | 2020-09-27 07:20 | 2020-09-27 07:20 | 2020-09-27 10:15 | 175 | SERV | SERVICE | 40224490229 | 512 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Replaced connectors at house | -90.0625 | 30.0088 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-27 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 1 | 1341431194 | Yes | ORLEANS | FAIR | 182 | 2020-09-27 08:14 | 2020-09-27 08:14 | 2020-09-27 11:16 | 182 | SERV | SERVICE | 38818468278 | 2015 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Change connection | -90.1077 | 29.949 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-27 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 9
2020 | 1 | 1341431544 | Yes | EAST ORLEANS | FAIR | 160 | 2020-09-27 08:43 | 2020-09-27 08:46 | 2020-09-27 11:23 | 160 | SERV | SERVICE | 41815491458 | 1612 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Had to run new service Customer back in lights. Upgrading to 1/0 service | -90.0121 | 30.0117 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-27 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 9
2020 | 194 | 1341439577 | Yes | EAST ORLEANS | FAIR | 173 | 2020-09-27 14:17 | 2020-09-27 16:15 | 2020-09-27 17:10 | 33562 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 194 | EPRI | Equipment Failure - Primary Conductor | N | bad span of cable serrviceman switced out and restored bp s (pwd) | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-27 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 9
2020 | 97 | 1341480456 | Yes | ORLEANS | FAIR | 59 | 2020-09-28 10:02 | 2020-09-28 10:02 | 2020-09-28 11:01 | 5723 | LFUS | 28028 | 3881346534 | 1916 | ENOI | 1 | 97 | EMER | Emergency Switching | N | opened for safety to replace x arm | -90.1081 | 29.9409 | Other | Line Fuse | Emergency Switching | 2020-09-28 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 1 | 1341508095 | Yes | EAST ORLEANS | FAIR | 59 | 2020-09-28 15:02 | 2020-09-28 15:02 | 2020-09-28 16:01 | 59 | TFUS | 73834 | 41794477095 | 2325 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | vines in transformer | -90.0132 | 29.9723 | Vegetation | Transformer Fuse | Vegetation | 2020-09-28 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 9
2020 | 11 | 1341516726 | Yes | ORLEANS | FAIR | 157 | 2020-09-28 16:24 | 2020-09-28 16:25 | 2020-09-28 19:01 | 1727 | TFUS | 59095 | 39847474995 | 1512 | ENOI | 1 | 11 | ASQL | Animal - Squirrel | N | taken out by squirrel refused ok | -90.075 | 29.9671 | Animal | Transformer Fuse | Animal | 2020-09-28 | DLIN | D | Council District D | Jared Brossett | 70116 | 9
2020 | 1 | 1341522499 | Yes | ORLEANS | FAIR | 37 | 2020-09-28 17:08 | 2020-09-28 17:08 | 2020-09-28 17:46 | 37 | SERV | SERVICE | 39418468154 | 1554 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.0887 | 29.9485 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-28 | DLIN | B | Council District B | Jay Banks | 70125 | 9
2020 | 110 | 1341534162 | Yes | EAST ORLEANS | FAIR | 102 | 2020-09-28 23:31 | 2020-09-28 23:31 | 2020-09-29 01:13 | 11220 | DIS | 25241 | 4106948783 | 616 | ENOI | 6 | 110 | EPOL | Equipment Failure - Pole | N |  | -90.0359 | 30.0019 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-09-28 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 71 | 1341534424 | Yes | EAST ORLEANS | FAIR | 141 | 2020-09-28 23:31 | 2020-09-29 00:57 | 2020-09-29 01:52 | 10011 | DIS | 25242 | 4085648451 | 616 | ENOI | 6 | 71 | EPOL | Equipment Failure - Pole | N |  | -90.0429 | 29.9931 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-09-28 | DLIN | D | Council District D | Jared Brossett | 70126 | 9
2020 | 21 | 1341560670 | Yes | EAST ORLEANS | FAIR | 115 | 2020-09-29 14:09 | 2020-09-29 15:17 | 2020-09-29 16:04 | 2415 | LFUS | 80286 | 4168650033 | 2212 | ENOI | 6 | 21 | EFSW | Equipment Failure - Fuse Switch | N | Riser came out top of switch use stick to put new riser in top switch | -90.0161 | 30.0361 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-29 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 9
2020 | 1 | 1341576165 | Yes | ORLEANS | FAIR | 38 | 2020-09-29 20:54 | 2020-09-29 20:54 | 2020-09-29 21:32 | 38 | SERV | SERVICE | 37970469514 | 2014 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | Had to change meter can t get in touch with amoc new AM14085570 serial 160348221 rd 00000 | -90.1346 | 29.9526 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 1 | 1341577986 | Yes | ORLEANS | FAIR | 36 | 2020-09-29 22:49 | 2020-09-29 22:49 | 2020-09-29 23:25 | 36 | SERV | SERVICE | 38362472742 | 2016 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Part lights bad connections at pole | -90.122 | 29.9613 | Equipment Failure | Service Conductor | Equipment Failure | 2020-09-29 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 9
2020 | 132 | 1341587245 | Yes | ORLEANS | FAIR | 136 | 2020-09-30 03:04 | 2020-09-30 04:15 | 2020-09-30 05:20 | 17952 | LFUS | 27738 | 3844747103 | 2015 | ENOI | 1 | 132 | VLGL | Tree/Limb Growing Inside R.O.W. | N | 2521 fern TOL hw | -90.1194 | 29.9565 | Vegetation | Line Fuse | Vegetation | 2020-09-30 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 9
2020 | 1448 | 1341594100 | Yes | ORLEANS | FAIR | 17 | 2020-09-30 08:49 | 2020-09-30 09:06 | 2020-09-30 09:06 | 24616 | SBKR | 1554 | 3950246993 | 1554 | ENOI | 1 | 1448 | UNKN | Inspected Unknown | N |  | -90.086 | 29.9532 | Other | Substation Breaker | Other | 2020-09-30 | DLIN | B | Council District B | Jay Banks | 70113 | 9
2020 | 92 | 1341594696 | Yes | EAST ORLEANS | FAIR | 170 | 2020-09-30 09:00 | 2020-09-30 11:26 | 2020-09-30 11:51 | 15640 | LFUS | 17806 | 4049749130 | 502 | ENOI | 6 | 92 | SCHD | Scheduled Interruption | N | lfuse out to make repairs | -90.0537 | 30.0117 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-09-30 | DLIN | D | Council District D | Jared Brossett | 70122 | 9
2020 | 260 | 1341598923 | Yes | ORLEANS | FAIR | 86 | 2020-09-30 10:05 | 2020-09-30 11:09 | 2020-09-30 11:31 | 22360 | LFUS | 27862 | 3863946745 | 1916 | ENOI | 1 | 260 | EFSW | Equipment Failure - Fuse Switch | N | Lateral sw 27862 failed replaced switch | -90.1135 | 29.9468 | Equipment Failure | Line Fuse | Equipment Failure | 2020-09-30 | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 9
2020 | 1 | 1341619575 | Yes | ORLEANS | FAIR | 142 | 2020-09-30 17:37 | 2020-09-30 17:37 | 2020-09-30 19:59 | 142 | SECO | SERVICE | 39277457273 | 1922 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | Conductor was melted together. Made repairs to service wire. | -90.0937 | 29.9186 | Equipment Failure | Secondary Conductor | Equipment Failure | 2020-09-30 | DLIN | B | Council District B | Jay Banks | 70115 | 9
2020 | 28 | 1341630879 | Yes | ORLEANS | FAIR | 40 | 2020-10-01 08:02 | 2020-10-01 08:02 | 2020-10-01 08:42 | 1120 | TFUS | 30968 | 39006457323 | 1912 | ENOI | 1 | 28 | SCHD | Scheduled Interruption | N | Contractor working on pole | -90.1021 | 29.9187 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-01 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 32 | 1341633941 | Yes | EAST ORLEANS | FAIR | 155 | 2020-10-01 08:50 | 2020-10-01 09:16 | 2020-10-01 11:25 | 4960 | LFUS | 17516 | 4038149069 | 502 | ENOI | 6 | 32 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0575 | 30.0101 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-01 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 7 | 1341635082 | Yes | EAST ORLEANS | FAIR | 171 | 2020-10-01 09:24 | 2020-10-01 09:24 | 2020-10-01 12:15 | 1197 | LFUS | 87012 | 4218447758 | 2345 | ENOI | 6 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0009 | 29.9733 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-01 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 10
2020 | 5 | 1341638874 | Yes | ORLEANS | FAIR | 278 | 2020-10-01 10:53 | 2020-10-01 10:53 | 2020-10-01 15:32 | 1390 | TFUS | 21052 | 38993493407 | 402 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | Switched out feeder to change feeder arm out broken arm | -90.1012 | 30.0178 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-01 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 2 | 1341641989 | Yes | ORLEANS | FAIR | 91 | 2020-10-01 11:41 | 2020-10-01 11:41 | 2020-10-01 13:12 | 182 | TFUS | 72291 | 38713481932 | 2011 | ENOI | 1 | 2 | EONE | Equipment Failure - Neutral / Shield Conductor | N | Broken neutral on pole repaired | -90.1104 | 29.9865 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-01 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 3 | 1341659959 | Yes | ORLEANS | FAIR | 74 | 2020-10-01 18:23 | 2020-10-01 18:23 | 2020-10-01 19:37 | 222 | TFUS | 27450 | 38424495165 | 409 | ENOI | 1 | 3 | ASQL | Animal - Squirrel | N | Taken out by squirrel clearedcrefused ok | -90.1192 | 30.0229 | Animal | Transformer Fuse | Animal | 2020-10-01 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 9 | 1341662110 | Yes | ORLEANS | FAIR | 79 | 2020-10-01 18:47 | 2020-10-01 19:27 | 2020-10-01 20:06 | 711 | TFUS | 548318 | 38068466523 | B0527 | ENOI | 1 | 9 | ASQL | Animal - Squirrel | N | Squirrell took out transformer. Refused and threw back in. | -90.1313 | 29.9442 | Animal | Transformer Fuse | Animal | 2020-10-01 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 6 | 1341682844 | Yes | EAST ORLEANS | FAIR | 72 | 2020-10-02 08:58 | 2020-10-02 08:58 | 2020-10-02 10:10 | 432 | TFUS | 73851 | 41450472851 | 2346 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0245 | 29.9608 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-02 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 10
2020 | 15 | 1341685939 | Yes | EAST ORLEANS | FAIR | 19 | 2020-10-02 10:26 | 2020-10-02 10:30 | 2020-10-02 10:46 | 285 | TFUS | 56111 | 40720489548 | 1702 | ENOI | 6 | 15 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0467 | 30.0068 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-02 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 21 | 1341688762 | Yes | ORLEANS | FAIR | 156 | 2020-10-02 12:09 | 2020-10-02 12:09 | 2020-10-02 14:45 | 3276 | TFUS | 1002436 | 39908465550 | 2137 | ENOI | 1 | 21 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0734 | 29.941 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-02 | DLIN | B | Council District B | Jay Banks | 70130 | 10
2020 | 7 | 1341713349 | Yes | ORLEANS | FAIR | 236 | 2020-10-03 09:04 | 2020-10-03 10:41 | 2020-10-03 13:00 | 1652 | TFUS | 16496 | 39878490708 | 512 | ENOI | 1 | 7 | ASQL | Animal - Squirrel | N | squirrel took out transformer refused good | -90.0736 | 30.0102 | Animal | Transformer Fuse | Animal | 2020-10-03 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 7 | 1341719731 | Yes | EAST ORLEANS | FAIR | 163 | 2020-10-03 14:31 | 2020-10-03 14:31 | 2020-10-03 17:14 | 1141 | TFUS | 76230 | 43648497558 | 1601 | ENOI | 6 | 7 | ASQL | Animal - Squirrel | N | Cleared squirrel and refused transformer | -89.9542 | 30.0279 | Animal | Transformer Fuse | Animal | 2020-10-03 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 66 | 1341721328 | Yes | ORLEANS | FAIR | 98 | 2020-10-03 16:12 | 2020-10-03 16:38 | 2020-10-03 17:50 | 6468 | LFUS | 27945 | 3920748012 | 904 | ENOI | 1 | 66 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons | -90.0951 | 29.9812 | Other | Line Fuse | Other | 2020-10-03 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 13 | 1341734126 | Yes | ORLEANS | FAIR | 296 | 2020-10-04 07:30 | 2020-10-04 07:30 | 2020-10-04 12:26 | 3848 | TFUS | 718130 | 40257475488 | 614 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0619 | 29.9682 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-04 | DLIN | C | Council District C | Kristin Palmer | 70116 | 10
2020 | 1 | 1341744169 | Yes | ORLEANS | FAIR | 152 | 2020-10-04 10:38 | 2020-10-04 10:53 | 2020-10-04 13:10 | 152 | SECO | SECONDARY COND | 38208473188 | 2022 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | repaired conection at pole | -90.1268 | 29.9626 | Equipment Failure | Secondary Conductor | Equipment Failure | 2020-10-04 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 32 | 1341766810 | Yes | ORLEANS | FAIR | 305 | 2020-10-05 08:00 | 2020-10-05 08:00 | 2020-10-05 13:05 | 9760 | LFUS | 21511 | 3909746426 | 1925 | ENOI | 1 | 32 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0993 | 29.9378 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-05 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 185 | 1341769558 | Yes | ORLEANS | FAIR | 191 | 2020-10-05 09:40 | 2020-10-05 09:40 | 2020-10-05 12:51 | 35335 | LFUS | 27892 | 3834945923 | 1914 | ENOI | 1 | 185 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1227 | 29.9241 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 8 | 1341770525 | Yes | ORLEANS | FAIR | 70 | 2020-10-05 10:08 | 2020-10-05 10:21 | 2020-10-05 11:19 | 560 | TFUS | 73749 | 39960488721 | 1704 | ENOI | 1 | 8 | EFSW | Equipment Failure - Fuse Switch | N | fuse was blown; refused transformer | -90.0708 | 30.0046 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-05 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1 | 1341775504 | Yes | ORLEANS | FAIR | 656 | 2020-10-05 12:35 | 2020-10-05 17:07 | 2020-10-05 23:31 | 656 | SERV | SERVICE | 38356464843 | 2024 | ENOI | 1 | 1 | SLAK | Slack Conductor / Loose Connection | N | bad connection at pole | -90.1225 | 29.9395 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-05 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 53 | 1341780844 | Yes | ORLEANS | FAIR | 65 | 2020-10-05 14:00 | 2020-10-05 14:00 | 2020-10-05 15:05 | 3551 | DIS | 24742 | 4029549045 | 1701 | ENOI | 1 | 53 | VHCL | Vehicle | N | vehicle hit pole at intersection of sumpter and elysian fields; wire down and crossarms broken RELATED TO TKT#1341779380, 1341780117, 1341779794 (A.STEWART) | -90.0602 | 30.0094 | Public Damage | Disconnect Switch | Public Damage | 2020-10-05 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 5 | 1341780117 | Yes | ORLEANS | FAIR | 584 | 2020-10-05 14:00 | 2020-10-05 20:48 | 2020-10-05 23:44 | 2920 | DIS | 24418 | 4031248821 | 1701 | ENOI | 1 | 5 | VHCL | Vehicle | N | vehicle hit pole at intersection of sumpter and elysian fields; wire down and crossarms broken RELSTED TO TKT#1341779380, 1341780844, 1341779794 (A.STEWART) | -90.0597 | 30.0033 | Public Damage | Disconnect Switch | Public Damage | 2020-10-05 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 22 | 1341779380 | Yes | ORLEANS | FAIR | 37 | 2020-10-05 14:00 | 2020-10-05 14:13 | 2020-10-05 14:38 | 814 | SBKR | 1701 | 4024448723 | 1701 | ENOI | 1 | 22 | VHCL | Vehicle | N | vehicle hit pole at intersection of sumpter and elysian fields; wire down and crossarms broken HW. RELATED TO TKT#1341780844, 1341780117, 1341779794 (A.STEWART) | -90.062 | 30.0006 | Public Damage | Substation Breaker | Public Damage | 2020-10-05 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1786 | 1341789315 | NO | ORLEANS | FAIR | 78 | 2020-10-05 17:58 | 2020-10-05 19:13 | 2020-10-05 19:16 | 139308 | TRAN | 1712 | 4023848726 | 1712 | ENOI | 1 | 1786 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.0622 | 30.0007 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1421 | 1341789476 | NO | ORLEANS | FAIR | 78 | 2020-10-05 17:58 | 2020-10-05 19:06 | 2020-10-05 19:16 | 110838 | TRAN | 1711 | 4024048726 | 1711 | ENOI | 1 | 1421 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.0621 | 30.0007 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 2028 | 1341790197 | NO | EAST ORLEANS | FAIR | 78 | 2020-10-05 17:58 | 2020-10-05 19:18 | 2020-10-05 19:17 | 158184 | TRAN | 1710 | 4024148723 | 1710 | ENOI | 6 | 2028 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.0621 | 30.0006 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 129 | 1341790334 | NO | ORLEANS | FAIR | 78 | 2020-10-05 17:58 | 2020-10-05 18:42 | 2020-10-05 19:16 | 10062 | TRAN | 1713 | 4023548725 | 1713 | ENOI | 1 | 129 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.0623 | 30.0006 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 22 | 1341789173 | NO | ORLEANS | FAIR | 122 | 2020-10-05 17:58 | 2020-10-05 19:22 | 2020-10-05 20:00 | 2684 | TRAN | 1701 | 4024448723 | 1701 | ENOI | 1 | 22 | PVTR | Potential/Voltage Transformer | N | Potential Transformer failure , all customers restored thru field switching | -90.062 | 30.0006 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1494 | 1341789281 | NO | EAST ORLEANS | FAIR | 122 | 2020-10-05 17:58 | 2020-10-05 19:06 | 2020-10-05 20:00 | 182268 | TRAN | 1708 | 4024448726 | 1708 | ENOI | 6 | 1494 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.062 | 30.0007 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1926 | 1341790104 | NO | ORLEANS | FAIR | 122 | 2020-10-05 17:58 | 2020-10-05 19:56 | 2020-10-05 20:00 | 234972 | TRAN | 1704 | 4023848723 | 1704 | ENOI | 1 | 1926 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.0622 | 30.0006 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1462 | 1341790810 | NO | EAST ORLEANS | FAIR | 122 | 2020-10-05 17:58 | 2020-10-05 19:59 | 2020-10-05 20:00 | 178364 | TRAN | 1702 | 4024148726 | 1702 | ENOI | 6 | 1462 | PVTR | Potential/Voltage Transformer | N | Potential Xfmr failed | -90.0621 | 30.0007 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 2169 | 1341790889 | NO | ORLEANS | FAIR | 122 | 2020-10-05 17:58 | 2020-10-05 19:52 | 2020-10-05 20:00 | 264618 | TRAN | 1703 | 4024048723 | 1703 | ENOI | 1 | 2169 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.0621 | 30.0006 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1022 | 1341791289 | NO | ORLEANS | FAIR | 122 | 2020-10-05 17:58 | 2020-10-05 19:55 | 2020-10-05 20:00 | 124684 | TRAN | 1705 | 4023648723 | 1705 | ENOI | 1 | 1022 | PVTR | Potential/Voltage Transformer | N | Substation Transformer - Potential / Voltage | -90.0623 | 30.0006 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 2116 | 1341790897 | NO | EAST ORLEANS | FAIR | 122 | 2020-10-05 17:58 | 2020-10-05 20:08 | 2020-10-05 20:00 | 258152 | TRAN | 1709 | 4024348726 | 1709 | ENOI | 6 | 2116 | SEOT | Substation Equipment Other (Describe in remarks) | N | Substation Equipment Other | -90.0621 | 30.0007 | Equipment Failure | Transmission | Equipment Failure | 2020-10-05 | TLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 19 | 1341804358 | Yes | ORLEANS | FAIR | 251 | 2020-10-06 05:35 | 2020-10-06 05:35 | 2020-10-06 09:46 | 4769 | LFUS | 21037 | 4042447372 | 614 | ENOI | 1 | 19 | SCHD | Scheduled Interruption | N | planned outage | -90.0566 | 29.9635 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-06 | DLIN | C | Council District C | Kristin Palmer | 70116 | 10
2020 | 54 | 1341805846 | Yes | ORLEANS | FAIR | 321 | 2020-10-06 07:49 | 2020-10-06 07:49 | 2020-10-06 13:10 | 17334 | LFUS | 21517 | 3906446476 | 1925 | ENOI | 1 | 54 | SCHD | Scheduled Interruption | N | Scheduled Interruption, allen slammens with Pike Electric scheduled outage till 3:00 PM | -90.1001 | 29.9394 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-06 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 41 | 1341806723 | Yes | EAST ORLEANS | FAIR | 120 | 2020-10-06 08:25 | 2020-10-06 08:25 | 2020-10-06 10:25 | 4920 | LFUS | 17858 | 4047049301 | 506 | ENOI | 6 | 41 | SCHD | Scheduled Interruption | N | Scheduled Interruption, joey tatman | -90.0548 | 30.0161 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 5 | 1341806828 | Yes | EAST ORLEANS | FAIR | 209 | 2020-10-06 08:27 | 2020-10-06 08:27 | 2020-10-06 11:56 | 1045 | TFUS | 80351 | 43508508346 | 2217 | ENOI | 6 | 5 | SCHD | Scheduled Interruption | N |  | -89.9581 | 30.0575 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-06 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 48 | 1341807407 | Yes | ORLEANS | FAIR | 77 | 2020-10-06 08:44 | 2020-10-06 08:56 | 2020-10-06 10:01 | 3696 | LFUS | 27636 | 39960488721 | 1704 | ENOI | 1 | 48 | EFLK | Equipment Failure - Fuse Link | N | Refused lateral 27636 looked clear | -90.0708 | 30.0046 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-06 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 135 | 1341828716 | Yes | ORLEANS | FAIR | 256 | 2020-10-06 19:08 | 2020-10-06 22:10 | 2020-10-06 23:24 | 34560 | LFUS | 36896 | 3922547409 | 912 | ENOI | 1 | 135 | EARM | Equipment Failure - Crossarm | N | Broken crossarm changed out | -90.0945 | 29.9647 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-06 | DLIN | B | Council District B | Jay Banks | 70119 | 10
2020 | 20 | 1341842812 | Yes | ORLEANS | FAIR | 60 | 2020-10-07 09:00 | 2020-10-07 09:10 | 2020-10-07 10:00 | 1200 | LFUS | 33642 | 3853646279 | 1926 | ENOI | 1 | 20 | SCHD | Scheduled Interruption | N | changing 3 poles, scheduled outage | -90.117 | 29.9339 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-07 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 10
2020 | 119 | 1341843333 | Yes | ORLEANS | FAIR | 60 | 2020-10-07 09:00 | 2020-10-07 09:15 | 2020-10-07 10:01 | 7140 | LFUS | 21028 | 4025947660 | 614 | ENOI | 1 | 119 | SCHD | Scheduled Interruption | N | schduled outage for woody washington crew 504-329-2633 changing 3 poles | -90.0618 | 29.9713 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-07 | DLIN | C | Council District C | Kristin Palmer | 70116 | 10
2020 | 78 | 1341843328 | Yes | EAST ORLEANS | FAIR | 121 | 2020-10-07 09:00 | 2020-10-07 09:15 | 2020-10-07 11:01 | 9438 | LFUS | 37123 | 4056947641 | 614 | ENOI | 6 | 78 | SCHD | Scheduled Interruption | N | schduled outage for woody washington crew | -90.0522 | 29.9708 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-07 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 2083 | 1341857823 | NO | ORLEANS | FAIR | 16 | 2020-10-07 13:45 | 2020-10-07 14:13 | 2020-10-07 14:01 | 33328 | TRAN | 912 | 3898247404 | 912 | ENOI | 1 | 2083 | UNKI | Unknown - Under Investigation | N |  | -90.1023 | 29.9647 | Other | Transmission | Other | 2020-10-07 | TLIN | B | Council District B | Jay Banks | 70119 | 10
2020 | 2064 | 1341858056 | NO | ORLEANS | FAIR | 16 | 2020-10-07 13:45 | 2020-10-07 14:12 | 2020-10-07 14:01 | 33024 | TRAN | 911 | 3898147405 | 911 | ENOI | 1 | 2064 | UNKI | Unknown - Under Investigation | N |  | -90.1024 | 29.9647 | Other | Transmission | Other | 2020-10-07 | TLIN | B | Council District B | Jay Banks | 70119 | 10
2020 | 35 | 1341870875 | Yes | EAST ORLEANS | FAIR | 284 | 2020-10-07 17:47 | 2020-10-07 21:54 | 2020-10-07 22:31 | 9940 | LFUS | 26058 | 4328650129 | 1605 | ENOI | 6 | 35 | EPRI | Equipment Failure - Primary Conductor | N | bad casle | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-07 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 44 | 1341880059 | Yes | EAST ORLEANS | FAIR | 179 | 2020-10-08 03:22 | 2020-10-08 03:31 | 2020-10-08 06:21 | 7876 | LFUS | 21799 | 4397251427 | 2217 | ENOI | 6 | 44 | EFSW | Equipment Failure - Fuse Switch | N | Refused C phase at lateral sw # 21799 and lateral sw # 95373--Changed bad switch at 95373--27108 not blown | -89.9432 | 30.0738 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-08 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 661 | 1341892385 | Yes | ORLEANS | FAIR | 97 | 2020-10-08 12:03 | 2020-10-08 12:03 | 2020-10-08 13:40 | 64117 | DIS | 24095 | 3908347374 | 2025 | ENOI | 1 | 661 | EPRI | Equipment Failure - Primary Conductor | N | burnt jumper | -90.0992 | 29.9639 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-10-08 | DLIN | B | Council District B | Jay Banks | 70119 | 10
2020 | 10 | 1341893155 | Yes | EAST ORLEANS | FAIR | 152 | 2020-10-08 12:38 | 2020-10-08 12:38 | 2020-10-08 15:10 | 1520 | TFUS | 1546336 | 41037495184 | 1001 | ENOI | 6 | 10 | VHCL | Vehicle | N | Dump truck hit service drop while unloading sand. Contractor not on site. Repaired #4 service drop mid span. Dmorehead | -90.0365 | 30.0222 | Public Damage | Transformer Fuse | Public Damage | 2020-10-08 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 4 | 1341900103 | Yes | ORLEANS | FAIR | 36 | 2020-10-08 15:24 | 2020-10-08 15:24 | 2020-10-08 16:00 | 144 | TFUS | 15071 | 38719491186 | 411 | ENOI | 1 | 4 | ASQL | Animal - Squirrel | N | refused | -90.1101 | 30.0118 | Animal | Transformer Fuse | Animal | 2020-10-08 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 4 | 1341901495 | Yes | ORLEANS | FAIR | 73 | 2020-10-08 16:18 | 2020-10-08 16:18 | 2020-10-08 17:31 | 292 | XFMR | 15071 | 38719491186 | 411 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | bad 50 kva changed out | -90.1101 | 30.0118 | Equipment Failure | Transformer | Equipment Failure | 2020-10-08 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 10 | 1341904016 | Yes | EAST ORLEANS | FAIR | 82 | 2020-10-08 16:42 | 2020-10-08 16:42 | 2020-10-08 18:04 | 820 | TFUS | 527252 | 42121501096 | 2212 | ENOI | 6 | 10 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | see click | -90.0021 | 30.0382 | Other | Transformer Fuse | Other | 2020-10-08 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 38 | 1341907196 | Yes | EAST ORLEANS | FAIR | 83 | 2020-10-08 20:18 | 2020-10-08 20:41 | 2020-10-08 21:41 | 3154 | LFUS | 27968 | 4101147482 | 2347 | ENOI | 6 | 38 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | see click | -90.0381 | 29.9663 | Other | Line Fuse | Other | 2020-10-08 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 6 | 1341912498 | Yes | ORLEANS | RAIN | 85 | 2020-10-08 23:54 | 2020-10-08 23:58 | 2020-10-09 01:19 | 510 | TFUS | 551074 | 38260457761 | 1914 | ENOI | 1 | 6 | VINE | Vine Growing into Line | N | vines on transformer | -90.1257 | 29.9202 | Vegetation | Transformer Fuse | Vegetation | 2020-10-08 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 36 | 1341914377 | Yes | EAST ORLEANS | FAIR | 372 | 2020-10-09 00:46 | 2020-10-09 02:13 | 2020-10-09 06:58 | 13392 | LFUS | 21114 | 4101048078 | 621 | ENOI | 6 | 36 | EARM | Equipment Failure - Crossarm | N |  | -90.0379 | 29.9827 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 24 | 1341916932 | Yes | EAST ORLEANS | FAIR | 171 | 2020-10-09 01:53 | 2020-10-09 04:01 | 2020-10-09 04:44 | 4104 | TFUS | 3005286 | 42615493129 | 1604 | ENOI | 6 | 24 | VINE | Vine Growing into Line | N | Cleared vines on pole by transformer and refused transformer. | -89.9867 | 30.0162 | Vegetation | Transformer Fuse | Vegetation | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 11 | 1341918026 | Yes | ORLEANS | RAIN | 128 | 2020-10-09 02:13 | 2020-10-09 02:13 | 2020-10-09 04:21 | 1408 | TFUS | 63702 | 38959479227 | 2011 | ENOI | 1 | 11 | EARM | Equipment Failure - Crossarm | N | burnt crossarm on alexander st | -90.103 | 29.9789 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 30 | 1341918966 | Yes | EAST ORLEANS | FAIR | 199 | 2020-10-09 02:40 | 2020-10-09 04:22 | 2020-10-09 06:00 | 5970 | LFUS | 23024 | 4187250055 | 2212 | ENOI | 6 | 30 | EPRI | Equipment Failure - Primary Conductor | N | Found bad cable between vault 22 and vault 23. Isolated cable and refused B phase sw 23024 | -90.01 | 30.0367 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 6 | 1341919598 | Yes | ORLEANS | RAIN | 48 | 2020-10-09 03:02 | 2020-10-09 03:02 | 2020-10-09 03:50 | 288 | LFUS | 44391 | 3896947916 | 2011 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1026 | 29.9787 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 21 | 1341974210 | Yes | ORLEANS | FAIR | 120 | 2020-10-09 14:53 | 2020-10-09 14:55 | 2020-10-09 16:53 | 2520 | TFUS | 64219 | 39443457762 | 1911 | ENOI | 1 | 21 | VINE | Vine Growing into Line | N | refused ok | -90.0884 | 29.9199 | Vegetation | Transformer Fuse | Vegetation | 2020-10-09 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 13 | 1341986034 | Yes | EAST ORLEANS | WIND | 155 | 2020-10-09 15:16 | 2020-10-09 15:18 | 2020-10-09 17:51 | 2015 | TFUS | 32969 | 40390489547 | 1702 | ENOI | 6 | 13 | EPRI | Equipment Failure - Primary Conductor | N | Had to change and reinstall hot line clamp. | -90.0572 | 30.0069 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 20 | 1342021213 | Yes | EAST ORLEANS | FAIR | 147 | 2020-10-09 16:04 | 2020-10-09 18:12 | 2020-10-09 18:31 | 2940 | LFUS | 32535 | 4171647159 | 2346 | ENOI | 6 | 20 | EARM | Equipment Failure - Crossarm | N | broken crossarm | -90.016 | 29.9571 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 10
2020 | 20 | 1342084103 | Yes | ORLEANS | WIND | 155 | 2020-10-09 17:25 | 2020-10-09 20:00 | 2020-10-09 20:00 | 3100 | LFUS | 38498 | 38382466786 | 2013 | ENOI | 1 | 20 | ESEC | Secondary/Service Conductor | N |  | -90.1216 | 29.9448 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 1 | 1342159892 | Yes | EAST ORLEANS | FAIR | 90 | 2020-10-09 18:10 | 2020-10-09 18:14 | 2020-10-09 19:40 | 90 | SERV | SERVICE | 40712490534 | 1702 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.047 | 30.0096 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 41 | 1342294124 | Yes | EAST ORLEANS | THDR | 91 | 2020-10-09 19:58 | 2020-10-09 20:38 | 2020-10-09 21:29 | 3731 | LFUS | 37075 | 4044849567 | 505 | ENOI | 6 | 41 | EFSW | Equipment Failure - Fuse Switch | N | Equipment Failure - Fuse Switch | -90.0554 | 30.0236 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 14 | 1342577508 | Yes | ORLEANS | HURR | 499 | 2020-10-09 20:07 | 2020-10-09 22:12 | 2020-10-10 04:26 | 6986 | TFUS | 72912 | 38787481577 | 2011 | ENOI | 1 | 14 | STRM | Storm | N | REFUSED XFMR | -90.1083 | 29.9855 | Other | Transformer Fuse | Other | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 1549 | 1342402636 | Yes | EAST ORLEANS | HURR | 173 | 2020-10-09 20:15 | 2020-10-09 23:20 | 2020-10-09 23:08 | 267977 | RCLR | 26149 | 4071647804 | 622 | ENOI | 6 | 1549 | STRM | Storm | N | Storm | -90.0471 | 29.9752 | Other | Recloser | Other | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 12 | 1342380798 | Yes | EAST ORLEANS | HURR | 501 | 2020-10-09 20:33 | 2020-10-10 00:08 | 2020-10-10 04:54 | 6012 | LFUS | 81358 | 4118949082 | 617 | ENOI | 6 | 12 | STRM | Storm | N | Storm | -90.0322 | 30.0101 | Other | Line Fuse | Other | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 40 | 1342393067 | Yes | EAST ORLEANS | HURR | 531 | 2020-10-09 20:35 | 2020-10-10 04:36 | 2020-10-10 05:26 | 21240 | RCLR | 27973 | 4555150350 | 2213 | ENOI | 6 | 40 | STRM | Storm | N | Recloser out from weather high wind back on | -89.8937 | 30.0438 | Other | Recloser | Other | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 8 | 1342352534 | Yes | EAST ORLEANS | HURR | 724 | 2020-10-09 20:38 | 2020-10-10 08:33 | 2020-10-10 08:42 | 5792 | TFUS | 59497 | 40503482799 | 613 | ENOI | 6 | 8 | EARM | Equipment Failure - Crossarm | N | changed primary arm all customers back in lights | -90.0538 | 29.9883 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 4 | 1342369784 | Yes | EAST ORLEANS | HURR | 175 | 2020-10-09 20:38 | 2020-10-09 21:30 | 2020-10-09 23:33 | 700 | TFUS | 70701 | 40716478358 | 622 | ENOI | 6 | 4 | STRM | Storm | N | Storm | -90.0473 | 29.976 | Other | Transformer Fuse | Other | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 1782 | 1342345146 | Yes | ORLEANS | HURR | 45 | 2020-10-09 20:44 | 2020-10-09 21:34 | 2020-10-09 21:29 | 80190 | SBKR | 1915 | 3909545676 | 1915 | ENOI | 1 | 1782 | STRM | Storm | N | high winds in the area; possible limb across primary | -90.0994 | 29.9172 | Other | Substation Breaker | Other | 2020-10-09 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 22 | 1342380260 | Yes | ORLEANS | HURR | 376 | 2020-10-09 20:45 | 2020-10-09 20:59 | 2020-10-10 03:01 | 8272 | LFUS | 17788 | 3893448852 | 413 | ENOI | 1 | 22 | STRM | Storm | N | high winds slapped phases together | -90.1032 | 30.0044 | Other | Line Fuse | Other | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 12 | 1342350280 | Yes | ORLEANS | HURR | 369 | 2020-10-09 20:47 | 2020-10-10 01:58 | 2020-10-10 02:56 | 4428 | LFUS | 21445 | 3858046232 | 1926 | ENOI | 1 | 12 | VOHL | Overhanging Limb | N | removed limb off line and closed in | -90.1156 | 29.9326 | Vegetation | Line Fuse | Vegetation | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 10
2020 | 32 | 1342371866 | Yes | ORLEANS | HURR | 370 | 2020-10-09 20:50 | 2020-10-10 02:27 | 2020-10-10 03:00 | 11840 | LFUS | 62834 | 3951747832 | 1513 | ENOI | 1 | 32 | EARR | Equipment Failure - Arrestor | N | blown arrestor | -90.0853 | 29.9761 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 7 | 1342358848 | Yes | ORLEANS | HURR | 471 | 2020-10-09 20:52 | 2020-10-09 22:05 | 2020-10-10 04:43 | 3297 | TFUS | 1190863 | 38492483458 | 407 | ENOI | 1 | 7 | LGHT | Lightning | N | refused ok | -90.1175 | 29.9907 | Lightning | Transformer Fuse | Lightning | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 1 | 1342363302 | Yes | ORLEANS | FAIR | 648 | 2020-10-09 20:56 | 2020-10-09 20:56 | 2020-10-10 07:44 | 648 | SERV | SERVICE | 38334468875 | 2015 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | both hot legs burnt open changed out connections on pole | -90.123 | 29.9507 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 1 | 1342379646 | Yes | EAST ORLEANS | HURR | 696 | 2020-10-09 20:56 | 2020-10-09 20:56 | 2020-10-10 08:32 | 696 | TFUS | 1289513 | 4982953811 | 1204 | ENOI | 6 | 1 | UNKN | Inspected Unknown | N |  | -89.7573 | 30.1369 | Other | Transformer Fuse | Other | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 9 | 1342379903 | Yes | ORLEANS | HURR | 451 | 2020-10-09 20:59 | 2020-10-10 04:49 | 2020-10-10 04:30 | 4059 | TFUS | 63843 | 40205478609 | 627 | ENOI | 1 | 9 | STRM | Storm | N | Storm | -90.0634 | 29.9769 | Other | Transformer Fuse | Other | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70116 | 10
2020 | 110 | 1342374522 | Yes | EAST ORLEANS | HURR | 91 | 2020-10-09 21:02 | 2020-10-09 21:48 | 2020-10-09 22:33 | 10010 | LFUS | 46249 | 4222549338 | 1607 | ENOI | 6 | 110 | STRM | Storm | N | Storm Completion | -89.9992 | 30.0168 | Other | Line Fuse | Other | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 8 | 1342376707 | Yes | EAST ORLEANS | FAIR | 533 | 2020-10-09 21:06 | 2020-10-10 01:26 | 2020-10-10 06:00 | 4264 | TFUS | 78448 | 40954474687 | 2347 | ENOI | 6 | 8 | VINE | Vine Growing into Line | N | Cleared vines from pole and refused transformer | -90.0398 | 29.9659 | Vegetation | Transformer Fuse | Vegetation | 2020-10-09 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 10 | 1342388349 | Yes | EAST ORLEANS | HURR | 491 | 2020-10-09 21:11 | 2020-10-10 01:48 | 2020-10-10 05:22 | 4910 | TFUS | 59545 | 40743478282 | 622 | ENOI | 6 | 10 | STRM | Storm | N | Storm | -90.0465 | 29.9758 | Other | Transformer Fuse | Other | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 2 | 1342392159 | Yes | EAST ORLEANS | FAIR | 899 | 2020-10-09 21:28 | 2020-10-09 22:26 | 2020-10-10 12:27 | 1798 | TFUS | 63006 | 43433509001 | 2217 | ENOI | 6 | 2 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Had to take out slack in the shield and primary wire. Also had to cut limbs from a tree. Refused lateral customers back in lights. | -89.9604 | 30.0595 | Other | Transformer Fuse | Other | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 32 | 1342392559 | Yes | ORLEANS | HURR | 293 | 2020-10-09 21:37 | 2020-10-10 00:23 | 2020-10-10 02:30 | 9376 | LFUS | 37696 | 3962045874 | 1911 | ENOI | 1 | 32 | VOHL | Overhanging Limb | N | removed limb off line and closed back in | -90.0828 | 29.9224 | Vegetation | Line Fuse | Vegetation | 2020-10-09 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 115 | 1342394603 | Yes | EAST ORLEANS | HURR | 140 | 2020-10-09 21:46 | 2020-10-09 22:26 | 2020-10-10 00:06 | 16100 | LFUS | 21016 | 4057248047 | 613 | ENOI | 6 | 115 | STRM | Storm | N | Storm | -90.0518 | 29.9821 | Other | Line Fuse | Other | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 4 | 1342589352 | Yes | ORLEANS | FAIR | 697 | 2020-10-09 21:56 | 2020-10-10 00:19 | 2020-10-10 09:33 | 2788 | TFUS | 72310 | 38902483866 | 904 | ENOI | 1 | 4 | ESEC | Secondary/Service Conductor | N | Relaired secondary in tree | -90.1046 | 29.9917 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 334 | 1342404856 | Yes | ORLEANS | HURR | 160 | 2020-10-09 21:58 | 2020-10-10 00:39 | 2020-10-10 00:38 | 53440 | RCLR | 24944 | 3983048290 | 1711 | ENOI | 1 | 334 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up at switch 23669 | -90.0752 | 29.9887 | Equipment Failure | Recloser | Equipment Failure | 2020-10-09 | DLIN | D | Council District D | Jared Brossett | 70119 | 10
2020 | 756 | 1342406527 | Yes | ORLEANS | HURR | 157 | 2020-10-09 22:00 | 2020-10-10 00:34 | 2020-10-10 00:37 | 118692 | RCLR | 92900 | 3981748250 | 1711 | ENOI | 1 | 756 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up at switch 23669 | -90.0755 | 29.9877 | Equipment Failure | Recloser | Equipment Failure | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 185 | 1342418378 | Yes | ORLEANS | HURR | 203 | 2020-10-09 22:22 | 2020-10-10 01:31 | 2020-10-10 01:45 | 37555 | LFUS | 33243 | 3832347263 | 2016 | ENOI | 1 | 185 | EARM | Equipment Failure - Crossarm | N | repaired arm and closed switch back in | -90.1232 | 29.9609 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 98 | 1342431457 | Yes | ORLEANS | HURR | 174 | 2020-10-09 22:32 | 2020-10-10 00:33 | 2020-10-10 01:26 | 17052 | LFUS | 21493 | 3943946191 | 1924 | ENOI | 1 | 98 | EARM | Equipment Failure - Crossarm | N | replaced crossarm and closed switch back in | -90.0882 | 29.9313 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 425 | 1342442483 | Yes | EAST ORLEANS | HURR | 138 | 2020-10-09 22:36 | 2020-10-10 00:52 | 2020-10-10 00:54 | 58650 | RCLR | 23804 | 4215449166 | 1607 | ENOI | 6 | 425 | STRM | Storm | N | primary down | -90.0016 | 30.0121 | Other | Recloser | Other | 2020-10-09 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 77 | 1342452990 | Yes | ORLEANS | HURR | 200 | 2020-10-09 22:48 | 2020-10-10 01:34 | 2020-10-10 02:08 | 15400 | LFUS | 55730 | 3829946513 | 2014 | ENOI | 1 | 77 | VLGL | Tree/Limb Growing Inside R.O.W. | N | b and c phase blown and sub lateral b and c also blown taken out by tree limb on sub lateral | -90.1243 | 29.9405 | Vegetation | Line Fuse | Vegetation | 2020-10-09 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 176 | 1342491807 | Yes | EAST ORLEANS | HURR | 342 | 2020-10-09 23:35 | 2020-10-10 05:00 | 2020-10-10 05:17 | 60192 | LFUS | 21145 | 4065847641 | 622 | ENOI | 6 | 176 | EFLK | Equipment Failure - Fuse Link | N | Equipment Failure - Fuse Link | -90.0492 | 29.9709 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-09 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 134 | 1342729077 | Yes | EAST ORLEANS | HURR | 445 | 2020-10-10 01:03 | 2020-10-10 08:16 | 2020-10-10 08:28 | 59630 | LFUS | 27627 | 4217649174 | 1607 | ENOI | 6 | 134 | EARM | Equipment Failure - Crossarm | N |  | -90.0006 | 30.0123 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 4 | 1342553109 | Yes | EAST ORLEANS | HURR | 444 | 2020-10-10 01:34 | 2020-10-10 05:04 | 2020-10-10 08:58 | 1776 | TFUS | 649952 | 50404547928 | 1204 | ENOI | 6 | 4 | ECNS | Equipment Failure - Connector Sleeve | N | Jumper burnt open | -89.7386 | 30.164 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 7 | 1342644961 | Yes | EAST ORLEANS | HURR | 221 | 2020-10-10 04:51 | 2020-10-10 06:35 | 2020-10-10 08:33 | 1547 | TFUS | 1333256 | 42025492065 | 1607 | ENOI | 6 | 7 | EARM | Equipment Failure - Crossarm | N |  | -90.0055 | 30.0134 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 185 | 1342692549 | Yes | ORLEANS | FAIR | 192 | 2020-10-10 05:16 | 2020-10-10 08:18 | 2020-10-10 08:28 | 35520 | LFUS | 33243 | 3832347263 | 2016 | ENOI | 1 | 185 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burnt open repaired and back in | -90.1232 | 29.9609 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 68 | 1342670923 | Yes | EAST ORLEANS | WIND | 184 | 2020-10-10 06:24 | 2020-10-10 09:01 | 2020-10-10 09:29 | 12512 | LFUS | 24971 | 4214250165 | 2212 | ENOI | 6 | 68 | EELB | Equipment Failure - Elbow | N | V-22 elbows bad | -90.0015 | 30.0397 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 11 | 1342691346 | Yes | EAST ORLEANS | HURR | 263 | 2020-10-10 07:01 | 2020-10-10 09:55 | 2020-10-10 11:24 | 2893 | TFUS | 1258228 | 42956506322 | 2223 | ENOI | 6 | 11 | EOSC | Equipment Failure - Shield Conductor | N | Picked up secondary wires and shield wires refused lateral | -89.9755 | 30.0523 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 32 | 1342694089 | Yes | ORLEANS | HURR | 153 | 2020-10-10 07:12 | 2020-10-10 07:12 | 2020-10-10 09:45 | 4896 | LFUS | 27629 | 3835547281 | 2016 | ENOI | 1 | 32 | EARM | Equipment Failure - Crossarm | N | replaced | -90.1222 | 29.9614 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 17 | 1342696057 | Yes | ORLEANS | HURR | 153 | 2020-10-10 07:12 | 2020-10-10 07:12 | 2020-10-10 09:45 | 2601 | LFUS | 27880 | 3833247302 | 2016 | ENOI | 1 | 17 | EARM | Equipment Failure - Crossarm | N | repaired | -90.123 | 29.962 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 45 | 1342698918 | Yes | EAST ORLEANS | FAIR | 267 | 2020-10-10 07:13 | 2020-10-10 10:54 | 2020-10-10 11:40 | 12015 | LFUS | 25370 | 4385351220 | 2217 | ENOI | 6 | 45 | EPRI | Equipment Failure - Primary Conductor | N | BAD CABLE BETWEEN V14 &amp;amp; V 15 CABLE ISOLATED | -89.9472 | 30.0681 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 3 | 1342703888 | Yes | EAST ORLEANS | HURR | 51 | 2020-10-10 07:25 | 2020-10-10 07:25 | 2020-10-10 08:16 | 153 | LFUS | 61870 | 4104748930 | 1702 | ENOI | 6 | 3 | ECON | Equipment Failure - Connector / Sleeve | N | Bottom side of switch came out dropped out lateral and repaired bottom side jumper | -90.0366 | 30.006 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 1 | 1342727662 | Yes | EAST ORLEANS | HURR | 170 | 2020-10-10 08:05 | 2020-10-10 08:05 | 2020-10-10 10:55 | 170 | TFUS | 1483809 | 40334487975 | 1702 | ENOI | 6 | 1 | EFSW | Equipment Failure - Fuse Switch | N | Top side of switch came out of switch installed new riser and checked voltay | -90.0593 | 30.0025 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1 | 1342733291 | Yes | EAST ORLEANS | HURR | 172 | 2020-10-10 08:16 | 2020-10-10 08:16 | 2020-10-10 11:08 | 172 | TFUS | 1205773 | 41301496426 | 1002 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Jumper burned off of switch | -90.0282 | 30.0254 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 14 | 1342761039 | Yes | ORLEANS | HURR | 238 | 2020-10-10 08:51 | 2020-10-10 11:20 | 2020-10-10 12:49 | 3332 | TFUS | 71245 | 39107457897 | 1922 | ENOI | 1 | 14 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.0991 | 29.9203 | Vegetation | Transformer Fuse | Vegetation | 2020-10-10 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 2 | 1342782564 | Yes | EAST ORLEANS | HURR | 52 | 2020-10-10 09:21 | 2020-10-10 09:21 | 2020-10-10 10:13 | 104 | TFUS | 1558443 | 41315476454 | 621 | ENOI | 6 | 2 | EFLK | Equipment Failure - Fuse Link | N | Heavy wind caused a phase to contact span guy. Customers back in lights | -90.0284 | 29.9706 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 306 | 1342938838 | Yes | ORLEANS | HURR | 202 | 2020-10-10 10:38 | 2020-10-10 13:54 | 2020-10-10 14:00 | 61812 | LFUS | 21206 | 4020247905 | 627 | ENOI | 1 | 306 | EARM | Equipment Failure - Crossarm | N | replaced | -90.0635 | 29.9781 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-10 | DLIN | D | Council District D | Jared Brossett | 70116 | 10
2020 | 3 | 1342841552 | Yes | EAST ORLEANS | HURR | 75 | 2020-10-10 10:47 | 2020-10-10 10:47 | 2020-10-10 12:02 | 225 | TFUS | 1546203 | 48529511855 | 1204 | ENOI | 6 | 3 | UNKN | Inspected Unknown | N | REFUSED OKAY | -89.7991 | 30.0656 | Other | Transformer Fuse | Other | 2020-10-10 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 7 | 1342844796 | Yes | ORLEANS | FAIR | 92 | 2020-10-10 10:53 | 2020-10-10 10:53 | 2020-10-10 12:25 | 644 | TFUS | 1128675 | 39152459219 | 1923 | ENOI | 1 | 7 | ESEC | Secondary/Service Conductor | N | Repaired open wire secondary | -90.0975 | 29.924 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 1 | 1342859625 | Yes | EAST ORLEANS | FAIR | 109 | 2020-10-10 11:16 | 2020-10-10 11:16 | 2020-10-10 13:05 | 109 | TFUS | C65648 | 4128449354 | 1009 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | High wind caused fuse to blow. Refused and customer back in lights | -90.0289 | 30.0178 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 1 | 1342897780 | Yes | ORLEANS | HURR | 99 | 2020-10-10 12:01 | 2020-10-10 12:01 | 2020-10-10 13:40 | 99 | SERV | SERVICE | 38863479939 | 2011 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | Spliced service wire | -90.1059 | 29.9809 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-10 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 1 | 1342894028 | Yes | ORLEANS | FAIR | 59 | 2020-10-10 12:04 | 2020-10-10 12:04 | 2020-10-10 13:03 | 59 | TFUS | 1120095 | 3909645836 | 1923 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Replaced riser on switch | -90.0992 | 29.9216 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-10 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 12 | 1343141664 | Yes | ORLEANS | FAIR | 19 | 2020-10-10 20:11 | 2020-10-10 20:17 | 2020-10-10 20:30 | 228 | TFUS | 79699 | 38510464533 | 2024 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1177 | 29.9388 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-10 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 1 | 1343178292 | Yes | ORLEANS CBD | FAIR | 958 | 2020-10-11 02:06 | 2020-10-11 02:06 | 2020-10-11 18:04 | 958 | SBKR | 1842 | 4015346700 | 1842 | ENOI | 4 | 1 | EPRI | Equipment Failure - Primary Conductor | N | Equipment Failure - Primary Conductor | -90.0656 | 29.945 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-10-11 | DLIN | B | Council District B | Jay Banks | 70130 | 10
2020 | 83 | 1343203521 | Yes | EAST ORLEANS | FAIR | 157 | 2020-10-11 06:43 | 2020-10-11 08:52 | 2020-10-11 09:20 | 13031 | LFUS | 77258 | 43767504790 | 2214 | ENOI | 6 | 83 | EFLK | Equipment Failure - Fuse Link | N | Had to refuse lateral customers back in | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-11 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 1 | 1343231395 | Yes | EAST ORLEANS | FAIR | 70 | 2020-10-11 08:38 | 2020-10-11 08:38 | 2020-10-11 09:48 | 70 | SERV | SERVICE | 42498503150 | 2215 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Hot leg failed | -89.9901 | 30.0438 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-11 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 19 | 1343233645 | Yes | ORLEANS | FAIR | 83 | 2020-10-11 08:43 | 2020-10-11 08:49 | 2020-10-11 10:06 | 1577 | TFUS | 75856 | 39446482480 | 1711 | ENOI | 1 | 19 | EOSC | Equipment Failure - Shield Conductor | N | pick back up in clear | -90.0873 | 29.9878 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-11 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 1401 | 1343252250 | Yes | ORLEANS | FAIR | 12 | 2020-10-11 09:53 | 2020-10-11 10:04 | 2020-10-11 10:05 | 16812 | SBKR | 1711 | 4024048726 | 1711 | ENOI | 1 | 1401 | EOSC | Equipment Failure - Shield Conductor | N | sheild wire came down, picked back up in clear | -90.0621 | 30.0007 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-10-11 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 186 | 1343331819 | Yes | ORLEANS | FAIR | 197 | 2020-10-11 14:03 | 2020-10-11 16:29 | 2020-10-11 17:20 | 36642 | LFUS | 22110 | 3992046226 | 2135 | ENOI | 1 | 186 | EFSW | Equipment Failure - Fuse Switch | N | replaced switch and got everyone back in | -90.0731 | 29.9321 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-11 | DLIN | B | Council District B | Jay Banks | 70130 | 10
2020 | 483 | 1343334847 | Yes | ORLEANS | FAIR | 8 | 2020-10-11 14:12 | 2020-10-11 14:22 | 2020-10-11 14:20 | 3864 | RCLR | 74824 | 38761473389 | 2017 | ENOI | 1 | 483 | EMER | Emergency Switching | N | Emergency Switching | -90.1093 | 29.9629 | Other | Recloser | Emergency Switching | 2020-10-11 | DLIN | B | Council District B | Jay Banks | 70125 | 10
2020 | 2 | 1343346799 | Yes | ORLEANS | FAIR | 54 | 2020-10-11 15:01 | 2020-10-11 15:01 | 2020-10-11 15:55 | 108 | TFUS | 20521 | 38489491799 | 411 | ENOI | 1 | 2 | EFSW | Equipment Failure - Fuse Switch | N | replaced swicth and wire | -90.1171 | 30.0136 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-11 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 147 | 1343346856 | Yes | ORLEANS | FAIR | 102 | 2020-10-11 15:03 | 2020-10-11 15:14 | 2020-10-11 16:45 | 14994 | LFUS | 27949 | 3986347312 | 1512 | ENOI | 1 | 147 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons, removed and refused | -90.0745 | 29.962 | Other | Line Fuse | Other | 2020-10-11 | DLIN | C | Council District C | Kristin Palmer | 70112 | 10
2020 | 13 | 1343348926 | Yes | ORLEANS | FAIR | 130 | 2020-10-11 15:11 | 2020-10-11 15:11 | 2020-10-11 17:21 | 1690 | TFUS | 693371 | 39695462102 | 2135 | ENOI | 1 | 13 | VINE | Vine Growing into Line | N | removed and refused | -90.0802 | 29.9318 | Vegetation | Transformer Fuse | Vegetation | 2020-10-11 | DLIN | B | Council District B | Jay Banks | 70130 | 10
2020 | 21 | 1343477422 | Yes | ORLEANS | FAIR | 451 | 2020-10-12 08:29 | 2020-10-12 16:09 | 2020-10-12 16:00 | 9359 | DIS | 24676 | 3836546670 | 2013 | ENOI | 1 | 21 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1221 | 29.9448 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-10-12 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 1 | 1343530614 | Yes | ORLEANS | FAIR | 125 | 2020-10-12 12:24 | 2020-10-12 12:25 | 2020-10-12 14:29 | 125 | SERV | SERVICE | 39187463649 | 1922 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | hot leg connection on ferry service burnt open | -90.0962 | 29.9361 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-12 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 10 | 1343625571 | Yes | EAST ORLEANS | FAIR | 293 | 2020-10-12 22:08 | 2020-10-12 22:19 | 2020-10-13 03:01 | 2930 | LFUS | 21228 | 4111648658 | 616 | ENOI | 6 | 10 | VHCL | Vehicle | N | car hit pole, shield wire and primary down | -90.0344 | 29.9984 | Public Damage | Line Fuse | Public Damage | 2020-10-12 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 10 | 1343629668 | Yes | ORLEANS | FAIR | 64 | 2020-10-13 00:56 | 2020-10-13 00:56 | 2020-10-13 02:00 | 640 | XFMR | 569485 | 39111467798 | 2021 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | crew replaced xfmr | -90.0983 | 29.9476 | Scheduled Interruption | Transformer | Scheduled Interruption | 2020-10-13 | DLIN | B | Council District B | Jay Banks | 70125 | 10
2020 | 370 | 1343631113 | Yes | EAST ORLEANS | FAIR | 167 | 2020-10-13 03:22 | 2020-10-13 05:09 | 2020-10-13 06:10 | 61790 | LFUS | 27045 | 4279549796 | 1613 | ENOI | 6 | 370 | MALD | Malicious Damage | N | Unknown male in walkin vault Bundy and lake forest stealing copper out of vault cut locks and pulled fuses crew isolated vault waited for Nopd no show supervisor and crew put new locks on door | -97.0758 | 27.9066 | Public Damage | Line Fuse | Public Damage | 2020-10-13 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 43 | 1343665603 | Yes | ORLEANS | FAIR | 263 | 2020-10-13 10:03 | 2020-10-13 10:13 | 2020-10-13 14:26 | 11309 | LFUS | 21399 | 3878246456 | 1554 | ENOI | 1 | 43 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.1092 | 29.9389 | Vegetation | Line Fuse | Vegetation | 2020-10-13 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 19 | 1343723191 | Yes | EAST ORLEANS | FAIR | 316 | 2020-10-13 17:09 | 2020-10-13 18:16 | 2020-10-13 22:25 | 6004 | XFMR | 618913 | 43073502200 | 2214 | ENOI | 6 | 19 | ETRD | Equipment Failure - Transformer | N | REPLACED XFMR | -89.9721 | 30.0409 | Equipment Failure | Transformer | Equipment Failure | 2020-10-13 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 51 | 1343723441 | Yes | EAST ORLEANS | FAIR | 288 | 2020-10-13 17:12 | 2020-10-13 18:03 | 2020-10-13 22:00 | 14688 | TFUS | 1315142 | 43065502307 | 2214 | ENOI | 6 | 51 | ETRD | Equipment Failure - Transformer | N | REPLACED XFMR | -89.9723 | 30.0411 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-13 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 1 | 1343787472 | Yes | EAST ORLEANS | FAIR | 338 | 2020-10-14 08:59 | 2020-10-14 08:59 | 2020-10-14 14:37 | 338 | SERV | SERVICE | 44548502658 | 2213 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | BAD CONNECTION IN HAND HOLE | -89.9253 | 30.0415 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-14 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 271 | 1343772620 | Yes | EAST ORLEANS | FAIR | 481 | 2020-10-14 09:10 | 2020-10-14 16:43 | 2020-10-14 17:11 | 130351 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 271 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.8029 | 30.0695 | Scheduled Interruption | Recloser | Scheduled Interruption | 2020-10-14 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 1 | 1343784502 | Yes | EAST ORLEANS | FAIR | 249 | 2020-10-14 11:52 | 2020-10-14 11:52 | 2020-10-14 16:01 | 249 | TFUS | 1318247 | 45166503065 | 2213 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | Assign to Chris Bowden need big bucket truck to reach pole | -89.9059 | 30.0423 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-14 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 29 | 1343801274 | Yes | EAST ORLEANS | FAIR | 139 | 2020-10-14 14:53 | 2020-10-14 16:46 | 2020-10-14 17:12 | 4031 | DIS | 27671 | 4126048530 | 626 | ENOI | 6 | 29 | VHCL | Vehicle | N | car hit pole | -90.0297 | 29.9948 | Public Damage | Disconnect Switch | Public Damage | 2020-10-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 43 | 1343816538 | Yes | EAST ORLEANS | FAIR | 139 | 2020-10-14 14:53 | 2020-10-14 14:53 | 2020-10-14 17:12 | 6751 | OPEN | 4127548429 | 4127548429 | 626 | ENOI | 6 | 43 | VHCL | Vehicle | N | car hit pole | -90.0295 | 29.9922 | Public Damage | Open | Public Damage | 2020-10-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 32 | 1343816703 | Yes | EAST ORLEANS | FAIR | 139 | 2020-10-14 14:53 | 2020-10-14 14:53 | 2020-10-14 17:12 | 4608 | OPEN | 4127848384 | 4127848384 | 626 | ENOI | 6 | 32 | VHCL | Vehicle | N | car hit pole | -90.0295 | 29.9909 | Public Damage | Open | Public Damage | 2020-10-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 30 | 1343819745 | Yes | EAST ORLEANS | FAIR | 139 | 2020-10-14 14:53 | 2020-10-14 14:53 | 2020-10-14 17:12 | 5040 | OPEN | 4127648424 | 4127648424 | 626 | ENOI | 6 | 30 | VHCL | Vehicle | N | car hit pole | -90.0295 | 29.992 | Public Damage | Open | Public Damage | 2020-10-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 8 | 1343819503 | Yes | EAST ORLEANS | FAIR | 567 | 2020-10-14 14:53 | 2020-10-14 18:24 | 2020-10-15 00:20 | 4520 | OPEN | 4127848387 | 4127848387 | 626 | ENOI | 6 | 8 | VHCL | Vehicle | N | vehicle hit and broke pole at location | -90.0295 | 29.991 | Public Damage | Open | Public Damage | 2020-10-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 612 | 1343798913 | Yes | EAST ORLEANS | FAIR | 35 | 2020-10-14 14:54 | 2020-10-14 15:30 | 2020-10-14 15:29 | 21420 | SBKR | 626 | 4081248423 | 626 | ENOI | 6 | 612 | VHCL | Vehicle | N | vechile broke pole | -90.0442 | 29.9922 | Public Damage | Substation Breaker | Public Damage | 2020-10-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 1 | 1343816593 | Yes | ORLEANS CBD | FAIR | 51 | 2020-10-14 17:00 | 2020-10-14 17:00 | 2020-10-14 17:51 | 51 | SERV | SERVICE | 4015647048 | BIENV | ENOI | 4 | 1 | EMET | Equipment Failure - Metering | N | AMI meter was open. We contacted AMOC and they closed the meter restoring the customer power. |  |  | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-14 | DLIN | C | Council District C | Kristin Palmer | 70130 | 10
2020 | 59 | 1343834743 | Yes | EAST ORLEANS | FAIR | 24 | 2020-10-14 23:56 | 2020-10-14 23:56 | 2020-10-15 00:20 | 1475 | DIS | 27671 | 4126048530 | 626 | ENOI | 6 | 59 | EMER | Emergency Switching | N | Emergency Switching | -90.0297 | 29.9948 | Other | Disconnect Switch | Emergency Switching | 2020-10-14 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 50 | 1343840830 | Yes | ORLEANS | FAIR | 63 | 2020-10-15 07:04 | 2020-10-15 07:20 | 2020-10-15 08:07 | 3150 | LFUS | 28088 | 3840546706 | 2013 | ENOI | 1 | 50 | EFLK | Equipment Failure - Fuse Link | N | b phase taken out by tree limb | -90.1209 | 29.9456 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-15 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 1 | 1343842918 | Yes | EAST ORLEANS | FAIR | 108 | 2020-10-15 07:43 | 2020-10-15 08:51 | 2020-10-15 09:31 | 108 | SERV | SERVICE | 48001511715 | 1204 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Repaired open hot leg check voltage ok customer back in lights | -89.8162 | 30.0653 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-15 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 1 | 1343856329 | Yes | ORLEANS | FAIR | 238 | 2020-10-15 10:12 | 2020-10-15 11:06 | 2020-10-15 14:10 | 238 | SERV | SERVICE | 39931482239 | 1712 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Bad connection on Wilson rack | -90.0721 | 29.987 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-15 | DLIN | D | Council District D | Jared Brossett | 70119 | 10
2020 | 29 | 1343897500 | Yes | EAST ORLEANS | FAIR | 96 | 2020-10-15 19:55 | 2020-10-15 20:17 | 2020-10-15 21:31 | 2784 | TFUS | 58716 | 40636480827 | 613 | ENOI | 6 | 29 | EARM | Equipment Failure - Crossarm | N | replaced | -90.0499 | 29.9829 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-15 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 1 | 1343916904 | Yes | EAST ORLEANS | FAIR | 250 | 2020-10-16 08:51 | 2020-10-16 08:51 | 2020-10-16 13:01 | 250 | TFUS | 79186 | 42374490153 | 1601 | ENOI | 6 | 1 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -89.9946 | 30.0081 | Other | Transformer Fuse | Other | 2020-10-16 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 1 | 1343932405 | Yes | EAST ORLEANS | FAIR | 30 | 2020-10-16 12:15 | 2020-10-16 12:15 | 2020-10-16 12:45 | 30 | PRIM | 4153548847 | 4153548847 | 1601 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | refused c phase | -90.0211 | 30.0037 | Equipment Failure | Primary Meter | Equipment Failure | 2020-10-16 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 110 | 1343938574 | Yes | EAST ORLEANS | FAIR | 223 | 2020-10-16 14:14 | 2020-10-16 16:37 | 2020-10-16 17:57 | 24530 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 110 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-16 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 98 | 1343961307 | Yes | ORLEANS | FAIR | 240 | 2020-10-17 05:32 | 2020-10-17 07:30 | 2020-10-17 09:32 | 23520 | LFUS | 81207 | 3841346974 | 2013 | ENOI | 1 | 98 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.1205 | 29.953 | Vegetation | Line Fuse | Vegetation | 2020-10-17 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 11 | 1343972109 | Yes | EAST ORLEANS | FAIR | 149 | 2020-10-17 11:16 | 2020-10-17 11:16 | 2020-10-17 13:45 | 1639 | TFUS | 1171277 | 45081501432 | 1601 | ENOI | 6 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused trans | -89.9087 | 30.038 | Other | Transformer Fuse | Other | 2020-10-17 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 874 | 1343994559 | Yes | EAST ORLEANS | FAIR | 10 | 2020-10-18 02:19 | 2020-10-18 02:30 | 2020-10-18 02:29 | 8740 | RCLR | 35340 | 42415492357 | 1607 | ENOI | 6 | 874 | EMER | Emergency Switching | N | Opened for safety to clear broken pole | -89.9931 | 30.014 | Other | Recloser | Emergency Switching | 2020-10-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 56 | 1343995099 | Yes | EAST ORLEANS | FAIR | 206 | 2020-10-18 02:19 | 2020-10-18 04:47 | 2020-10-18 05:45 | 11480 | OPEN | 4247849222 | 4247849222 | 1607 | ENOI | 6 | 56 | VHCL | Vehicle | N | crew replaced broken pole | -89.9913 | 30.0136 | Public Damage | Open | Public Damage | 2020-10-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 874 | 1343996922 | Yes | EAST ORLEANS | FAIR | 22 | 2020-10-18 05:44 | 2020-10-18 06:06 | 2020-10-18 06:06 | 19228 | RCLR | 35340 | 42415492357 | 1607 | ENOI | 6 | 874 | EMER | Emergency Switching | N | opened for safety broken pole | -89.9931 | 30.014 | Other | Recloser | Emergency Switching | 2020-10-18 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 8 | 1344007545 | Yes | ORLEANS | FAIR | 155 | 2020-10-18 12:43 | 2020-10-18 12:47 | 2020-10-18 15:18 | 1240 | TFUS | 1000859 | 40079461993 | 2137 | ENOI | 1 | 8 | ASQL | Animal - Squirrel | N | refused ok | -90.068 | 29.9314 | Animal | Transformer Fuse | Animal | 2020-10-18 | DLIN | B | Council District B | Jay Banks | 70130 | 10
2020 | 11 | 1344026352 | Yes | ORLEANS | FAIR | 113 | 2020-10-18 21:38 | 2020-10-18 21:38 | 2020-10-18 23:31 | 1243 | TFUS | 1059652 | 39842478595 | 615 | ENOI | 1 | 11 | ESEC | Secondary/Service Conductor | N |  | -90.075 | 29.977 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-18 | DLIN | D | Council District D | Jared Brossett | 70119 | 10
2020 | 1 | 1344037129 | Yes | EAST ORLEANS | FAIR | 53 | 2020-10-19 08:45 | 2020-10-19 08:45 | 2020-10-19 09:38 | 53 | TFUS | 1285308 | 43097499517 | 1605 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | Refuse lateral in cubicle | -89.9711 | 30.0334 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-19 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 7 | 1344045014 | Yes | ORLEANS | FAIR | 229 | 2020-10-19 11:17 | 2020-10-19 13:53 | 2020-10-19 15:06 | 1603 | TFUS | 58234 | 40013485547 | 1703 | ENOI | 1 | 7 | VOHL | Overhanging Limb | N | removed and refused | -90.0694 | 29.9959 | Vegetation | Transformer Fuse | Vegetation | 2020-10-19 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 9 | 1344051590 | Yes | EAST ORLEANS | FAIR | 179 | 2020-10-19 13:51 | 2020-10-19 13:51 | 2020-10-19 16:50 | 1611 | DIS | 27415 | 4181347356 | 2347 | ENOI | 6 | 9 | EMER | Emergency Switching | N | broke pole | -90.0128 | 29.9626 | Other | Disconnect Switch | Emergency Switching | 2020-10-19 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 10
2020 | 4 | 1344069309 | Yes | EAST ORLEANS | FAIR | 88 | 2020-10-19 21:50 | 2020-10-19 21:50 | 2020-10-19 23:18 | 352 | TFUS | 569561 | 43305506036 | 2214 | ENOI | 6 | 4 | EFSW | Equipment Failure - Fuse Switch | N |  | -89.9647 | 30.0514 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-19 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 705 | 1344070818 | Yes | EAST ORLEANS | FOGG | 140 | 2020-10-20 00:24 | 2020-10-20 02:50 | 2020-10-20 02:44 | 98700 | SBKR | 1609 | 4351549757 | 1609 | ENOI | 6 | 705 | EPRI | Equipment Failure - Primary Conductor | N | Bad cable bet cub. 363 & cub. 404 | -89.9583 | 30.028 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-10-20 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 88 | 1344074340 | Yes | EAST ORLEANS | FOGG | 336 | 2020-10-20 00:24 | 2020-10-20 01:42 | 2020-10-20 06:00 | 29568 | SWIT | 36877 | 4369550041 | 1609 | ENOI | 6 | 88 | EPRI | Equipment Failure - Primary Conductor | N | Bad cable bet cub. 363 & 440 | -97.0758 | 27.9066 | Equipment Failure | Switch | Equipment Failure | 2020-10-20 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 2267 | 1344079352 | Yes | ORLEANS | FAIR | 9 | 2020-10-20 08:20 | 2020-10-20 08:29 | 2020-10-20 08:29 | 20403 | SBKR | 2011 | 3847547393 | 2011 | ENOI | 1 | 2267 | EMER | Emergency Switching | N | Emergency Switching | -90.1183 | 29.9645 | Other | Substation Breaker | Emergency Switching | 2020-10-20 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 1 | 1344081510 | Yes | ORLEANS | FAIR | 427 | 2020-10-20 08:49 | 2020-10-20 08:49 | 2020-10-20 15:56 | 427 | TFUS | 66208 | 39515457294 | 1911 | ENOI | 1 | 1 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.086 | 29.9185 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-20 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 170 | 1344084928 | Yes | ORLEANS | FAIR | 549 | 2020-10-20 10:10 | 2020-10-20 19:09 | 2020-10-20 19:19 | 93330 | OPEN | 3920545901 | 3920545901 | 1923 | ENOI | 1 | 170 | SCHD | Scheduled Interruption | N |  | -90.0958 | 29.9233 | Scheduled Interruption | Open | Scheduled Interruption | 2020-10-20 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 1 | 1344105912 | Yes | ORLEANS | FAIR | 40 | 2020-10-20 17:22 | 2020-10-20 17:39 | 2020-10-20 18:02 | 40 | SERV | SERVICE | 38708494778 | 401 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | Swapped meters | -90.1103 | 30.0217 | Other | Service Conductor | Other | 2020-10-20 | DLIN | D | Council District D | Jared Brossett | 70124 | 10
2020 | 14 | 1344122278 | Yes | EAST ORLEANS | FAIR | 127 | 2020-10-21 09:21 | 2020-10-21 09:28 | 2020-10-21 11:28 | 1778 | LFUS | 21258 | 4189950117 | 2212 | ENOI | 6 | 14 | EPRI | Equipment Failure - Primary Conductor | N | Primary down crew coming to pick up | -90.0092 | 30.0385 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-21 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 76 | 1344123237 | Yes | EAST ORLEANS | FAIR | 273 | 2020-10-21 09:43 | 2020-10-21 11:52 | 2020-10-21 14:16 | 20748 | LFUS | 77126 | 42764504198 | 2215 | ENOI | 6 | 76 | SCHD | Scheduled Interruption | N | back on | -89.9819 | 30.0462 | Scheduled Interruption | Line Fuse | Scheduled Interruption | 2020-10-21 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 1 | 1344126031 | Yes | EAST ORLEANS | FAIR | 162 | 2020-10-21 10:43 | 2020-10-21 10:43 | 2020-10-21 13:25 | 162 | TFUS | 503831 | 40962474734 | 2347 | ENOI | 6 | 1 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | Wind caused pole guard to fall across phases cleared and refused. | -90.0397 | 29.966 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-21 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 6 | 1344126223 | Yes | EAST ORLEANS | FAIR | 114 | 2020-10-21 10:47 | 2020-10-21 10:59 | 2020-10-21 12:41 | 684 | TFUS | 56956 | 40663489450 | 1702 | ENOI | 6 | 6 | ASQL | Animal - Squirrel | N | Squirrel came across the bushings on the top of the transformer. Took out the transformer and lateral fuse. Customer back in lights. | -90.0485 | 30.0066 | Animal | Transformer Fuse | Animal | 2020-10-21 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 7 | 1344140364 | Yes | ORLEANS | FAIR | 185 | 2020-10-21 16:38 | 2020-10-21 19:39 | 2020-10-21 19:43 | 1295 | TFUS | 1190863 | 38492483458 | 407 | ENOI | 1 | 7 | VINE | Vine Growing into Line | N | cleared vines refused ok | -90.1175 | 29.9907 | Vegetation | Transformer Fuse | Vegetation | 2020-10-21 | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 10
2020 | 563 | 1344145865 | Yes | EAST ORLEANS | FAIR | 242 | 2020-10-21 21:15 | 2020-10-22 00:27 | 2020-10-22 01:17 | 136246 | VFI | 26028 | 4359950142 | 2214 | ENOI | 6 | 563 | EPRI | Equipment Failure - Primary Conductor | N | BAD CABLE | -97.0758 | 27.9066 | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | 2020-10-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 160 | 1344146679 | Yes | EAST ORLEANS | FAIR | 155 | 2020-10-21 21:16 | 2020-10-22 01:13 | 2020-10-21 23:51 | 24800 | LFUS | 25932 | 4317750280 | 1603 | ENOI | 6 | 160 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 145 | 1344146244 | Yes | EAST ORLEANS | FAIR | 242 | 2020-10-21 21:16 | 2020-10-22 00:52 | 2020-10-22 01:18 | 35090 | VFI | 26073 | 4345250370 | 2214 | ENOI | 6 | 145 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | 2020-10-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 376 | 1344146000 | Yes | EAST ORLEANS | FAIR | 154 | 2020-10-21 21:17 | 2020-10-22 01:12 | 2020-10-21 23:51 | 57904 | LFUS | 25878 | 4309450396 | 1603 | ENOI | 6 | 376 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 166 | 1344145994 | Yes | EAST ORLEANS | FAIR | 240 | 2020-10-21 21:17 | 2020-10-22 01:10 | 2020-10-22 01:17 | 39840 | LFUS | 25734 | 4314750328 | 1603 | ENOI | 6 | 166 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-21 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 1 | 1344149207 | Yes | EAST ORLEANS | FAIR | 10 | 2020-10-22 01:07 | 2020-10-22 01:07 | 2020-10-22 01:17 | 10 | TFUS | 70983 | 40713473979 | 623 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | repaired jumper connection | -90.0477 | 29.964 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-22 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 1 | 1344177684 | Yes | EAST ORLEANS | FAIR | 255 | 2020-10-22 15:40 | 2020-10-22 15:40 | 2020-10-22 19:55 | 255 | TFUS | 503831 | 40962474734 | 2347 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N |  | -90.0397 | 29.966 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-22 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 1 | 1344182077 | Yes | ORLEANS | FAIR | 63 | 2020-10-22 17:49 | 2020-10-22 17:49 | 2020-10-22 18:52 | 63 | SERV | SERVICE | 38596479525 | 400 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Spliced service refused stinger transformer | -90.1144 | 29.9798 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-22 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 2 | 1344188499 | Yes | EAST ORLEANS | FAIR | 64 | 2020-10-22 19:54 | 2020-10-22 19:54 | 2020-10-22 20:58 | 128 | TFUS | 1364684 | 41340480819 | 616 | ENOI | 6 | 2 | EARM | Equipment Failure - Crossarm | N | Changed out Xarm | -90.0275 | 29.9827 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-22 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 42 | 1344188504 | Yes | EAST ORLEANS | FAIR | 54 | 2020-10-22 19:55 | 2020-10-22 20:31 | 2020-10-22 20:49 | 2268 | LFUS | 74488 | 4115847718 | 616 | ENOI | 6 | 42 | EPOL | Equipment Failure - Pole | N | POLE ON FIRE | -90.0332 | 29.9728 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-22 | DLIN | D | Council District D | Jared Brossett | 70117 | 10
2020 | 1 | 1344189090 | Yes | ORLEANS | FAIR | 52 | 2020-10-22 20:56 | 2020-10-22 21:00 | 2020-10-22 21:48 | 52 | SERV | SERVICE | 38024459942 | 2013 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | Open ami meter | -90.133 | 29.9262 | Other | Service Conductor | Other | 2020-10-22 | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 10
2020 | 8 | 1344195526 | Yes | EAST ORLEANS | FAIR | 116 | 2020-10-23 07:51 | 2020-10-23 10:00 | 2020-10-23 09:47 | 928 | XFMR | 646302 | 44360508377 | 2213 | ENOI | 6 | 8 | ETRD | Equipment Failure - Transformer | N | need crew to change transformer | -89.9312 | 30.0575 | Equipment Failure | Transformer | Equipment Failure | 2020-10-23 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 180 | 1344214299 | Yes | ORLEANS | RAIN | 133 | 2020-10-23 13:05 | 2020-10-23 15:06 | 2020-10-23 15:18 | 23940 | LFUS | 27677 | 4025648435 | 1708 | ENOI | 1 | 180 | EARM | Equipment Failure - Crossarm | N | changed arm and picked up phase back in lights | -90.0618 | 29.9927 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 237 | 1344221327 | Yes | ORLEANS | RAIN | 103 | 2020-10-23 14:33 | 2020-10-23 14:43 | 2020-10-23 16:16 | 24411 | LFUS | 38003 | 3986247643 | 907 | ENOI | 1 | 237 | EARR | Equipment Failure - Arrestor | N | bad arrestor changed out | -90.0742 | 29.971 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-23 | DLIN | D | Council District D | Jared Brossett | 70116 | 10
2020 | 1117 | 1344233870 | Yes | EAST ORLEANS | THDR | 49 | 2020-10-23 15:16 | 2020-10-23 16:04 | 2020-10-23 16:05 | 54733 | DIS | 14735 | 4033949066 | 512 | ENOI | 6 | 1117 | EARR | Equipment Failure - Arrestor | N | replaced bad arrestor | -90.0589 | 30.01 | Equipment Failure | Disconnect Switch | Equipment Failure | 2020-10-23 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 12 | 1344245380 | Yes | EAST ORLEANS | THDR | 178 | 2020-10-23 17:08 | 2020-10-23 17:08 | 2020-10-23 20:06 | 2136 | TFUS | 1290883 | 41595494360 | 1010 | ENOI | 6 | 12 | EARM | Equipment Failure - Crossarm | N |  | -90.019 | 30.0197 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-23 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 83 | 1344251402 | Yes | ORLEANS | FAIR | 61 | 2020-10-23 17:44 | 2020-10-23 18:13 | 2020-10-23 18:45 | 5063 | LFUS | 21506 | 3915246393 | 1925 | ENOI | 1 | 83 | EARM | Equipment Failure - Crossarm | N | burning crossarm | -90.0974 | 29.9368 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-23 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 1 | 1344263748 | Yes | ORLEANS | THDR | 63 | 2020-10-23 19:57 | 2020-10-23 19:57 | 2020-10-23 21:00 | 63 | SERV | SERVICE | 38763459544 | 1921 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | spliced service | -90.1099 | 29.925 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-23 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 32 | 1344271536 | Yes | EAST ORLEANS | FAIR | 224 | 2020-10-23 21:16 | 2020-10-23 22:21 | 2020-10-24 01:01 | 7168 | LFUS | 27049 | 4800751170 | 1204 | ENOI | 6 | 32 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.8158 | 30.0653 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-23 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 3 | 1344296374 | Yes | EAST ORLEANS | FAIR | 259 | 2020-10-24 07:30 | 2020-10-24 07:30 | 2020-10-24 11:49 | 544 | RCLR | 35432 | 4484649798 | 1601 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | Scheduled Interruption, crew replacing several xarms | -89.9163 | 30.0287 | Scheduled Interruption | Recloser | Scheduled Interruption | 2020-10-24 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 32 | 1344296766 | Yes | EAST ORLEANS | FAIR | 238 | 2020-10-24 07:51 | 2020-10-24 07:51 | 2020-10-24 11:49 | 7616 | DIS | 25589 | 4504149968 | 1205 | ENOI | 6 | 32 | SCHD | Scheduled Interruption | N | Scheduled Interruption, crew replacing several xarms | -89.9101 | 30.0333 | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | 2020-10-24 | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 10
2020 | 2532 | 1344300830 | Yes | ORLEANS | FAIR | 9 | 2020-10-24 09:34 | 2020-10-24 09:43 | 2020-10-24 09:43 | 22788 | SBKR | 1924 | 3909545682 | 1924 | ENOI | 1 | 2532 | EMER | Emergency Switching | N | Emergency Switching | -90.0994 | 29.9173 | Other | Substation Breaker | Emergency Switching | 2020-10-24 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 1 | 1344301517 | Yes | EAST ORLEANS | FAIR | 330 | 2020-10-24 09:48 | 2020-10-24 12:54 | 2020-10-24 15:19 | 330 | SERV | SERVICE | 40523476314 | 623 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N |  | -90.0534 | 29.9705 | Equipment Failure | Service Conductor | Equipment Failure | 2020-10-24 | DLIN | C | Council District C | Kristin Palmer | 70117 | 10
2020 | 1797 | 1344303082 | Yes | ORLEANS | FAIR | 33 | 2020-10-24 09:52 | 2020-10-24 10:24 | 2020-10-24 10:25 | 62895 | DIS | 23963 | 3918846073 | 1924 | ENOI | 1 | 1797 | EMER | Emergency Switching | N | Emergency Switching | -90.0963 | 29.9281 | Other | Disconnect Switch | Emergency Switching | 2020-10-24 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 735 | 1344301915 | Yes | ORLEANS | FAIR | 349 | 2020-10-24 09:52 | 2020-10-24 15:41 | 2020-10-24 15:41 | 256515 | SBKR | 1924 | 3909545682 | 1924 | ENOI | 1 | 735 | VLGL | Tree/Limb Growing Inside R.O.W. | N | limb fell on line and broke switch at switch 23881 biles crew to fix | -90.0967 | 29.9278 | Vegetation | Substation Breaker | Vegetation | 2020-10-24 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 93 | 1344315394 | Yes | EAST ORLEANS | FAIR | 115 | 2020-10-24 15:05 | 2020-10-24 16:08 | 2020-10-24 17:00 | 10695 | LFUS | 17971 | 4163749296 | 1001 | ENOI | 6 | 93 | EPOL | Equipment Failure - Pole | N | broke 45 ft pole | -90.0176 | 30.016 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-24 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 1 | 1344322837 | Yes | ORLEANS | FAIR | 92 | 2020-10-24 18:24 | 2020-10-24 18:24 | 2020-10-24 19:56 | 92 | SERV | SERVICE | 39600480218 | 1711 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | Open ami meter | -90.0826 | 29.9816 | Other | Service Conductor | Other | 2020-10-24 | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 10
2020 | 3039 | 1344336892 | Yes | EAST ORLEANS | FAIR | 101 | 2020-10-25 07:08 | 2020-10-25 08:47 | 2020-10-25 08:49 | 306939 | SBKR | 623 | 4081748423 | 623 | ENOI | 6 | 3039 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | S&WB crane cleaning out canal at Peoples & Florida hit feeder cauing it to burn down. | -90.044 | 29.9922 | Public Damage | Substation Breaker | Public Damage | 2020-10-25 | DLIN | D | Council District D | Jared Brossett | 70126 | 10
2020 | 11 | 1344344105 | Yes | ORLEANS | FAIR | 97 | 2020-10-25 11:06 | 2020-10-25 11:19 | 2020-10-25 12:43 | 1067 | TFUS | 79295 | 38731462297 | 1926 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | unwrapped secondary off of guy wire and repaired lateral switch bottom riser | -90.1108 | 29.9325 | Other | Transformer Fuse | Other | 2020-10-25 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 90 | 1344360493 | Yes | EAST ORLEANS | FAIR | 170 | 2020-10-25 22:26 | 2020-10-26 00:22 | 2020-10-26 01:16 | 15300 | RCLR | 35340 | 42415492357 | 1607 | ENOI | 6 | 90 | VHCL | Vehicle | N | vehicle hit and broke feeder pole | -89.9931 | 30.014 | Public Damage | Recloser | Public Damage | 2020-10-25 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 6 | 1344365307 | Yes | ORLEANS | FAIR | 149 | 2020-10-26 07:14 | 2020-10-26 07:14 | 2020-10-26 09:43 | 894 | TFUS | 73716 | 38972467670 | 1553 | ENOI | 1 | 6 | ECON | Equipment Failure - Connector / Sleeve | N | part power do to load wire burning up in meter pan electrician on sight to fix problem | -90.1029 | 29.9472 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-26 | DLIN | B | Council District B | Jay Banks | 70125 | 10
2020 | 33 | 1344365523 | Yes | EAST ORLEANS | FAIR | 34 | 2020-10-26 07:28 | 2020-10-26 07:52 | 2020-10-26 08:01 | 1122 | SBKR | 2326 | 4214747796 | 2326 | ENOI | 6 | 33 | VHCL | Vehicle | N | truck pulled down pole, PID chg to NO, related to #1344365693 (dgault) | -90.0022 | 29.9745 | Public Damage | Substation Breaker | Public Damage | 2020-10-26 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 10
2020 | 6 | 1344365693 | Yes | EAST ORLEANS | FAIR | 568 | 2020-10-26 07:33 | 2020-10-26 07:39 | 2020-10-26 17:01 | 3408 | TFUS | 73469 | 41964478771 | 2347 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | replaced pole | -90.0077 | 29.9767 | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | 2020-10-26 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 10
2020 | 5 | 1344365786 | Yes | EAST ORLEANS | FAIR | 495 | 2020-10-26 07:40 | 2020-10-26 07:40 | 2020-10-26 15:55 | 2475 | TFUS | 1550272 | 41921478296 | 2325 | ENOI | 6 | 5 | VHCL | Vehicle | N | truck pulled down pole, PID chg to NO, related to #1344365693 (dgault) | -90.0091 | 29.9755 | Public Damage | Transformer Fuse | Public Damage | 2020-10-26 | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 10
2020 | 2 | 1344368962 | Yes | ORLEANS | FAIR | 185 | 2020-10-26 08:56 | 2020-10-26 08:56 | 2020-10-26 12:01 | 370 | TFUS | 61733 | 39146461882 | 1924 | ENOI | 1 | 2 | ECON | Equipment Failure - Connector / Sleeve | N | changed conections at pole | -90.0976 | 29.9313 | Equipment Failure | Transformer Fuse | Equipment Failure | 2020-10-26 | DLIN | B | Council District B | Jay Banks | 70115 | 10
2020 | 1 | 1344374186 | Yes | EAST ORLEANS | FAIR | 280 | 2020-10-26 11:16 | 2020-10-26 11:16 | 2020-10-26 15:56 | 280 | TFUS | 1028862 | 4226148755 | 1612 | ENOI | 6 | 1 | VHCL | Vehicle | N | Guy wire hit by grass cutter-- Repaired guy wire on transformer pole. NO PID REQUIRED PER NETWORK. JVICKNAIR | -89.9982 | 30.0009 | Public Damage | Transformer Fuse | Public Damage | 2020-10-26 | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 10
2020 | 17 | 1344381710 | Yes | EAST ORLEANS | FAIR | 267 | 2020-10-26 14:16 | 2020-10-26 17:59 | 2020-10-26 18:43 | 4539 | LFUS | 89081 | 4036348774 | 1702 | ENOI | 6 | 17 | EPOL | Equipment Failure - Pole | N | replaced pole | -90.0582 | 30.002 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-26 | DLIN | D | Council District D | Jared Brossett | 70122 | 10
2020 | 1 | 1344402393 | Yes | EAST ORLEANS | FAIR | 47 | 2020-10-27 09:07 | 2020-10-27 09:36 | 2020-10-27 09:54 | 47 | SWIT | 36877 | 4369550041 | 1609 | ENOI | 6 | 1 | SCHD | Scheduled Interruption | N | Opened for crew to install primary jumpers in Cubicles 363 & 440 | -97.0758 | 27.9066 | Scheduled Interruption | Switch | Scheduled Interruption | 2020-10-27 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 7 | 1344402477 | Yes | EAST ORLEANS | FAIR | 104 | 2020-10-27 09:09 | 2020-10-27 09:09 | 2020-10-27 10:53 | 728 | VFI | 27054 | 4359950142 | 2214 | ENOI | 6 | 7 | SCHD | Scheduled Interruption | N | Opened for crew to make up primary jumpers in Cubicles 363 and 440 | -97.0758 | 27.9066 | Scheduled Interruption | Vacuum Fault Interrupter | Scheduled Interruption | 2020-10-27 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 229 | 1344404101 | Yes | EAST ORLEANS | FAIR | 10 | 2020-10-27 09:55 | 2020-10-27 10:07 | 2020-10-27 10:05 | 2290 | SBKR | 1609 | 4351549757 | 1609 | ENOI | 6 | 229 | EPRI | Equipment Failure - Primary Conductor | N | found second fault between Cubicles 363 and 440 | -89.9583 | 30.028 | Equipment Failure | Substation Breaker | Equipment Failure | 2020-10-27 | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 10
2020 | 933 | 1344420095 | Yes | EAST ORLEANS | FAIR | 79 | 2020-10-27 16:12 | 2020-10-27 17:24 | 2020-10-27 17:31 | 73707 | RCLR | 23216 | 4406549717 | 1601 | ENOI | 6 | 933 | EOSC | Equipment Failure - Shield Conductor | N | Shield wire came down across phases | -89.9408 | 30.0267 | Equipment Failure | Recloser | Equipment Failure | 2020-10-27 | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 10
2020 | 75 | 1344423526 | Yes | ORLEANS | FAIR | 81 | 2020-10-27 18:04 | 2020-10-27 19:10 | 2020-10-27 19:25 | 6075 | LFUS | 47654 | 3921046887 | 1553 | ENOI | 1 | 75 | ECNS | Equipment Failure - Connector Sleeve | N | riser came out of switch dropped out lateral to put riser back in and reenergized lateral | -90.0954 | 29.9504 | Equipment Failure | Line Fuse | Equipment Failure | 2020-10-27 | DLIN | B | Council District B | Jay Banks | 70125 | 10