## CI Cause Category Details
Row Labels | Sum of CI
Animal | 12238
Animal - Bird Reportable Inc (Mortality or Injury) | 9868
Animal - Other (Describe in Remarks Field) | 1373
Animal - Squirrel | 997
Equipment Failure | 54598 | 86341 | Distribution CI's, slide 1 of presentation
Breaker - Oil | 43 | 19913 | Scheduled Interruption & Emergency Switching CI's, slide 4 of presentation
Cable Failure in manhole | 30 | 17049 | Transmission CI's, slide 9 of presentation
Equipment Failure - Air Break / Disconnect Switch | 23 | 123303 | Total CI's reported January - June 2020
Equipment Failure - Arrestor | 1770
Equipment Failure - Automatic Sleeve | 1168
Equipment Failure - Capacitor | 1691
Equipment Failure - Connector / Sleeve | 194
Equipment Failure - Connector Sleeve | 5763
Equipment Failure - Crossarm | 13046
Equipment Failure - Elbow | 1098
Equipment Failure - Fuse Link | 1106
Equipment Failure - Fuse Switch | 500
Equipment Failure - Insulator | 671
Equipment Failure - Metering | 10
Equipment Failure - Neutral / Shield Conductor | 16
Equipment Failure - Other (Describe in Remarks Fie | 577
Equipment Failure - Pole | 1852
Equipment Failure - Primary Conductor | 11561
Equipment Failure - Shield Conductor | 56
Equipment Failure - Transformer | 2047
Secondary/Service Conductor | 137
Slack Conductor / Loose Connection | 2226
Substation Bushing - Breaker | 7169
Switching Cabinet | 1841
Transformer Splicing chamber failure | 3
Foreign Trouble | 231
Foreign Trouble - Neighboring Utility | 231
Human Error | 5153
Company - Distribution Business (Describe in remar | 37
Entergy Distribution Contractor (Describe in rema | 134
Human Error - Company (Describe in Remarks Field) | 3336
Improper Design (Describe in Remarks Field) | 1574
Mis-Coordination (Describe in remarks) | 72
Lightning | 7561
Lightning | 7561
Other | 23986
Corrosion | 35
Emergency Switching | 13809
Fire - Other (Describe in Remarks Field) | 167
Foreign Objects (Describe in Remarks Field) | 7348
Inspected Unknown | 2389
Meter Exchange | 9
Unknown - Under Investigation | 229
Public Damage | 8618
Human Error - Non-Entergy Workers (Describe in Rem | 204
Malicious Damage | 1
Vehicle | 8413
Scheduled Interruption | 6104
Scheduled Interruption | 6104
Vegetation | 4814
Overhanging Limb | 169
Tree On Line Outside R.O.W | 1083
Tree/Limb Growing Inside R.O.W. | 277
Vine Growing into Line | 3285
Grand Total | 123303

## CI by District & Weather
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
Sum of CI
DISTRICT | WEATHER_CONDITION | Summary Cause Updated | CAUSE_DESC | MONTH | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 12786 | 10.37%
Council District B | [9 empty] | 40312 | 32.69%
Council District C | [9 empty] | 4835 | 3.921%
Council District D | [9 empty] | 38251 | 31.02%
Council District E | [9 empty] | 27119 | 21.99%
Grand Total | [9 empty] | 123303 | 100%

## CI by District & Zip Code
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
Sum of CI
DISTRICT | ZIP | Summary Cause Updated | CAUSE_DESC | MONTH | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 12786 | 10.37%
Council District B | [9 empty] | 40312 | 32.69%
Council District C | [9 empty] | 4835 | 3.921%
Council District D | [9 empty] | 38251 | 31.02%
Council District E | [9 empty] | 27119 | 21.99%
Grand Total | [9 empty] | 123303 | 100%

## data
'Date Table'[Year] | CI | 'Outages_NOCC-CAT'[Year] | CASE_ID | In_NOCC_Reporting | NETWORK_NAME | WEATHER_CONDITION | TOTAL_DURATION_MINUTES | FIRST_CALL_DATE_TIME | ACTUAL_CUSTOMER_MINUTES | DEVICE_TYPE | DEVICE_ID | DISTRIBUTION_LOCATION_NBR | FEEDER_ID | Fdr_Owner | LOCAL_OFFICE_NBR | TOTAL_CUSTOMERS_AFFECTED | CAUSE | CAUSE_DESC | MAJOR_EVENT | REMARKS | LONGITUDE | LATITUDE | AdvPeriod | V_Reliability_Custs_Legal_Entity.Cust_SRVD | Days to Include | SUMMARY_CAUSE | DEVICE_TYPE_DESC | Summary Cause Updated | System | DISTRICTID | DISTRICT | REPNAME | ZIP | MONTH
2020 | 2835 | 2020 | 1324909780 | Yes | ORLEANS | FAIR | 6 | 2020-03-04 | 17010 | SBKR | 2147 | 4012946119 | 2147 | ENOI | 1 | 2835 | VINE | Vine Growing into Line | N | cause has been confirmed that "Root Cause" was vines on bayonet & primary x-arm | -90.0851 | 29.9198 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Substation Breaker | Vegetation | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 2835 | 2020 | 1324968746 | Yes | ORLEANS | FAIR | 6 | 2020-03-04 | 17010 | SBKR | 2147 | 4012946119 | 2147 | ENOI | 1 | 2835 | EMER | Emergency Switching | N | crossarm at location on fire de-energized to put fire out Chippewa at Pleasant | -90.0851 | 29.9198 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 27 | 2020 | 1333959403 | Yes | ORLEANS | FAIR | 6 | 2020-06-28 | 162 | LFUS | 36854 | 3915045734 | 1922 | ENOI | 1 | 27 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0977 | 29.9187 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 999 | 2020 | 1328247232 | Yes | EAST ORLEANS | THDR | 7 | 2020-04-18 | 6993 | SBKR | 2215 | 4334550772 | 2215 | ENOI | 6 | 999 | EPOL | Equipment Failure - Pole | N | Pole burned in half:; Recloser went out at the same time: | -89.9633 | 30.0559 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 1959 | 2020 | 1333439250 | Yes | ORLEANS | THDR | 7 | 2020-06-22 | 13713 | SBKR | 2027 | 3848547391 | 2027 | ENOI | 1 | 1959 | EMER | Emergency Switching | N | had to emergency switch due to crossarm braces breaking and phase laying on arm due to squirrel at Burdette & Collipissa | -90.1127 | 29.959 | NP | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 58 | 2020 | 1330847188 | Yes | EAST ORLEANS | FAIR | 8 | 2020-05-17 | 464 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 58 | EMER | Emergency Switching | N | Taken out for safety of crew to replace a failed sub. trans | -89.9561 | 30.0595 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Emergency Switching | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 7 | 2020 | 1332848514 | Yes | ORLEANS | FAIR | 9 | 2020-06-09 | 63 | TFUS | 66220 | 39421460869 | 2147 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0889 | 29.9282 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 8 | 2020 | 1330847277 | Yes | EAST ORLEANS | FAIR | 10 | 2020-05-17 | 80 | TFUS | 677437 | 43644509686 | 2217 | ENOI | 6 | 8 | EMER | Emergency Switching | N | Taken out for safety of crew to switch lateral back to normal configuration | -89.9538 | 30.0612 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Emergency Switching | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 1451 | 2020 | 1323244545 | Yes | ORLEANS | FAIR | 11 | 2020-01-27 | 15961 | SBKR | 1554 | 3950446990 | 1554 | ENOI | 1 | 1451 | UNKN | Inspected Unknown | N | serviceman did not find anything on line; closed bkr in and holding | -90.086 | 29.9532 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 9 | 2020 | 1326232294 | Yes | ORLEANS | FAIR | 11 | 2020-04-02 | 99 | TFUS | 25627 | 40043493837 | 503 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0681 | 30.0188 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 3 | 2020 | 1332038205 | Yes | ORLEANS | FAIR | 11 | 2020-05-30 | 33 | TFUS | 59150 | 39069458193 | 1923 | ENOI | 1 | 3 | ASQL | Animal - Squirrel | N | refused | -90.1003 | 29.9211 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 6 | 2020 | 1322735719 | Yes | EAST ORLEANS | FAIR | 12 | 2020-01-14 | 72 | TFUS | 73176 | 41551474793 | 2347 | ENOI | 6 | 6 | ESEC | Secondary/Service Conductor | N | made repairs to trans | -90.0211 | 29.966 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 4 | 2020 | 1332172550 | Yes | EAST ORLEANS | FAIR | 12 | 2020-06-02 | 48 | TFUS | 1522713 | 41850474478 | 2347 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0116 | 29.965 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 3 | 2020 | 1324170082 | Yes | EAST ORLEANS | FAIR | 15 | 2020-02-19 | 45 | TFUS | 62400 | 42950505451 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | crew is onsite | -89.976 | 30.0498 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 6 | 2020 | 1324396947 | Yes | EAST ORLEANS | FAIR | 15 | 2020-02-23 | 90 | TFUS | 73309 | 41856476262 | 2325 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0114 | 29.97 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 2365 | 2020 | 1323253767 | Yes | ORLEANS | FAIR | 17 | 2020-01-27 | 40205 | SBKR | 907 | 3897447410 | 907 | ENOI | 1 | 2365 | EMER | Emergency Switching | N | had to drop feeder for transformers on fire | -90.1026 | 29.9648 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70119 | 1
2020 | 14 | 2020 | 1324463884 | Yes | ORLEANS | FAIR | 17 | 2020-02-24 | 238 | LFUS | 21578 | 3886948465 | 904 | ENOI | 1 | 14 | EARM | Equipment Failure - Crossarm | N |  | -90.1055 | 29.9938 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 21 | 2020 | 1325526619 | Yes | ORLEANS | FAIR | 18 | 2020-03-18 | 378 | TFUS | 729628 | 39681459752 | 2146 | ENOI | 1 | 21 | ECNS | Equipment Failure - Connector Sleeve | N | jumper repaired on xfmr | -90.0807 | 29.9253 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 351 | 2020 | 1326453968 | Yes | EAST ORLEANS | FAIR | 18 | 2020-04-07 | 6318 | SWIT | 26183 | 4438750548 | 1609 | ENOI | 6 | 351 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Switch | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 841 | 2020 | 1321761982 | Yes | EAST ORLEANS | FAIR | 19 | 2020-01-06 | 15979 | SBKR | 1602 | 4351549756 | 1602 | ENOI | 6 | 841 | ESWC | Switching Cabinet | N | Fault in CUB 554 caused outage | -89.9583 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 17 | 2020 | 1323822707 | Yes | ORLEANS | FAIR | 19 | 2020-02-11 | 323 | TFUS | 642509 | 39383459492 | 2147 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | scheduled outage | -90.0902 | 29.9247 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 45 | 2020 | 1325284832 | Yes | ORLEANS | FAIR | 20 | 2020-03-11 | 900 | LFUS | 33186 | 3975145935 | 2147 | ENOI | 1 | 45 | SCHD | Scheduled Interruption | N | crew has an ouitage setup until 10:00 am | -90.0787 | 29.924 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 47 | 2020 | 1328262165 | Yes | ORLEANS | THDR | 20 | 2020-04-18 | 940 | LFUS | 37999 | 3976747636 | 907 | ENOI | 1 | 47 | EARM | Equipment Failure - Crossarm | N | Crew On Site Working | -90.0774 | 29.9708 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 4 | 2020 | 1332562157 | Yes | EAST ORLEANS | FAIR | 20 | 2020-06-07 | 80 | LFUS | 37126 | 4080148127 | 622 | ENOI | 6 | 4 | EMER | Emergency Switching | N |  | -90.0444 | 29.9843 | NP | 210557 | Jan1 to Yesterday | Other | Line Fuse | Emergency Switching | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 36 | 2020 | 1333174135 | Yes | EAST ORLEANS | FAIR | 20 | 2020-06-17 | 720 | LFUS | 37015 | 4208449910 | 2212 | ENOI | 6 | 36 | HECD | Company - Distribution Business (Describe in remar | N | Underground crew was switching the loop back to normal when the fuse blew Cable was tested and was good prior to switching Crew refused lateral Customers back in lights | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Human Error | Line Fuse | Human Error | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 313 | 2020 | 1323305072 | Yes | ORLEANS | FAIR | 21 | 2020-01-29 | 6573 | DIS | 25494 | 3882647318 | 2011 | ENOI | 1 | 313 | EMER | Emergency Switching | N | SHIELD WIRE DOWN | -90.1072 | 29.9624 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 222 | 2020 | 1323655478 | Yes | EAST ORLEANS | WIND | 21 | 2020-02-07 | 4662 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 222 | EARM | Equipment Failure - Crossarm | N |  | -90.0021 | 29.9747 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 68 | 2020 | 1324566317 | Yes | ORLEANS | FAIR | 21 | 2020-02-26 | 1428 | LFUS | 33137 | 3866247573 | 2026 | ENOI | 1 | 68 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1125 | 29.9694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 4 | 2020 | 1324676386 | Yes | EAST ORLEANS | FAIR | 21 | 2020-02-28 | 84 | TFUS | 60105 | 42939493496 | 1604 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9765 | 30.0171 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1398 | 2020 | 1325215886 | Yes | EAST ORLEANS | FAIR | 21 | 2020-03-09 | 29358 | SBKR | 2217 | 4334250776 | 2217 | ENOI | 6 | 1398 | VHCL | Vehicle | N | pole hit at morrison and gannon RELATED TO TKT# 1325216450 (AKS0 | -89.9634 | 30.056 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Substation Breaker | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 1 | 2020 | 1321890202 | Yes | ORLEANS | FAIR | 22 | 2020-01-09 | 22 | SERV | METER | 38903461840 | 1914 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | Changed **TFUS 77590 * 11 to SERV 77590 * 1** --- meter was not all rthe way into meter socket. per 310 treed3 | -90.1052 | 29.9311 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 1 | 2020 | 1324005232 | Yes | ORLEANS | FAIR | 23 | 2020-02-15 | 23 | SECO | METER | 39473478021 | 912 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | 3128 dumaine AMI mtr had open indication AMOC doesnt work weekends and DOC doesnt have control to close mtrs changed to mtr#8180311 sn-57104979 r-00000 | -90.0866 | 29.9755 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Secondary Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 2
2020 | 5 | 2020 | 1326080529 | Yes | ORLEANS | FAIR | 23 | 2020-03-30 | 115 | DIS | 42102 | 3953347149 | 1506 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N |  | -90.085 | 29.9575 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 14 | 2020 | 1326717859 | Yes | ORLEANS | THDR | 24 | 2020-04-10 | 336 | TFUS | 1002285 | 39996464841 | 2137 | ENOI | 1 | 14 | LGHT | Lightning | N | taken out by weather refused ok | -90.0706 | 29.9392 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 42 | 2020 | 1333125808 | Yes | EAST ORLEANS | FAIR | 24 | 2020-06-16 | 1008 | LFUS | 16057-F | 4167149321 | 1001 | ENOI | 6 | 42 | SCHD | Scheduled Interruption | N |  | -90.0168 | 30.0167 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 119 | 2020 | 1323549856 | Yes | EAST ORLEANS | THDR | 25 | 2020-02-05 | 2975 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 119 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Crews found balloons on feeder on Florida & Egania | -90.0441 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 22 | 2020 | 1331192284 | Yes | ORLEANS | FAIR | 25 | 2020-05-22 | 550 | TFUS | C72989 | 40049476465 | 1712 | ENOI | 1 | 22 | FOTH | Fire - Other (Describe in Remarks Field) | N | 2 alarm fire | -90.0686 | 29.9711 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 10 | 2020 | 1334053395 | Yes | ORLEANS | FAIR | 25 | 2020-06-29 | 250 | TFUS | 613211 | 39853488253 | 1704 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | contractors working on pole have xfmr out | -90.0742 | 30.0036 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 1917 | 2020 | 1323805621 | Yes | ORLEANS | FAIR | 26 | 2020-02-11 | 49842 | SBKR | 2146 | 4012946121 | 2146 | ENOI | 1 | 1917 | EMER | Emergency Switching | N | dropped out for the crew , whencrew was in the process of closing in a laterial the switch came off of the arm and was being supported by the switch stick. | -90.0665 | 29.9291 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 7 | 2020 | 1329047348 | Yes | EAST ORLEANS | FAIR | 26 | 2020-04-25 | 182 | TFUS | 54299 | 43126496588 | 1611 | ENOI | 6 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9704 | 30.0254 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 234 | 2020 | 1323084559 | Yes | EAST ORLEANS | FAIR | 27 | 2020-01-21 | 3510 | RCLR | 37793 | 4946452184 | 1204 | ENOI | 6 | 234 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.7693 | 30.0927 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 118 | 2020 | 1324456985 | Yes | EAST ORLEANS | FAIR | 28 | 2020-02-24 | 3304 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 118 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Serviceman patrolled feeder the next morning & found balloons on line at Florida & Gorden Sts. Removed okay | -90.0441 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 76 | 2020 | 1327925033 | Yes | EAST ORLEANS | FAIR | 28 | 2020-04-15 | 2128 | LFUS | 21116 | 4094548019 | 621 | ENOI | 6 | 76 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0402 | 29.981 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 1 | 2020 | 1326497490 | Yes | ORLEANS | FAIR | 29 | 2020-04-08 | 29 | TFUS | 30704 | 38166472777 | 2022 | ENOI | 1 | 1 | HECD | Company - Distribution Business (Describe in remar | N | Switched out for scheduled outage. Outage had been cancelled previously. | -90.1283 | 29.9614 | 19-YTD20 | 210557 | Jan1 to Yesterday | Human Error | Transformer Fuse | Human Error | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 56 | 2020 | 1326730930 | Yes | EAST ORLEANS | THDR | 29 | 2020-04-10 | 1624 | RCLR | 37793 | 4946452184 | 1204 | ENOI | 6 | 56 | EPOL | Equipment Failure - Pole | N | 2 broke poles, isulated and got recloser back in | -89.7692 | 30.0928 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 159 | 2020 | 1332243281 | Yes | EAST ORLEANS | FAIR | 29 | 2020-06-03 | 4611 | LFUS | 27893 | 4082548786 | 625 | ENOI | 6 | 159 | SCHD | Scheduled Interruption | N | Crew working at location | -90.0435 | 30.0021 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 69 | 2020 | 1334136458 | Yes | ORLEANS | FAIR | 29 | 2020-06-30 | 2001 | LFUS | 17782 | 3855249274 | 411 | ENOI | 1 | 69 | EARM | Equipment Failure - Crossarm | N |  | -90.115 | 30.0162 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 132 | 2020 | 1333078694 | Yes | EAST ORLEANS | FAIR | 30 | 2020-06-15 | 3960 | LFUS | 81486 | 4250450410 | 2215 | ENOI | 6 | 132 | ASQL | Animal - Squirrel | N |  | -89.9899 | 30.0464 | NP | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 28 | 2020 | 1334134211 | Yes | ORLEANS | FAIR | 31 | 2020-06-30 | 868 | LFUS | 33731 | 3954748313 | 1711 | ENOI | 1 | 28 | EARM | Equipment Failure - Crossarm | N | crew replace crossarm behind lateral | -90.0841 | 29.9894 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 1462 | 2020 | 1324238968 | Yes | ORLEANS | RAIN | 32 | 2020-02-20 | 46784 | SBKR | 1702 | 4024148726 | 1702 | ENOI | 1 | 1462 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Serviceman found a piece of molding fell onto primary, cleared object & feeder restored okay | -90.0621 | 30.0007 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 16 | 2020 | 1326349496 | Yes | ORLEANS | FAIR | 32 | 2020-04-05 | 512 | LFUS | 28046 | 3913346967 | 1553 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0978 | 29.9527 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 2 | 2020 | 1332305188 | Yes | EAST ORLEANS | FAIR | 32 | 2020-06-04 | 64 | DIS | 16212 | 4126949011 | 507 | ENOI | 6 | 2 | EABS | Equipment Failure - Air Break / Disconnect Switch | N | repaired | -90.0295 | 30.0081 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 36 | 2020 | 1321744962 | Yes | EAST ORLEANS | FAIR | 34 | 2020-01-05 | 1224 | LFUS | 62597 | 4159649935 | 2212 | ENOI | 6 | 36 | ASQL | Animal - Squirrel | N | squirrel took out over head portion thata casuse outage for underground dwillin | -90.0189 | 30.0333 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 52 | 2020 | 1322857299 | Yes | EAST ORLEANS | FAIR | 34 | 2020-01-16 | 1768 | LFUS | 24311 | 4173149985 | 2212 | ENOI | 6 | 52 | VINE | Vine Growing into Line | N | vines grew into b phase cleaared as muc as i could but someone needs to coem clear vines road out lateral all lights came back on as i can tell | -90.0146 | 30.0348 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 188 | 2020 | 1325394639 | Yes | ORLEANS | FAIR | 34 | 2020-03-14 | 11656 | DIS | 23640 | 3850345854 | 1914 | ENOI | 1 | 188 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up and phase on ground | -90.118 | 29.9223 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 88 | 2020 | 1322332691 | Yes | ORLEANS | THDR | 35 | 2020-01-11 | 3080 | LFUS | 37781 | 3988848138 | 1709 | ENOI | 1 | 88 | LGHT | Lightning | N | ispected unknown refused advise jcox7 | -90.0735 | 29.9846 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 2 | 2020 | 1325891147 | Yes | EAST ORLEANS | FAIR | 35 | 2020-03-27 | 70 | XFMR | 79978 | 4290350439 | 2216 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N | crew changing out transformer. | -89.9774 | 30.0469 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 130 | 2020 | 1326339990 | Yes | EAST ORLEANS | FAIR | 35 | 2020-04-05 | 4550 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 130 | EINS | Equipment Failure - Insulator | N |  | -90.044 | 29.9708 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 1 | 2020 | 1321689819 | Yes | ORLEANS | RAIN | 36 | 2020-01-03 | 36 | SERV | SERVICE | 38483463662 | 2024 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | changed conector at pole voltage check good gkathma | -90.1185 | 29.9362 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 5 | 2020 | 1321924209 | Yes | ALGIERS ELEC ONLY | FAIR | 36 | 2020-01-10 | 180 | LFUS | 5534-F | 4462845638 | W1715 | ENOI | 81 | 5 | EARM | Equipment Failure - Crossarm | N | Crew to replace cross-arm downstream of this device, per Zach Washington...........PC | -89.9246 | 29.9144 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 2 | 2020 | 1322818414 | Yes | EAST ORLEANS | FAIR | 36 | 2020-01-15 | 72 | XFMR | 79392 | 49613525017 | 1204 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N |  | -89.7641 | 30.1015 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 1288 | 2020 | 1323526756 | Yes | ORLEANS | FAIR | 36 | 2020-02-05 | 46368 | DIS | 21967 | 3862946737 | 2024 | ENOI | 1 | 1288 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1138 | 29.9464 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 2
2020 | 69 | 2020 | 1324974438 | Yes | EAST ORLEANS | FAIR | 36 | 2020-03-04 | 2484 | LFUS | 27936 | 4357949598 | 1601 | ENOI | 6 | 69 | EARM | Equipment Failure - Crossarm | N |  | -89.9565 | 30.0236 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 6 | 2020 | 1325363398 | Yes | ORLEANS | FAIR | 36 | 2020-03-13 | 216 | TFUS | 73716 | 38972467670 | 1553 | ENOI | 1 | 6 | AOTH | Animal - Other (Describe in Remarks Field) | N | refused tf squirel got across tf fuse | -90.1029 | 29.9472 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 4 | 2020 | 1333384123 | Yes | EAST ORLEANS | FAIR | 36 | 2020-06-21 | 144 | TFUS | 559321 | 42629493295 | 1604 | ENOI | 6 | 4 | ASQL | Animal - Squirrel | N | refused ok | -89.9863 | 30.0166 | NP | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 16 | 2020 | 1324336355 | Yes | EAST ORLEANS | FAIR | 37 | 2020-02-21 | 592 | TFUS | 54971 | 40370486325 | 1708 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0581 | 29.9981 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1 | 2020 | 1331998631 | Yes | EAST ORLEANS | FAIR | 37 | 2020-05-29 | 37 | SERV | METER | 41960497608 | 2212 | ENOI | 6 | 1 | MTEX | Meter Exchange | N | Contractor in area changing meters cust was not informed meter was being changed Meter change was completed and power back on | -90.0075 | 30.0287 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 3033 | 2020 | 1334007784 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 | 112221 | SUBN | 623 | 4081748423 | 623 | ENOI | 6 | 3033 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.044 | 29.9922 | NP | 210557 | Jan1 to Yesterday | Animal | Substation | Animal | TRANS | D | Council District D | Jared Brossett | 70126 | 6
2020 | 2890 | 2020 | 1334008664 | NO | ORLEANS | FAIR | 37 | 2020-06-29 | 106930 | SUBN | 627 | 4081148423 | 627 | ENOI | 1 | 2890 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0442 | 29.9922 | NP | 210557 | Jan1 to Yesterday | Animal | Substation | Animal | TRANS | D | Council District D | Jared Brossett | 70126 | 6
2020 | 1840 | 2020 | 1334008312 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 | 68080 | SUBN | 622 | 4082448424 | 622 | ENOI | 6 | 1840 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0438 | 29.9922 | NP | 210557 | Jan1 to Yesterday | Animal | Substation | Animal | TRANS | D | Council District D | Jared Brossett | 70126 | 6
2020 | 1050 | 2020 | 1334008170 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 | 38850 | SUBN | 621 | 4082548424 | 621 | ENOI | 6 | 1050 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0438 | 29.9922 | NP | 210557 | Jan1 to Yesterday | Animal | Substation | Animal | TRANS | D | Council District D | Jared Brossett | 70126 | 6
2020 | 713 | 2020 | 1334008015 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 | 26381 | SUBN | 626 | 4081248423 | 626 | ENOI | 6 | 713 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0442 | 29.9922 | NP | 210557 | Jan1 to Yesterday | Animal | Substation | Animal | TRANS | D | Council District D | Jared Brossett | 70126 | 6
2020 | 311 | 2020 | 1334008118 | NO | EAST ORLEANS | FAIR | 37 | 2020-06-29 | 11507 | SUBN | 625 | 4081348423 | 625 | ENOI | 6 | 311 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N |  | -90.0441 | 29.9922 | NP | 210557 | Jan1 to Yesterday | Animal | Substation | Animal | TRANS | D | Council District D | Jared Brossett | 70126 | 6
2020 | 4 | 2020 | 1323272107 | Yes | ORLEANS | FAIR | 38 | 2020-01-28 | 152 | TFUS | 3004438 | 38731464304 | 1926 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Planned outage contractors working per#305 | -90.1105 | 29.938 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 1
2020 | 123 | 2020 | 1324415315 | Yes | ORLEANS | FAIR | 38 | 2020-02-24 | 4674 | LFUS | 27615 | 3972747795 | 615 | ENOI | 1 | 123 | SCHD | Scheduled Interruption | N | crew changing out pole | -90.0786 | 29.9753 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70119 | 2
2020 | 10 | 2020 | 1326747880 | Yes | ORLEANS | THDR | 38 | 2020-04-10 | 380 | TFUS | 58865 | 39943475082 | 1712 | ENOI | 1 | 10 | LGHT | Lightning | N | refused transformer | -90.072 | 29.9673 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 137 | 2020 | 1321931828 | Yes | EAST ORLEANS | FAIR | 39 | 2020-01-10 | 5343 | DIS | 38259 | 4126248306 | 626 | ENOI | 6 | 137 | SCHD | Scheduled Interruption | N | Scheduled Interruption; crew picking up low hanging primary | -90.0301 | 29.9887 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 74 | 2020 | 1326694904 | Yes | EAST ORLEANS | THDR | 39 | 2020-04-09 | 2886 | LFUS | 27758 | 4093547749 | 622 | ENOI | 6 | 74 | EARM | Equipment Failure - Crossarm | N | arm broke on north johnson | -90.0405 | 29.9737 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 100 | 2020 | 1331969611 | Yes | ORLEANS | FAIR | 39 | 2020-05-28 | 3900 | LFUS | 27677 | 4025648435 | 1708 | ENOI | 1 | 100 | VHCL | Vehicle | N | car broke pole and primary down KC - CHGD PID TO NO - RELATED TO #1331974211 (DGAULT) | -90.0618 | 29.9927 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 1 | 2020 | 1321722737 | Yes | ORLEANS | FAIR | 40 | 2020-01-04 | 40 | SERV | SERVICE | 40316487839 | 1701 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Changed **TFUS 58867 5 to SERV 58867 5** --- hot leg burnt at pole dcain2 | -90.0596 | 30.0022 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 315 | 2020 | 1323252770 | Yes | EAST ORLEANS | FAIR | 40 | 2020-01-27 | 12600 | SBKR | 625 | 4081248423 | 625 | ENOI | 6 | 315 | VHCL | Vehicle | N | vehicle hit guy wire and flipped into feeder, removed and back on RELAED TO KT# 1323254789 (AKS) | -90.0442 | 29.9922 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Substation Breaker | Public Damage | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 4 | 2020 | 1327185933 | Yes | ORLEANS | THDR | 40 | 2020-04-12 | 160 | TFUS | 63874 | 38617470487 | 2015 | ENOI | 1 | 4 | EFSW | Equipment Failure - Fuse Switch | N | Riser came out of top of switch repaired | -90.114 | 29.9549 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 21 | 2020 | 1324132510 | Yes | ALGIERS ELEC ONLY | FAIR | 41 | 2020-02-18 | 861 | TFUS | BY149697 | 4115346444 | W1725 | ENOI | 81 | 21 | SCHD | Scheduled Interruption | N | opened transforemr to replace cut out (pwd) | -90.0342 | 29.9376 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 2088 | 2020 | 1326128164 | Yes | ORLEANS | WIND | 41 | 2020-03-31 | 85608 | SBKR | 912 | 3898147404 | 912 | ENOI | 1 | 2088 | SLAK | Slack Conductor / Loose Connection | N | gravier and s clark, high wind, possible slack spans on dog leg of lateral | -90.1023 | 29.9647 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 3 | 2020 | 1326905718 | Yes | EAST ORLEANS | FAIR | 41 | 2020-04-12 | 123 | TFUS | 1324626 | 40667491561 | 502 | ENOI | 6 | 3 | EARM | Equipment Failure - Crossarm | N | sec x arm short..temp safe ..refused trans | -90.0485 | 30.0125 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 1 | 2020 | 1332002483 | Yes | ORLEANS | FAIR | 41 | 2020-05-29 | 41 | SERV | METER | 39610464869 | 2132 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | amoc failed to turn on meter for us again | -90.0827 | 29.9393 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 244 | 2020 | 1333153301 | Yes | EAST ORLEANS | FAIR | 41 | 2020-06-16 | 10004 | RCLR | 92431 | 4143549262 | 1010 | ENOI | 6 | 244 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Baloons | -90.0241 | 30.015 | NP | 210557 | Jan1 to Yesterday | Other | Recloser | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 5 | 2020 | 1329422545 | Yes | ORLEANS | THDR | 42 | 2020-04-29 | 210 | TFUS | 491803 | 38262464952 | 2014 | ENOI | 1 | 5 | VINE | Vine Growing into Line | N | refused transformer OK per A.Bengston - vines growing on transformer | -90.1253 | 29.94 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 56 | 2020 | 1331679281 | Yes | EAST ORLEANS | THDR | 42 | 2020-05-26 | 2352 | LFUS | 21009 | 4043448299 | 613 | ENOI | 6 | 56 | EARR | Equipment Failure - Arrestor | N | removed arrestor and refused lateral | -90.056 | 29.989 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 75 | 2020 | 1333637766 | Yes | ORLEANS | THDR | 42 | 2020-06-24 | 3150 | LFUS | 27800 | 3921945756 | 1922 | ENOI | 1 | 75 | LGHT | Lightning | N | weather | -90.0955 | 29.9192 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 1052 | 2020 | 1333734478 | Yes | EAST ORLEANS | RAIN | 42 | 2020-06-25 | 44184 | SBKR | 510 | 4075449220 | 510 | ENOI | 6 | 1052 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons on primary; removed and closed back bkr | -90.0457 | 30.0141 | NP | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 25 | 2020 | 1330267400 | Yes | ORLEANS | FAIR | 43 | 2020-05-11 | 1075 | TFUS | 715357T | 38980494050 | 402 | ENOI | 1 | 25 | ASQL | Animal - Squirrel | N | SQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.1016 | 30.0197 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 4 | 2020 | 1332896314 | Yes | ORLEANS | FAIR | 43 | 2020-06-10 | 172 | TFUS | 62939 | 39314467651 | 2021 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | scheduled outage, customer was notified | -90.092 | 29.947 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 296 | 2020 | 1333627636 | Yes | EAST ORLEANS | THDR | 43 | 2020-06-24 | 12728 | SBKR | 2223 | 4334850763 | 2223 | ENOI | 6 | 296 | ESLV | Equipment Failure - Automatic Sleeve | N | Wire burned down at an auto sleeve Possible lightning strike | -89.9655 | 30.0597 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 1 | 2020 | 1322173499 | Yes | ORLEANS | WIND | 44 | 2020-01-11 | 44 | SECO | SECONDARY COND | 39729483055 | 627 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Changed **TFUS 9 to TFUS 1** --- loose connection at pole repaired and checked voltage jcox7 | -90.0785 | 29.9892 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Secondary Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 3 | 2020 | 1323551129 | Yes | ORLEANS | WIND | 44 | 2020-02-05 | 132 | TFUS | 76190 | 38463461461 | 1917 | ENOI | 1 | 3 | LGHT | Lightning | N | weather | -90.1191 | 29.9303 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 4 | 2020 | 1326353195 | Yes | ORLEANS | FAIR | 44 | 2020-04-05 | 176 | LFUS | 36687 | 3982147304 | 1511 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0758 | 29.9617 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70112 | 4
2020 | 28 | 2020 | 1327971627 | Yes | ORLEANS | FAIR | 44 | 2020-04-15 | 1232 | LFUS | 33059 | 3895147524 | 903 | ENOI | 1 | 28 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1031 | 29.9681 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 201 | 2020 | 1330344055 | Yes | EAST ORLEANS | FAIR | 44 | 2020-05-11 | 8844 | SBKR | 2347 | 4216047802 | 2347 | ENOI | 6 | 201 | FTNU | Foreign Trouble - Neighboring Utility | N | Feeder burned down caused by AT&T pole set next to primary conductors | -90.0217 | 29.9642 | 19-YTD20 | 210557 | Jan1 to Yesterday | Foreign Trouble | Substation Breaker | Foreign Trouble | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 9 | 2020 | 1330685705 | Yes | EAST ORLEANS | FAIR | 44 | 2020-05-15 | 396 | TFUS | 25629 | 41409497201 | 1010 | ENOI | 6 | 9 | ASQL | Animal - Squirrel | N | Inspected line and saw several squirrels in the vicinity. Refused pot customers back in lights | -90.025 | 30.0276 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 7 | 2020 | 1323551125 | Yes | ORLEANS | WIND | 45 | 2020-02-05 | 315 | TFUS | 1099405 | 39552488027 | 1703 | ENOI | 1 | 7 | LGHT | Lightning | N | weather | -90.0838 | 30.0031 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1536 | 2020 | 1329000225 | Yes | EAST ORLEANS | FAIR | 45 | 2020-04-25 | 69120 | VFI | 27486 | 4366350629 | 2213 | ENOI | 6 | 1536 | HEID | Improper Design (Describe in Remarks Field) | N | Equipment labeled incorrectly from manufacturer: Fdr carrying portion of 2217 & all of Fdr 1603 & Fdr #1609 at the time | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Human Error | Vacuum Fault Interrupter | Human Error | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 7 | 2020 | 1333304996 | Yes | ORLEANS | FAIR | 45 | 2020-06-20 | 315 | TFUS | 71373 | 40138487847 | 1704 | ENOI | 1 | 7 | ECNS | Equipment Failure - Connector Sleeve | N | trans riser off | -90.0654 | 30.0023 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 1 | 2020 | 1329779166 | Yes | EAST ORLEANS | FAIR | 46 | 2020-05-02 | 46 | SERV | METER | 4118648377 | 626 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N |  | -90.0324 | 29.9907 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 387 | 2020 | 1330059994 | Yes | EAST ORLEANS | FAIR | 46 | 2020-05-07 | 17802 | LFUS | 17996 | 4139649803 | 1010 | ENOI | 6 | 387 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | tranformer hanger broke | -90.0252 | 30.0298 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 54 | 2020 | 1332853836 | Yes | EAST ORLEANS | FAIR | 46 | 2020-06-09 | 2484 | LFUS | 27018 | 4356549765 | 1601 | ENOI | 6 | 54 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9566 | 30.0283 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 11 | 2020 | 1334037216 | Yes | EAST ORLEANS | FAIR | 46 | 2020-06-29 | 506 | TFUS | 1258228 | 42956506322 | 2215 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | transfer secondary | -89.9755 | 30.0523 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 77 | 2020 | 1321760883 | Yes | ORLEANS | FAIR | 47 | 2020-01-06 | 3619 | LFUS | 33980 | 3956946513 | 2132 | ENOI | 1 | 77 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons let go by cust. removed balloons and refused lfus. dsmit36 | -89.9849 | 30.033 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 241 | 2020 | 1323644227 | Yes | EAST ORLEANS | WIND | 47 | 2020-02-06 | 11327 | RCLR | 10123 | 4137849331 | 1001 | ENOI | 6 | 241 | UNKN | Inspected Unknown | N | high winds moved through area at time of lockout | -90.026 | 30.0169 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Recloser | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 16 | 2020 | 1330267381 | Yes | ORLEANS | FAIR | 47 | 2020-05-11 | 752 | TFUS | 20937 | 38983494277 | 402 | ENOI | 1 | 16 | ASQL | Animal - Squirrel | N | SQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.1015 | 30.0204 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 7 | 2020 | 1332453070 | Yes | ORLEANS | FAIR | 47 | 2020-06-06 | 329 | TFUS | 72330 | 38956483423 | 904 | ENOI | 1 | 7 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.1028 | 29.9906 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 8 | 2020 | 1333184155 | Yes | EAST ORLEANS | FAIR | 47 | 2020-06-17 | 376 | TFUS | 70051 | 4082247647 | 622 | ENOI | 6 | 8 | UNKN | Inspected Unknown | N | Refused transformer Inspected unknown | -90.044 | 29.9708 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 3 | 2020 | 1321852054 | Yes | EAST ORLEANS | FAIR | 48 | 2020-01-08 | 144 | XFMR | 665472 | 41954472941 | 2346 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N |  | -90.0084 | 29.9607 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 1486 | 2020 | 1332937358 | Yes | ORLEANS | FAIR | 48 | 2020-06-11 | 62412 | SBKR | 2015 | 3847647388 | 2015 | ENOI | 1 | 1486 | HECO | Human Error - Company (Describe in Remarks Field) | N | att contractor set new pole into primary wires, dropped out for safety, woulod not close by scada, field switched RELATED TO AM 1332939453 | -90.1183 | 29.9644 | NP | 210557 | Jan1 to Yesterday | Human Error | Substation Breaker | Human Error | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 11 | 2020 | 1322240774 | Yes | ORLEANS | THDR | 49 | 2020-01-11 | 539 | LFUS | 33059 | 38974475070 | 903 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | roof blew off building taking out a and b phase and taking down 1 span open wire secondary, picked up wire and refused lateral mrusse8 | -90.1025 | 29.9676 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70119 | 1
2020 | 4 | 2020 | 1332541060 | Yes | ORLEANS | THDR | 49 | 2020-06-07 | 196 | SBKR | 1543 | 3950446996 | 1543 | ENOI | 1 | 4 | UNKN | Inspected Unknown | N | storm fault is on overhead behind switch 25810 | -90.086 | 29.9533 | NP | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | B | Council District B | Jay Banks | 70113 | 6
2020 | 44 | 2020 | 1333624070 | Yes | ORLEANS | THDR | 49 | 2020-06-24 | 2156 | LFUS | 17771 | 3855249253 | 411 | ENOI | 1 | 44 | LGHT | Lightning | N | B phase only out for lightning | -90.115 | 30.0157 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 8 | 2020 | 1333998899 | Yes | EAST ORLEANS | FAIR | 49 | 2020-06-29 | 392 | TFUS | 68283 | 4245749238 | 1607 | ENOI | 6 | 8 | SCHD | Scheduled Interruption | N |  | -89.992 | 30.0141 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 10 | 2020 | 1324063576 | Yes | EAST ORLEANS | FAIR | 50 | 2020-02-17 | 500 | TFUS | 61817 | 40999477699 | 611 | ENOI | 6 | 10 | SCHD | Scheduled Interruption | N | contractor are transfering pole they have pot out | -90.0384 | 29.9742 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 102 | 2020 | 1324519542 | Yes | ALGIERS ELEC ONLY | FAIR | 50 | 2020-02-26 | 5100 | RCLR | 5070 | 4119546688 | W1725 | ENOI | 81 | 102 | LGHT | Lightning | N | closed back in per I. Caruthers..........PC | -90.0326 | 29.9444 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Recloser | Lightning | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 1 | 2020 | 1325687193 | Yes | EAST ORLEANS | FAIR | 50 | 2020-03-23 | 50 | SERV | SERVICE | 4286350315 | 2216 | ENOI | 6 | 1 | MALD | Malicious Damage | N | Someone pulled meter broke into business check voltage ok plugged in meter and sealed customer back on, CHg PID to NO, criminal mischief - security dept issue | -89.9788 | 30.0435 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Service Conductor | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 7 | 2020 | 1329965434 | Yes | ORLEANS | FAIR | 50 | 2020-05-06 | 350 | TFUS | 1165240 | 39842492859 | 510 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | crew on site | -90.0745 | 30.016 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 19 | 2020 | 1330267215 | Yes | ORLEANS | FAIR | 50 | 2020-05-11 | 950 | TFUS | 26730 | 39048496285 | 402 | ENOI | 1 | 19 | ASQL | Animal - Squirrel | N | SQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.0994 | 30.0258 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 11 | 2020 | 1332116630 | Yes | ORLEANS | FAIR | 50 | 2020-06-01 | 550 | TFUS | 56189 | 40199476023 | 614 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0639 | 29.9698 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 115 | 2020 | 1323805002 | Yes | ORLEANS | FAIR | 52 | 2020-02-11 | 5980 | LFUS | F05219 | 3960746184 | 2146 | ENOI | 1 | 115 | SCHD | Scheduled Interruption | N | crew onsite transferring pole | -90.083 | 29.9309 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 63 | 2020 | 1326824377 | Yes | ORLEANS | FAIR | 52 | 2020-04-11 | 3276 | LFUS | 97780 | 3989247799 | 615 | ENOI | 1 | 63 | VINE | Vine Growing into Line | N | Back on cleared trees | -90.0734 | 29.9753 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 31 | 2020 | 1330924517 | Yes | ORLEANS | FAIR | 52 | 2020-05-18 | 1612 | LFUS | 28057 | 3935546596 | 1915 | ENOI | 1 | 31 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | BALLONS | -90.091 | 29.9424 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 1833 | 2020 | 1332939453 | Yes | ORLEANS | FAIR | 52 | 2020-06-11 | 100815 | DIS | 23726 | 3856047253 | 2015 | ENOI | 1 | 1833 | HECO | Human Error - Company (Describe in Remarks Field) | N | att contractor set new pole into primary wires, dropped out for safety, woulod not close by scada, field switched DUPLICATE RELATED TO AMFM 1332937358 | -90.1156 | 29.9606 | NP | 210557 | Jan1 to Yesterday | Human Error | Disconnect Switch | Human Error | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 5 | 2020 | 1322933942 | Yes | ALGIERS ELEC ONLY | FAIR | 53 | 2020-01-17 | 265 | TFUS | BY110681 | 4226045412 | W1714 | ENOI | 81 | 5 | SCHD | Scheduled Interruption | N | Nick Carroll will have xfmr out | -89.9995 | 29.9089 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 14 | 2020 | 1323616190 | Yes | ORLEANS | RAIN | 53 | 2020-02-06 | 742 | TFUS | 641930 | 40302484935 | 1708 | ENOI | 1 | 14 | VOHL | Overhanging Limb | N | limb fell across bushing and riser on transformer. per 310 | -90.0602 | 29.9942 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 12 | 2020 | 1324081149 | Yes | EAST ORLEANS | FAIR | 53 | 2020-02-18 | 636 | XFMR | 633552 | 40981476969 | 611 | ENOI | 6 | 12 | SCHD | Scheduled Interruption | N | crew onsite removing old transformer | -90.0389 | 29.9722 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 172 | 2020 | 1325175370 | Yes | ORLEANS | FAIR | 53 | 2020-03-07 | 9460 | OPEN | 3863645932 | 3863645932 | 1917 | ENOI | 1 | 172 | EMER | Emergency Switching | N | opened for safety of crew to epair broke x am for clearance | -90.1137 | 29.9243 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Open | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 577 | 2020 | 1330633097 | Yes | ORLEANS | FAIR | 53 | 2020-05-14 | 30581 | RCLR | 71181 | 4025148173 | 1709 | ENOI | 1 | 577 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | ballons and streamers on lines cleared and closed recloser KC | -90.0618 | 29.9854 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Recloser | Other | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 6 | 2020 | 1330606553 | Yes | ORLEANS | FAIR | 53 | 2020-05-14 | 318 | TFUS | 28059 | 39653492706 | 509 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | refused transformer | -90.0805 | 30.0156 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 2306 | 2020 | 1331552667 | NO | ORLEANS | FAIR | 53 | 2020-05-26 | 122218 | SUBN | 614 | 4081448420 | 614 | ENOI | 1 | 2306 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0441 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | D | Council District D | Jared Brossett | 70126 | 5
2020 | 2101 | 2020 | 1331559065 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 | 111353 | SUBN | 611 | 4081848420 | 611 | ENOI | 6 | 2101 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.044 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | D | Council District D | Jared Brossett | 70126 | 5
2020 | 1761 | 2020 | 1331547286 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 | 93333 | SUBN | 613 | 4081548420 | 613 | ENOI | 6 | 1761 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0441 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | D | Council District D | Jared Brossett | 70126 | 5
2020 | 729 | 2020 | 1331554315 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 | 38637 | SUBN | 617 | 4081048420 | 617 | ENOI | 6 | 729 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0442 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | D | Council District D | Jared Brossett | 70126 | 5
2020 | 150 | 2020 | 1331561189 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 | 7950 | SUBN | 616 | 4081148420 | 616 | ENOI | 6 | 150 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0442 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | D | Council District D | Jared Brossett | 70126 | 5
2020 | 122 | 2020 | 1331553195 | NO | EAST ORLEANS | FAIR | 53 | 2020-05-26 | 6466 | SUBN | 612 | 4081648420 | 612 | ENOI | 6 | 122 | SBBK | Substation Bushing - Breaker | N | insulatopr broke on feeder 615 causing transformer to open | -90.0441 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | D | Council District D | Jared Brossett | 70126 | 5
2020 | 12 | 2020 | 1322234430 | Yes | ORLEANS | THDR | 54 | 2020-01-11 | 648 | TFUS | 518794 | 38168466520 | 2014 | ENOI | 1 | 12 | LGHT | Lightning | N | out by weather. refused ok dsmit36 | -90.1283 | 29.9443 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 213 | 2020 | 1328278670 | Yes | EAST ORLEANS | THDR | 54 | 2020-04-18 | 11502 | SBKR | 2347 | 4216047802 | 2347 | ENOI | 6 | 213 | LGHT | Lightning | N | Loop Scheme worked properly restoring all load down of reclosers | -90.0018 | 29.9747 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Substation Breaker | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 19 | 2020 | 1333097236 | Yes | EAST ORLEANS | FAIR | 54 | 2020-06-15 | 1026 | LFUS | 21262 | 4224350265 | 2212 | ENOI | 6 | 19 | VHCL | Vehicle | N | car hit pole it took lateral out on gus refused and customers are back in lights | -89.9982 | 30.0424 | NP | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 3 | 2020 | 1323085293 | Yes | EAST ORLEANS | FAIR | 55 | 2020-01-21 | 165 | LFUS | F05622 | 4830351192 | 1204 | ENOI | 6 | 3 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.8064 | 30.0658 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 23 | 2020 | 1323924228 | Yes | EAST ORLEANS | FAIR | 55 | 2020-02-13 | 1265 | LFUS | 21736 | 4186649358 | 1612 | ENOI | 6 | 23 | SCHD | Scheduled Interruption | N | crew got lateral back in | -90.0105 | 30.0175 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 5 | 2020 | 1325459780 | Yes | ORLEANS | FAIR | 55 | 2020-03-17 | 275 | TFUS | 64925 | 40233479668 | 627 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | crew replacing cross arm | -90.0625 | 29.9798 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70119 | 3
2020 | 38 | 2020 | 1329000156 | Yes | EAST ORLEANS | FAIR | 55 | 2020-04-25 | 2090 | LFUS | 36879F | 4372350002 | 1609 | ENOI | 6 | 38 | HEID | Improper Design (Describe in Remarks Field) | N | Equipment labeled incorrectly from manufacture | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Human Error | Line Fuse | Human Error | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 5 | 2020 | 1329240394 | Yes | EAST ORLEANS | THDR | 55 | 2020-04-28 | 275 | TFUS | 68163 | 42021478356 | 2325 | ENOI | 6 | 5 | VINE | Vine Growing into Line | N | refused trans..cleared vines | -90.0061 | 29.9756 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 162 | 2020 | 1330486955 | Yes | EAST ORLEANS | FAIR | 55 | 2020-05-13 | 8910 | LFUS | 27845 | 4085148824 | 617 | ENOI | 6 | 162 | EARM | Equipment Failure - Crossarm | N |  | -90.0426 | 30.0032 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 16 | 2020 | 1332529957 | Yes | ORLEANS | FAIR | 55 | 2020-06-07 | 880 | TFUS | 1513065 | 39127478230 | 911 | ENOI | 1 | 16 | UNKN | Inspected Unknown | N |  | -90.0976 | 29.9762 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 735 | 2020 | 1323525567 | Yes | ORLEANS | FAIR | 56 | 2020-02-05 | 47040 | DIS | 23899 | 3851646958 | 2016 | ENOI | 1 | 735 | VHCL | Vehicle | N | car broke pole; shield wire down PID IN PROGRESS- WAITING ON CONTRACTORS | -90.1171 | 29.9525 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 8 | 2020 | 1324616546 | Yes | ORLEANS | FAIR | 56 | 2020-02-27 | 448 | TFUS | 60601 | 39064458650 | 1923 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | scheduled outage | -90.1004 | 29.9224 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 1 | 2020 | 1333250548 | Yes | ORLEANS | FAIR | 56 | 2020-06-19 | 56 | SERV | SERVICE | 39308462481 | 1554 | ENOI | 1 | 1 | HECO | Human Error - Company (Describe in Remarks Field) | N | AMOC turned off wrong meter | -90.0923 | 29.933 | NP | 210557 | Jan1 to Yesterday | Human Error | Service Conductor | Human Error | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 186 | 2020 | 1331025850 | Yes | ORLEANS | FAIR | 57 | 2020-05-20 | 10602 | SBKR | 907 | 3897447411 | 907 | ENOI | 1 | 186 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | opened 23596 and closed bkr in: Suspect balloons on N. Rochablave, Orleans to St. Peter | -90.1026 | 29.9649 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 824 | 2020 | 1333730057 | Yes | ORLEANS | FAIR | 57 | 2020-06-25 | 46968 | RCLR | 46606 | 3985746421 | 2137 | ENOI | 1 | 824 | VHCL | Vehicle | N | car hit guy wire and caused shield wire to come down SUBMITTED IN MINIMAL CLAIMS | -90.0748 | 29.9374 | NP | 210557 | Jan1 to Yesterday | Public Damage | Recloser | Public Damage | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 48 | 2020 | 1321847622 | Yes | EAST ORLEANS | FAIR | 58 | 2020-01-08 | 2784 | LFUS | 37416 | 40593476553 | 622 | ENOI | 6 | 48 | SCHD | Scheduled Interruption | N | crew on site | -90.0513 | 29.9711 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 9 | 2020 | 1326703115 | Yes | ORLEANS | THDR | 58 | 2020-04-10 | 522 | TFUS | 67458 | 38417468094 | 2016 | ENOI | 1 | 9 | LGHT | Lightning | N | taken out by weather refused ok | -90.1203 | 29.9485 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 9 | 2020 | 1326721350 | Yes | EAST ORLEANS | THDR | 58 | 2020-04-10 | 522 | XFMR | 54886 | 42273502070 | 2211 | ENOI | 6 | 9 | ETRD | Equipment Failure - Transformer | N | Bad 50 KVA, leads and switch | -89.9974 | 30.0409 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 3 | 2020 | 1332323007 | Yes | EAST ORLEANS | FAIR | 58 | 2020-06-05 | 174 | TFUS | 58769 | 41143476587 | 611 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | contract crew on site | -90.0337 | 29.9711 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 40 | 2020 | 1332478850 | Yes | EAST ORLEANS | FAIR | 58 | 2020-06-06 | 2320 | LFUS | 17870 | 4036349293 | 506 | ENOI | 6 | 40 | ECNS | Equipment Failure - Connector Sleeve | N | bottom side jumper of switch burned out of switch on c phase | -90.0582 | 30.0161 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 6 | 2020 | 1333168986 | Yes | EAST ORLEANS | FAIR | 58 | 2020-06-17 | 348 | LFUS | 89813 | 4164747805 | 2325 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0182 | 29.9749 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 25 | 2020 | 1325826194 | Yes | EAST ORLEANS | FAIR | 59 | 2020-03-25 | 1475 | LFUS | 58763 | 4259449242 | 1607 | ENOI | 6 | 25 | EARR | Equipment Failure - Arrestor | N | refused lat..blown arestor | -89.9874 | 30.0142 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 214 | 2020 | 1326339586 | Yes | EAST ORLEANS | FAIR | 59 | 2020-04-04 | 12626 | LFUS | 27890 | 4104247687 | 611 | ENOI | 6 | 214 | EARM | Equipment Failure - Crossarm | N |  | -90.0372 | 29.972 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 9 | 2020 | 1328552224 | Yes | ORLEANS | FAIR | 59 | 2020-04-21 | 531 | TFUS | 63578 | 39213462104 | 1924 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption; crew changing out wilson rack | -90.0953 | 29.9318 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 15 | 2020 | 1328992897 | Yes | ORLEANS | FAIR | 59 | 2020-04-25 | 885 | LFUS | 61341 | 3817446224 | 2013 | ENOI | 1 | 15 | VOHL | Overhanging Limb | N | REFUSED OKAY | -90.1283 | 29.9326 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 5 | 2020 | 1329231073 | Yes | ORLEANS | THDR | 59 | 2020-04-28 | 295 | TFUS | 1003896 | 38911489462 | 413 | ENOI | 1 | 5 | VLGL | Tree/Limb Growing Inside R.O.W. | N | cleared palm tree from transformer. refused ok. per 310 | -90.1039 | 30.0071 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 16 | 2020 | 1329520003 | Yes | ORLEANS | THDR | 59 | 2020-04-29 | 944 | TFUS | 62626 | 3989947531 | 1512 | ENOI | 1 | 16 | LGHT | Lightning | N | weather |  |  | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 546 | 2020 | 1330171041 | Yes | EAST ORLEANS | THDR | 59 | 2020-05-08 | 32214 | RCLR | 24641 | 4090648904 | 617 | ENOI | 6 | 546 | EARM | Equipment Failure - Crossarm | N | broken x arm braces | -90.0409 | 30.0054 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 10 | 2020 | 1331194913 | Yes | ORLEANS | FAIR | 59 | 2020-05-22 | 590 | TFUS | 3004338 | 38349471193 | 2016 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1223 | 29.9571 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 27 | 2020 | 1325908514 | Yes | ORLEANS | FAIR | 60 | 2020-03-27 | 1620 | TFUS | 76114 | 39176475866 | 911 | ENOI | 1 | 27 | ECNS | Equipment Failure - Connector Sleeve | N |  | -90.0962 | 29.9697 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 9 | 2020 | 1327514921 | Yes | ORLEANS | FAIR | 60 | 2020-04-13 | 540 | LFUS | 13221 | 3831747940 | 400 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1231 | 29.9796 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 50 | 2020 | 1328256797 | Yes | ORLEANS | THDR | 60 | 2020-04-18 | 3000 | LFUS | 33992 | 3981445947 | 2147 | ENOI | 1 | 50 | ECON | Equipment Failure - Connector / Sleeve | N | repaired broken jumper at switch pole | -90.0767 | 29.9244 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 534 | 2020 | 1330432634 | Yes | EAST ORLEANS | FAIR | 60 | 2020-05-12 | 32040 | VFI | 26140 | 4264649768 | 1610 | ENOI | 6 | 534 | AOTH | Animal - Other (Describe in Remarks Field) | N | rat contacted switch in cub. # 8 sw. # 76880 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Vacuum Fault Interrupter | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 1 | 2020 | 1331003965 | Yes | ORLEANS | FAIR | 60 | 2020-05-20 | 60 | TFUS | 1031021 | 4004048095 | 1712 | ENOI | 1 | 1 | AOTH | Animal - Other (Describe in Remarks Field) | N | transformer taken out by a bird refused ok per RBILES | -90.0687 | 29.9832 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 6 | 2020 | 1331051743 | Yes | EAST ORLEANS | FAIR | 60 | 2020-05-21 | 360 | TFUS | 65670 | 42759494914 | 1604 | ENOI | 6 | 6 | ASQL | Animal - Squirrel | N | Transformer fuse blown at loc refused ok | -89.9824 | 30.021 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 12 | 2020 | 1332522734 | Yes | ORLEANS | WIND | 60 | 2020-06-07 | 720 | TFUS | 33037 | 38934491554 | 413 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption had to take slack out of open wire secondary | -90.1033 | 30.0128 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 60 | 2020 | 1324759313 | Yes | ORLEANS | FAIR | 61 | 2020-03-02 | 3660 | LFUS | 37635 | 3979848210 | 1705 | ENOI | 1 | 60 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0763 | 29.9865 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 95 | 2020 | 1327000269 | Yes | EAST ORLEANS | WIND | 61 | 2020-04-12 | 5795 | LFUS | 27876 | 4359749690 | 1601 | ENOI | 6 | 95 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused lat 27876 B &amp;amp; C phase..wind | -89.9558 | 30.0259 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 5 | 2020 | 1330350483 | Yes | ORLEANS | FAIR | 61 | 2020-05-11 | 305 | TFUS | 67437 | 38720465716 | 2016 | ENOI | 1 | 5 | EFLK | Equipment Failure - Fuse Link | N | refused transformer | -90.1108 | 29.942 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 1125 | 2020 | 1331616285 | Yes | ORLEANS | FAIR | 61 | 2020-05-26 | 68625 | RCLR | 25190 | 4015448032 | 627 | ENOI | 1 | 1125 | EARR | Equipment Failure - Arrestor | N | Failed arrestor on C phase at Maniville & Abundance | -90.0649 | 29.9816 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 12 | 2020 | 1333445809 | Yes | ORLEANS | THDR | 61 | 2020-06-22 | 732 | TFUS | 58355 | 39713473480 | 1512 | ENOI | 1 | 12 | EARR | Equipment Failure - Arrestor | N | arrestor gave way cleared refused okay per ryan price | -90.0793 | 29.9629 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70112 | 6
2020 | 61 | 2020 | 1322256616 | Yes | ORLEANS | THDR | 63 | 2020-01-11 | 3843 | LFUS | 28031 | 3833945903 | 1914 | ENOI | 1 | 61 | LGHT | Lightning | N | lightning tagged an insulator 1 span from the lateral. Crew changed ins. and refused lateral rbiles | -90.1231 | 29.9237 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 4 | 2020 | 1325755199 | Yes | ORLEANS | FAIR | 63 | 2020-03-24 | 252 | TFUS | 66080 | 38427472556 | 2016 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1198 | 29.9608 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 3
2020 | 8 | 2020 | 1327276626 | Yes | ORLEANS | THDR | 63 | 2020-04-12 | 504 | TFUS | 67835 | 38533476792 | 2026 | ENOI | 1 | 8 | ECNS | Equipment Failure - Connector Sleeve | N | rier on switch | -90.1163 | 29.9725 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 121 | 2020 | 1324763424 | Yes | ORLEANS | FAIR | 64 | 2020-03-02 | 7744 | LFUS | 17521 | 3845449177 | 411 | ENOI | 1 | 121 | SCHD | Scheduled Interruption | N | back on | -90.1183 | 30.0136 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 5 | 2020 | 1332204038 | Yes | EAST ORLEANS | FAIR | 64 | 2020-06-03 | 320 | TFUS | 1190793 | 41070491992 | 501 | ENOI | 6 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0358 | 30.0133 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 2 | 2020 | 1327261864 | Yes | ORLEANS | THDR | 65 | 2020-04-12 | 130 | TFUS | 28160 | 38467482925 | 407 | ENOI | 1 | 2 | SLAK | Slack Conductor / Loose Connection | N | Phase out from high winds. Refused ok | -90.1181 | 29.9893 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 706 | 2020 | 1331064901 | Yes | EAST ORLEANS | FAIR | 65 | 2020-05-21 | 45890 | RCLR | 37681 | 4061148946 | 1702 | ENOI | 6 | 706 | EPRI | Equipment Failure - Primary Conductor | N | primary burned down possibly from overhanging limb | -90.0505 | 30.0066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 4 | 2020 | 1332807230 | Yes | EAST ORLEANS | FAIR | 65 | 2020-06-09 | 260 | TFUS | 69609 | 42039475082 | 2345 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N |  | -90.0055 | 29.9666 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 15 | 2020 | 1333728302 | Yes | ORLEANS | FAIR | 65 | 2020-06-25 | 975 | TFUS | 1027451 | 39043466975 | 1925 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1006 | 29.9452 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 5 | 2020 | 1333956683 | Yes | ORLEANS | FAIR | 65 | 2020-06-28 | 325 | TFUS | 58290 | 39656485112 | 1703 | ENOI | 1 | 5 | ASQL | Animal - Squirrel | N | refused pot | -90.0805 | 29.9949 | NP | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 4 | 2020 | 1322854567 | Yes | EAST ORLEANS | FAIR | 66 | 2020-01-16 | 264 | TFUS | 1605537 | 42777504021 | 2215 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | crew onsite | -89.9813 | 30.046 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 83 | 2020 | 1323219985 | Yes | ORLEANS | FAIR | 66 | 2020-01-26 | 5478 | LFUS | 27976 | 4035147852 | 1709 | ENOI | 1 | 83 | EPRI | Equipment Failure - Primary Conductor | N |  | -90.0588 | 29.9766 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70116 | 1
2020 | 25 | 2020 | 1324838882 | Yes | EAST ORLEANS | FAIR | 66 | 2020-03-03 | 1650 | LFUS | 31765 | 4178547304 | 2346 | ENOI | 6 | 25 | EARM | Equipment Failure - Crossarm | N | crew to change | -90.0138 | 29.9611 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 31 | 2020 | 1329727435 | Yes | ORLEANS | FAIR | 66 | 2020-05-01 | 2046 | SBKR | 1543 | 3950446996 | 1543 | ENOI | 1 | 31 | RBRD | Animal - Bird Reportable Inc (Mortality or Injury) | N | bird contacted B & C phase on T.P. # D01648; Repairs made & fdr restored | -90.086 | 29.9533 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Substation Breaker | Animal | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 5 | 2020 | 1330686117 | Yes | EAST ORLEANS | FAIR | 66 | 2020-05-15 | 330 | TFUS | 58802 | 48464512640 | 1204 | ENOI | 6 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.8012 | 30.0678 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 5
2020 | 13 | 2020 | 1323133322 | Yes | ORLEANS | FAIR | 67 | 2020-01-23 | 871 | TFUS | 72349 | 38762481819 | 903 | ENOI | 1 | 13 | VHCL | Vehicle | N | truck pulled down service line and tore meters and stem pipe off of house. related to ticket 1323096279 yesterday already sent to minimalclaimskc | -90.1091 | 29.9862 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 12 | 2020 | 1331295825 | Yes | ORLEANS | FAIR | 67 | 2020-05-24 | 804 | TFUS | 694320 | 39218473125 | 2025 | ENOI | 1 | 12 | VLFL | Tree On Line Outside R.O.W | N | limb on top of transformer | -90.0948 | 29.9622 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 135 | 2020 | 1332538496 | Yes | EAST ORLEANS | THDR | 67 | 2020-06-07 | 9045 | LFUS | 21145 | 4065847641 | 622 | ENOI | 6 | 135 | VLFL | Tree On Line Outside R.O.W | N | palm tree needs to be trimmed STORM - WO VSTO 2064873454; M WO 4315859; | -90.0492 | 29.9709 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 44 | 2020 | 1323525769 | Yes | ORLEANS | FAIR | 68 | 2020-02-05 | 3212 | DIS | 23892 | 3854246996 | 2016 | ENOI | 1 | 44 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1163 | 29.9536 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 2
2020 | 24 | 2020 | 1331506621 | Yes | ORLEANS | FAIR | 68 | 2020-05-26 | 1632 | LFUS | 37925 | 3855847562 | 2012 | ENOI | 1 | 24 | LGHT | Lightning | N | bad weather in area | -90.1156 | 29.9693 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 135 | 2020 | 1332522022 | Yes | EAST ORLEANS | THDR | 68 | 2020-06-07 | 9180 | LFUS | 21145 | 4065847641 | 622 | ENOI | 6 | 135 | VLFL | Tree On Line Outside R.O.W | N | Refused B and C phase at lateral sw.. Dead palm limbs fell into lateral | -90.0492 | 29.9709 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 7 | 2020 | 1332739620 | Yes | ORLEANS | THDR | 68 | 2020-06-08 | 476 | TFUS | 62239 | 39435458191 | 2147 | ENOI | 1 | 7 | LGHT | Lightning | N | taken out by lightning in thunderstorm this evening refused ok | -90.0885 | 29.9209 | NP | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 33 | 2020 | 1322288849 | Yes | EAST ORLEANS | FAIR | 69 | 2020-01-11 | 2277 | LFUS | 34976 | 4152747182 | 2346 | ENOI | 6 | 33 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | ballon got into secondary took out stinger pot which blew lateral fuse refuse lateral and transformer and lights are back on and good voltage dwillin | -90.022 | 29.9578 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 39 | 2020 | 1329102057 | Yes | ORLEANS | FAIR | 69 | 2020-04-27 | 2691 | LFUS | 33500 | 38848458600 | 1921 | ENOI | 1 | 39 | EFLK | Equipment Failure - Fuse Link | N | Refused transformer and lfus | -90.1071 | 29.9224 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 11 | 2020 | 1334006985 | Yes | ORLEANS | FAIR | 69 | 2020-06-29 | 759 | TFUS | 60257 | 39337457415 | 1922 | ENOI | 1 | 11 | EPOL | Equipment Failure - Pole | N |  | -90.0917 | 29.919 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 851 | 2020 | 1321740753 | Yes | EAST ORLEANS | FAIR | 70 | 2020-01-05 | 59570 | SBKR | 1602 | 4351549756 | 1602 | ENOI | 6 | 851 | ESWC | Switching Cabinet | N | opened in vfi 531 opened switch 38268 serviceman to ride remainng customer sout Cub, # 554 flashover Okay Temp | -89.9583 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 4 | 2020 | 1323577065 | Yes | EAST ORLEANS | THDR | 70 | 2020-02-05 | 280 | TFUS | 73153 | 41749477220 | 2325 | ENOI | 6 | 4 | LGHT | Lightning | N | refused B and C phase taken out by bad weather | -90.0149 | 29.9726 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 5 | 2020 | 1325457267 | Yes | ORLEANS | FAIR | 70 | 2020-03-17 | 350 | TFUS | 595357 | 3977848904 | 1704 | ENOI | 1 | 5 | EFSW | Equipment Failure - Fuse Switch | N | Just a transformer | -90.0768 | 30.0058 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 13 | 2020 | 1332580320 | Yes | ORLEANS | RAIN | 70 | 2020-06-07 | 910 | TFUS | 1417056 | 38757470419 | 2015 | ENOI | 1 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1096 | 29.9548 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 3 | 2020 | 1333646810 | Yes | ORLEANS | THDR | 70 | 2020-06-24 | 210 | TFUS | 613294 | 4038047469 | 614 | ENOI | 1 | 3 | VLFL | Tree On Line Outside R.O.W | N | limbs pulled service out of connections | -90.058 | 29.9662 | NP | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 2 | 2020 | 1322340541 | Yes | EAST ORLEANS | THDR | 71 | 2020-01-11 | 142 | PRIM | 4341249109 | 4341249109 | 1612 | ENOI | 6 | 2 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | MOULDING | -89.9618 | 30.0102 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Primary Meter | Other | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 1 | 2020 | 1323164693 | Yes | ORLEANS | FAIR | 71 | 2020-01-24 | 71 | SERV | SERVICE COND | 38374484905 | 407 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | bad connection at weather head changed out ok #305 | -90.1212 | 29.9948 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 27 | 2020 | 1325104705 | Yes | ORLEANS | FAIR | 71 | 2020-03-05 | 1917 | LFUS | 37993 | 3945647879 | 912 | ENOI | 1 | 27 | SCHD | Scheduled Interruption | N | RELI WORK COMPLETE | -90.0873 | 29.9776 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 229 | 2020 | 1331460994 | Yes | ORLEANS | FAIR | 71 | 2020-05-26 | 16259 | LFUS | 38007 | 3980547500 | 907 | ENOI | 1 | 229 | UNKI | Unknown - Under Investigation | N | refused 2 phases out, customer back on | -90.0763 | 29.9673 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 134 | 2020 | 1334033546 | Yes | ORLEANS | FAIR | 71 | 2020-06-29 | 9514 | LFUS | 27650 | 3977248967 | 1704 | ENOI | 1 | 134 | HCDC | Entergy Distribution Contractor (Describe in rema | N | entergy tree crew dropped branch on wires | -90.0769 | 30.0073 | NP | 210557 | Jan1 to Yesterday | Human Error | Line Fuse | Human Error | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 7 | 2020 | 1324294885 | Yes | EAST ORLEANS | WIND | 72 | 2020-02-20 | 504 | TFUS | 57875 | 40375486483 | 1708 | ENOI | 6 | 7 | EFSW | Equipment Failure - Fuse Switch | N | c phase fuse burnt in half..refused | -90.058 | 29.9985 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 25 | 2020 | 1332556627 | Yes | EAST ORLEANS | THDR | 72 | 2020-06-07 | 1800 | DIS | 25271 | 4255449627 | 1610 | ENOI | 6 | 25 | FTNU | Foreign Trouble - Neighboring Utility | N | WIRE LOW TOUCHING STREET LIGHT STANDARD: Open for safety to make repairs | -89.9888 | 30.0247 | NP | 210557 | Jan1 to Yesterday | Foreign Trouble | Disconnect Switch | Foreign Trouble | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 10 | 2020 | 1333166355 | Yes | ORLEANS | FAIR | 72 | 2020-06-17 | 720 | TFUS | 56513 | 39737489643 | 1704 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.078 | 30.0072 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 1166 | 2020 | 1323550211 | Yes | EAST ORLEANS | THDR | 73 | 2020-02-05 | 85118 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 1166 | EPRI | Equipment Failure - Primary Conductor | N | crew onsiyte picking up lateral | -90.0021 | 29.9747 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 10 | 2020 | 1323664900 | Yes | ORLEANS | FAIR | 73 | 2020-02-07 | 730 | TFUS | 1585375 | 39461462505 | 1924 | ENOI | 1 | 10 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | no comments | -90.0875 | 29.9329 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 250 | 2020 | 1325740722 | Yes | ORLEANS | FAIR | 73 | 2020-03-24 | 18250 | LFUS | 27910 | 4001447600 | 1712 | ENOI | 1 | 250 | EARM | Equipment Failure - Crossarm | N | end of arm broke and insulator came out of arm. reinstalled insulator | -90.0697 | 29.9698 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70116 | 3
2020 | 11 | 2020 | 1326996836 | Yes | ORLEANS | WIND | 73 | 2020-04-12 | 803 | TFUS | 1466818 | 39921488745 | 1704 | ENOI | 1 | 11 | VLFL | Tree On Line Outside R.O.W | N | Trees took out switch in transformer | -90.0721 | 30.0048 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 2113 | 2020 | 1330665977 | Yes | ORLEANS | THDR | 73 | 2020-05-15 | 154249 | SBKR | 1513 | 3951246991 | 1513 | ENOI | 1 | 2113 | LGHT | Lightning | N | wather, crew rode out, back on now | -90.0857 | 29.9532 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Substation Breaker | Lightning | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 16 | 2020 | 1333729167 | Yes | ORLEANS | FAIR | 73 | 2020-06-25 | 1168 | TFUS | 1464763 | 39976463231 | 2142 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0711 | 29.9347 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 11 | 2020 | 1321820424 | Yes | ORLEANS | FAIR | 74 | 2020-01-07 | 814 | TFUS | 55653 | 38968480755 | 904 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1024 | 29.9832 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 7 | 2020 | 1323000141 | Yes | ALGIERS ELEC ONLY | FAIR | 74 | 2020-01-19 | 518 | TFUS | 1417734 | 4264345881 | W1713 | ENOI | 81 | 7 | VOHL | Overhanging Limb | N | ROBERT COURET W-00 | -89.9873 | 29.9217 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 10 | 2020 | 1325141994 | Yes | ORLEANS | FAIR | 74 | 2020-03-06 | 740 | TFUS | 1060584 | 39925462472 | 2137 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.073 | 29.9326 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 716 | 2020 | 1323082860 | Yes | EAST ORLEANS | FAIR | 75 | 2020-01-21 | 53700 | SBKR | 1204 | 4544050173 | 1204 | ENOI | 6 | 716 | EPRI | Equipment Failure - Primary Conductor | N | poen midpoint breaker in | -89.8973 | 30.0387 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 265 | 2020 | 1329318727 | Yes | EAST ORLEANS | THDR | 75 | 2020-04-29 | 19875 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 265 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.8029 | 30.0695 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Recloser | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 22 | 2020 | 1325406620 | Yes | ALGIERS ELEC ONLY | FAIR | 76 | 2020-03-15 | 1672 | SBKR | W1725 | 4284345924 | W1725 | ENOI | 81 | 22 | VHCL | Vehicle | N | vehicle broke pole, Chgd PID to No, related to #1325409607 (DGault) | -89.981 | 29.9228 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Substation Breaker | Public Damage | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 121 | 2020 | 1330683233 | Yes | ORLEANS | THDR | 76 | 2020-05-15 | 9196 | LFUS | 27678 | 3904546057 | 1924 | ENOI | 1 | 121 | LGHT | Lightning | N | Lightning | -90.1009 | 29.9277 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 56 | 2020 | 1323138236 | Yes | ORLEANS | FAIR | 77 | 2020-01-23 | 4312 | LFUS | 27806 | 3884646637 | 1916 | ENOI | 1 | 56 | EARM | Equipment Failure - Crossarm | N | cross arm broke street side phase was cut down temp ok gor now #305 | -90.1068 | 29.9437 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 4 | 2020 | 1325037811 | Yes | EAST ORLEANS | RAIN | 77 | 2020-03-04 | 308 | LFUS | 36617 | 41796477686 | 2325 | ENOI | 6 | 4 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused single phase lat..wether | -90.0133 | 29.9738 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 69 | 2020 | 1333585739 | Yes | ORLEANS | THDR | 77 | 2020-06-23 | 5313 | LFUS | 21465 | 3928745922 | 1923 | ENOI | 1 | 69 | LGHT | Lightning | N | refused | -90.0933 | 29.9237 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 1 | 2020 | 1321900766 | Yes | EAST ORLEANS | FAIR | 78 | 2020-01-10 | 78 | SERV | SERVICE | 42073500359 | 2212 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N | ami meter burned up customer lug pulled meter meter #am10993i155 installed new meter 8154918 sn 92095254 cbowden | -90.0037 | 30.0361 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 5 | 2020 | 1322510653 | Yes | ORLEANS | FAIR | 78 | 2020-01-12 | 390 | TFUS | 1183487 | 39789466302 | 2137 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0772 | 29.9432 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 26 | 2020 | 1322629818 | Yes | ORLEANS | FAIR | 78 | 2020-01-13 | 2028 | DIS | 23138 | 3852247482 | 2012 | ENOI | 1 | 26 | SCHD | Scheduled Interruption | N | Line de-energized to safely replace xarms | -90.1168 | 29.9669 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 2 | 2020 | 1322605291 | Yes | EAST ORLEANS | FOGG | 78 | 2020-01-13 | 156 | TFUS | 1106471 | 41320493904 | 1009 | ENOI | 6 | 2 | EFLK | Equipment Failure - Fuse Link | N | refused b phase check customer ok cschexn | -90.0277 | 30.0186 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 19 | 2020 | 1323227281 | Yes | ALGIERS ELEC ONLY | FAIR | 78 | 2020-01-26 | 1482 | LFUS | 5699 | 4261545915 | W1713 | ENOI | 81 | 19 | UNKN | Inspected Unknown | N | blown lat fuse refused and held also transformer 3004469 was blown not sure if this is what caused the lat fuse to blow. both lat fuse and transformer had proper size fuses in them also | -89.9882 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 279 | 2020 | 1323663056 | Yes | EAST ORLEANS | THDR | 78 | 2020-02-07 | 21762 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 279 | EARR | Equipment Failure - Arrestor | N | blown arrestor | -90.0337 | 29.9718 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 28 | 2020 | 1324398683 | Yes | ORLEANS | FAIR | 78 | 2020-02-23 | 2184 | LFUS | 21435 | 3883945809 | 1921 | ENOI | 1 | 28 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | removed balloons off of line; a phase blown KC | -90.1073 | 29.9209 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 11 | 2020 | 1324416799 | Yes | EAST ORLEANS | FAIR | 78 | 2020-02-24 | 858 | TFUS | 71154 | 40600474196 | 623 | ENOI | 6 | 11 | ASQL | Animal - Squirrel | N | animal took out transformer re fused transformer and lights back on squirrel got into secondary | -90.0511 | 29.9648 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 62 | 2020 | 1333647584 | Yes | ORLEANS | THDR | 78 | 2020-06-24 | 4836 | LFUS | 60740 | 38393496276 | 409 | ENOI | 1 | 62 | LGHT | Lightning | N | taken out by lightning refused ok | -90.1202 | 30.026 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 5 | 2020 | 1322147313 | Yes | ORLEANS | WIND | 79 | 2020-01-11 | 395 | TFUS | 1385289 | 39706489324 | 1704 | ENOI | 1 | 5 | VOHL | Overhanging Limb | N | found tree branch on top of transformer resfued ok jcox7 | -90.079 | 30.0065 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 1 | 2020 | 1323764163 | Yes | EAST ORLEANS | WIND | 79 | 2020-02-10 | 79 | LFUS | 27269 | 41375485531 | 616 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | B and C Phase fuse were blown at the lateral switch. Inspected line and determined that #6 copper phases blew together with wind. Made cust contact. Back in lights. | -90.0263 | 29.9955 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 30 | 2020 | 1333998174 | Yes | EAST ORLEANS | FAIR | 79 | 2020-06-29 | 2370 | LFUS | 21743 | 4244349367 | 1604 | ENOI | 6 | 30 | SCHD | Scheduled Interruption | N |  | -89.9924 | 30.0175 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 297 | 2020 | 1334122667 | Yes | ORLEANS | FAIR | 79 | 2020-06-30 | 23463 | LFUS | 14694 | 38682495639 | 401 | ENOI | 1 | 297 | EPRI | Equipment Failure - Primary Conductor | N | UG primary splice blew up in manhole switched UG loop around to get everyone back in lights | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70124 | 6
2020 | 1 | 2020 | 1334136582 | Yes | ORLEANS | FAIR | 79 | 2020-06-30 | 79 | SERV | METER | 39379462185 | 1924 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter burnt up capacitor for AC | -90.0903 | 29.9321 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 2 | 2020 | 1321608611 | Yes | ORLEANS CBD | FAIR | 80 | 2020-01-01 | 160 | SBKR | 1822 | 4015446698 | 1822 | ENOI | 4 | 2 | EPRI | Equipment Failure - Primary Conductor | N | failure in manhole 6-1460; bad splice on b phase: The 2 cust. were restored manuelly at 6;35 AM Fder was restored 1/2/20 4:08 AM: The 3rd cust was a mis-match | -90.0656 | 29.9449 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 1 | 2020 | 1321637104 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-02 | 80 | TFUS | 1223486 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | vines grew into terminal pole toook out a phase cleared vines refused barrrel and got lights cback on and tested voltage lights cam eback on dwillin | -90.0377 | 30.0062 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 1 | 2020 | 1321713956 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-03 | 80 | SERV | SERVICE | 42029493934 | 1607 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed **TFUS 1315127 8 to SERV 1315127 8** --- sec conect..repaired tbrock | -90.0053 | 30.0185 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 9 | 2020 | 1323314478 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-29 | 720 | TFUS | 64100 | 43284495685 | 1611 | ENOI | 6 | 9 | SCHD | Scheduled Interruption | N |  | -89.9656 | 30.0229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 1 | 2020 | 1323491980 | Yes | ORLEANS | FAIR | 80 | 2020-02-04 | 80 | SERV | METER | 38614466197 | 1554 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | ami meter open internally | -90.1143 | 29.9433 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 64 | 2020 | 1323649733 | Yes | ORLEANS | WIND | 80 | 2020-02-06 | 5120 | LFUS | 28068 | 3960648669 | 1703 | ENOI | 1 | 64 | EPRI | Equipment Failure - Primary Conductor | N | high wind refused okay | -90.0821 | 29.9993 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 134 | 2020 | 1325707249 | Yes | ORLEANS | FAIR | 80 | 2020-03-23 | 10720 | LFUS | 27650 | 3977248967 | 1704 | ENOI | 1 | 134 | VLFL | Tree On Line Outside R.O.W | N | crew onsite making repairs | -90.0769 | 30.0073 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 8 | 2020 | 1326723023 | Yes | ORLEANS | THDR | 80 | 2020-04-10 | 640 | TFUS | 66889 | 38498468689 | 2016 | ENOI | 1 | 8 | VINE | Vine Growing into Line | N | Vines on transformer jumper refused ok | -90.1178 | 29.9501 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 9 | 2020 | 1328065709 | Yes | ORLEANS | FAIR | 80 | 2020-04-16 | 720 | LFUS | 69744 | 38350461226 | 1917 | ENOI | 1 | 9 | VOHL | Overhanging Limb | N | tree limbs got lateral together; made veg ticket; refused | -90.1227 | 29.9297 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 5 | 2020 | 1328327624 | Yes | ORLEANS | THDR | 80 | 2020-04-19 | 400 | LFUS | 61731 | 38375461112 | 1917 | ENOI | 1 | 5 | EONE | Equipment Failure - Neutral / Shield Conductor | N | found shield sleeve was pull out by tree. repaired laterial refused customer back in light. HW | -90.1219 | 29.9294 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 16 | 2020 | 1331796991 | Yes | ORLEANS | FAIR | 80 | 2020-05-27 | 1280 | TFUS | 497054 | 38780464215 | 1926 | ENOI | 1 | 16 | EARM | Equipment Failure - Crossarm | N | crew changing x arm secondary | -90.1092 | 29.9376 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 13 | 2020 | 1321665957 | Yes | EAST ORLEANS | RAIN | 81 | 2020-01-02 | 1053 | TFUS | 1205818 | 40891475703 | 622 | ENOI | 6 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.042 | 29.9687 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 29 | 2020 | 1331790819 | Yes | ORLEANS | FAIR | 81 | 2020-05-26 | 2349 | XFMR | 79237 | 38870462985 | 1554 | ENOI | 1 | 29 | ETRD | Equipment Failure - Transformer | N |  | -90.1063 | 29.9344 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 6 | 2020 | 1332220636 | Yes | ORLEANS | FAIR | 81 | 2020-06-03 | 486 | TFUS | 59762 | 39967488805 | 1704 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0706 | 30.005 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 2 | 2020 | 1327261824 | Yes | EAST ORLEANS | THDR | 82 | 2020-04-12 | 164 | TFUS | 78289 | 42002472445 | 2345 | ENOI | 6 | 2 | LGHT | Lightning | N | WIND | -90.0071 | 29.9593 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 52 | 2020 | 1332965516 | Yes | EAST ORLEANS | FAIR | 82 | 2020-06-11 | 4264 | LFUS | 21124 | 4118747946 | 621 | ENOI | 6 | 52 | ETRD | Equipment Failure - Transformer | N | bad transformer took lateral out 64977 | -90.0325 | 29.9789 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 1 | 2020 | 1333560528 | Yes | EAST ORLEANS | FAIR | 82 | 2020-06-23 | 82 | SERV | SERVICE | 40306494902 | 506 | ENOI | 6 | 1 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | unknown vehicle hit service while cleaning out empty lot next to location ripped down service and damaged meter pan stem pipe HOLD FOR PERMIT | -90.0597 | 30.0216 | NP | 210557 | Jan1 to Yesterday | Public Damage | Service Conductor | Public Damage | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 5 | 2020 | 1327463597 | Yes | ORLEANS | FAIR | 83 | 2020-04-13 | 415 | TFUS | 58389 | 40281489566 | 1704 | ENOI | 1 | 5 | EFLK | Equipment Failure - Fuse Link | N | REFUSED XFMR | -90.0607 | 30.007 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 1973 | 2020 | 1328252497 | Yes | EAST ORLEANS | THDR | 83 | 2020-04-18 | 163759 | RCLR | 25915 | 4284250608 | 2215 | ENOI | 6 | 1973 | EMER | Emergency Switching | N | Taken out when pole broke out due to fire. See breaker case. Went out at the same time | -89.9795 | 30.0516 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Recloser | Emergency Switching | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 7 | 2020 | 1323543759 | Yes | ORLEANS | FAIR | 84 | 2020-02-05 | 588 | TFUS | 79233 | 38298464075 | 2013 | ENOI | 1 | 7 | VLGL | Tree/Limb Growing Inside R.O.W. | N | palm tree branches hitting power lines in rear, trimmed what could get need vegetation to clear lines vege ticket created jmulle2 | -90.1242 | 29.9374 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 5 | 2020 | 1328065432 | Yes | ORLEANS | FAIR | 84 | 2020-04-16 | 420 | LFUS | 61731 | 38375461112 | 1917 | ENOI | 1 | 5 | VOHL | Overhanging Limb | N | tree limbs got lateral together; refused | -90.1219 | 29.9294 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 6 | 2020 | 1330023903 | Yes | ORLEANS | FAIR | 84 | 2020-05-07 | 504 | TFUS | 68159 | 38939477821 | 2026 | ENOI | 1 | 6 | ASQL | Animal - Squirrel | N | refused transformer, taken out by squirrel, installed animal gaurd | -90.1036 | 29.9751 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 167 | 2020 | 1323138006 | Yes | ALGIERS ELEC ONLY | THDR | 85 | 2020-01-23 | 14195 | RCLR | 5123 | 4150446191 | W0725 | ENOI | 81 | 167 | EMER | Emergency Switching | N | phase down on arm | -90.0231 | 29.9306 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Recloser | Emergency Switching | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 64 | 2020 | 1325827386 | Yes | EAST ORLEANS | FAIR | 85 | 2020-03-25 | 5440 | LFUS | 21147 | 4069347881 | 623 | ENOI | 6 | 64 | EARR | Equipment Failure - Arrestor | N | refused a phase..cleared arestor.. | -90.0481 | 29.9772 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 24 | 2020 | 1330267184 | Yes | ORLEANS | FAIR | 85 | 2020-05-11 | 2040 | TFUS | 20432 | 38950495409 | 402 | ENOI | 1 | 24 | AOTH | Animal - Other (Describe in Remarks Field) | N | squirrel refusedSQUIRREL TOOK OUT B PHASE AT TERMINAL POLE | -90.1024 | 30.0234 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70124 | 5
2020 | 6 | 2020 | 1332579461 | Yes | EAST ORLEANS | FAIR | 85 | 2020-06-07 | 510 | TFUS | 61392 | 42467503910 | 2215 | ENOI | 6 | 6 | UNKN | Inspected Unknown | N | Fuse blown went back in weather is fair | -89.9911 | 30.0459 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 42 | 2020 | 1323799758 | Yes | EAST ORLEANS | FAIR | 86 | 2020-02-10 | 3612 | LFUS | 17586 | 4099049317 | 508 | ENOI | 6 | 42 | EMER | Emergency Switching | N | crew straighting a pole | -90.0383 | 30.0167 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Emergency Switching | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1 | 2020 | 1324109171 | Yes | ALGIERS ELEC ONLY | FAIR | 86 | 2020-02-18 | 86 | SERV | SERVICE COND | 4212046002 | W1726 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N | Replaced connection on service line............PC | -90.0036 | 29.9252 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 2
2020 | 18 | 2020 | 1325039518 | Yes | EAST ORLEANS | RAIN | 86 | 2020-03-04 | 1548 | LFUS | 62285 | 41776478254 | 612 | ENOI | 6 | 18 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused lat..same as choctaw..wether | -90.014 | 29.9755 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 5 | 2020 | 1325467795 | Yes | EAST ORLEANS | FAIR | 86 | 2020-03-17 | 430 | TFUS | 1048649 | 44560510150 | 2213 | ENOI | 6 | 5 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | Contractors changing meters left breaker off NO PID | -89.9248 | 30.0623 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 1255 | 2020 | 1330667111 | Yes | ORLEANS | THDR | 86 | 2020-05-15 | 107930 | SBKR | 1553 | 3950346992 | 1553 | ENOI | 1 | 1255 | EPRI | Equipment Failure - Primary Conductor | N | wire down, switched out to pick up load | -90.086 | 29.9532 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 109 | 2020 | 1330875601 | Yes | ORLEANS | FAIR | 86 | 2020-05-18 | 9374 | LFUS | 27642 | 3849547154 | 2015 | ENOI | 1 | 109 | VLFL | Tree On Line Outside R.O.W | N | A Phase blown limb on line HW | -90.1179 | 29.9579 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 5
2020 | 11 | 2020 | 1332667181 | Yes | ORLEANS | RAIN | 86 | 2020-06-08 | 946 | TFUS | 517221 | 38337458934 | 1914 | ENOI | 1 | 11 | ESEC | Secondary/Service Conductor | N | refused | -90.1231 | 29.9233 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 10 | 2020 | 1333708543 | Yes | EAST ORLEANS | FAIR | 86 | 2020-06-25 | 860 | XFMR | 56467 | 40684488987 | 1702 | ENOI | 6 | 10 | ETRD | Equipment Failure - Transformer | N | transformer lid blown off oil on ground call environmental called crew Chad Gould | -90.048 | 30.0054 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 6 | 2020 | 1323534021 | Yes | EAST ORLEANS | RAIN | 87 | 2020-02-05 | 522 | TFUS | 66110 | 43572495525 | 1601 | ENOI | 6 | 6 | LGHT | Lightning | N | weather | -89.9566 | 30.0223 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1 | 2020 | 1331259986 | Yes | ORLEANS | FAIR | 87 | 2020-05-23 | 87 | SERV | SERVICE | 38041465503 | B0527 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | hot leg burned off at transformer | -90.1324 | 29.9415 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 225 | 2020 | 1331027686 | Yes | ORLEANS | FAIR | 88 | 2020-05-20 | 19800 | DIS | 23596 | 3953947389 | 907 | ENOI | 1 | 225 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Suspect balloons root cause along with phase slap afterwards: See breaker case | -90.0846 | 29.9641 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Other | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 23 | 2020 | 1332784990 | Yes | ORLEANS | FAIR | 88 | 2020-06-09 | 2024 | LFUS | 36892 | 3844646852 | 2016 | ENOI | 1 | 23 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1194 | 29.9495 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 23 | 2020 | 1321643125 | Yes | ORLEANS | THDR | 89 | 2020-01-02 | 2047 | LFUS | 27621 | 3858046356 | 1926 | ENOI | 1 | 23 | VOHL | Overhanging Limb | N | Crew on site picking up down primary | -90.1153 | 29.936 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 1
2020 | 8 | 2020 | 1323613484 | Yes | ORLEANS | RAIN | 89 | 2020-02-06 | 712 | TFUS | 60606 | 39493474594 | 907 | ENOI | 1 | 8 | ESEC | Secondary/Service Conductor | N | service wire failure caused transformer to fault. | -90.0861 | 29.9661 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 2
2020 | 127 | 2020 | 1323889600 | Yes | EAST ORLEANS | FAIR | 89 | 2020-02-12 | 11303 | LFUS | 27886 | 4082247647 | 622 | ENOI | 6 | 127 | UNKN | Inspected Unknown | N | Refused C phase at sw# 27886--Inspect unknown | -90.0441 | 29.9707 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 4 | 2020 | 1323938290 | Yes | EAST ORLEANS | FAIR | 89 | 2020-02-13 | 356 | TFUS | 32883 | 41762479118 | 612 | ENOI | 6 | 4 | VINE | Vine Growing into Line | N | dead vines..clear | -90.0144 | 29.9778 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 24 | 2020 | 1326987204 | Yes | ORLEANS | THDR | 89 | 2020-04-12 | 2136 | LFUS | 36920 | 3912948070 | 904 | ENOI | 1 | 24 | LGHT | Lightning | N | weather | -90.0974 | 29.9829 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 17 | 2020 | 1329905796 | Yes | ORLEANS | FAIR | 89 | 2020-05-05 | 1513 | LFUS | 75828 | 3989347536 | 1512 | ENOI | 1 | 17 | UNKN | Inspected Unknown | N | c phase on lateral was blown. inspected unknown. refused ok. | -90.0736 | 29.968 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 35 | 2020 | 1333571139 | Yes | EAST ORLEANS | RAIN | 89 | 2020-06-23 | 3115 | LFUS | 21259 | 4249750190 | 2216 | ENOI | 6 | 35 | LGHT | Lightning | N | refused lat | -89.9903 | 30.04 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 1 | 2020 | 1323096832 | Yes | ORLEANS | FAIR | 90 | 2020-01-22 | 90 | SERV | SERVICE | 39963459713 | 2147 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | bad connection at pole | -90.0718 | 29.9251 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 427 | 2020 | 1323653581 | Yes | EAST ORLEANS | WIND | 91 | 2020-02-07 | 38857 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 427 | EARM | Equipment Failure - Crossarm | N | Recloser was locked out; See recloser case | -90.0021 | 29.9747 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 28 | 2020 | 1324786656 | Yes | ORLEANS | FAIR | 91 | 2020-03-02 | 2548 | LFUS | 37635 | 3979848210 | 1705 | ENOI | 1 | 28 | EFLK | Equipment Failure - Fuse Link | N | latera fuse blown, refused. everything ok. | -90.0763 | 29.9865 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 29 | 2020 | 1328476758 | Yes | ORLEANS | FAIR | 91 | 2020-04-20 | 2639 | LFUS | 27933 | 4002247569 | 1712 | ENOI | 1 | 29 | LGHT | Lightning | N | Bc phases blown. Possibly from bad weather last night | -90.0694 | 29.9689 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 12 | 2020 | 1333573668 | Yes | ORLEANS | FAIR | 91 | 2020-06-23 | 1092 | TFUS | 3010046 | 39332457070 | 1922 | ENOI | 1 | 12 | LGHT | Lightning | N |  | -90.0919 | 29.9179 | NP | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 2 | 2020 | 1323182720 | Yes | ORLEANS | FAIR | 92 | 2020-01-24 | 184 | LFUS | 37944 | 38356458630 | 1914 | ENOI | 1 | 2 | EFLK | Equipment Failure - Fuse Link | N | Found phase switch blown on lateral to closed delta bank. Inspected primary and found flash mark where wire touched other potential. Refused lateral phase and threw it in. Back in lights. | -90.1226 | 29.9225 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 461 | 2020 | 1331523595 | Yes | ORLEANS | FAIR | 92 | 2020-05-26 | 42412 | RCLR | 24555 | 3978448919 | 1704 | ENOI | 1 | 461 | EARM | Equipment Failure - Crossarm | N | crossarm broke at perlita at mandolin | -90.0763 | 30.006 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 7 | 2020 | 1333180876 | Yes | EAST ORLEANS | FAIR | 92 | 2020-06-17 | 644 | TFUS | 71019 | 41133476214 | 611 | ENOI | 6 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0341 | 29.97 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 1 | 2020 | 1333180768 | Yes | EAST ORLEANS | FAIR | 92 | 2020-06-17 | 92 | TFUS | 1413542 | 41136476300 | 611 | ENOI | 6 | 1 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.034 | 29.9703 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 496 | 2020 | 1333878870 | Yes | ORLEANS | FAIR | 92 | 2020-06-26 | 45632 | RCLR | 62257 | 3890445946 | 1914 | ENOI | 1 | 496 | EARM | Equipment Failure - Crossarm | N | broken x arm | -90.1054 | 29.9247 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 10 | 2020 | 1322249652 | Yes | EAST ORLEANS | THDR | 93 | 2020-01-11 | 930 | LFUS | 38536 | 43220496192 | 1611 | ENOI | 6 | 10 | LGHT | Lightning | N | Changed **TFUS 1361822 8 to LFUS 1361822 8** --- refused B and C phase on lateral 38536 due to weather jvickna | -89.9677 | 30.0243 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 82 | 2020 | 1323525729 | Yes | ORLEANS | FAIR | 93 | 2020-02-05 | 7954 | DIS | 24330 | 3852446954 | 2016 | ENOI | 1 | 82 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1168 | 29.9525 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 7 | 2020 | 1332296675 | Yes | ORLEANS | FAIR | 93 | 2020-06-04 | 651 | TFUS | 1096588 | 39041467957 | 1553 | ENOI | 1 | 7 | VINE | Vine Growing into Line | N |  | -90.1006 | 29.948 | NP | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 31 | 2020 | 1333057543 | Yes | EAST ORLEANS | FAIR | 93 | 2020-06-14 | 3818 | LFUS | 37015 | 4208449910 | 2212 | ENOI | 6 | 31 | ETRD | Equipment Failure - Transformer | N | crew to change | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 30 | 2020 | 1333658927 | Yes | ORLEANS | THDR | 93 | 2020-06-24 | 2790 | LFUS | 28016 | 3959645842 | 2147 | ENOI | 1 | 30 | ASQL | Animal - Squirrel | N | Taken out by squirrel | -90.0832 | 29.9216 | NP | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 10 | 2020 | 1324327115 | Yes | ORLEANS | FAIR | 94 | 2020-02-21 | 940 | TFUS | 51666 | 39674493122 | 509 | ENOI | 1 | 10 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0799 | 30.017 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 37 | 2020 | 1328777629 | Yes | EAST ORLEANS | THDR | 94 | 2020-04-23 | 3478 | LFUS | 28007 | 4153647424 | 2347 | ENOI | 6 | 37 | EFLK | Equipment Failure - Fuse Link | N | REFUSED OKAY | -90.0216 | 29.9645 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 7 | 2020 | 1333119827 | Yes | EAST ORLEANS | FAIR | 94 | 2020-06-16 | 658 | TFUS | 566788 | 40676494014 | 506 | ENOI | 6 | 7 | ASQL | Animal - Squirrel | N | Refused transformer taken out by squirrel | -90.0482 | 30.019 | NP | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 10 | 2020 | 1333619744 | Yes | ORLEANS | THDR | 94 | 2020-06-24 | 940 | TFUS | 1527752 | 38973491142 | 403 | ENOI | 1 | 10 | VLFL | Tree On Line Outside R.O.W | N | limb on service pulled out of connections | -90.102 | 30.0118 | NP | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 5 | 2020 | 1333721976 | Yes | ORLEANS | FAIR | 94 | 2020-06-25 | 470 | TFUS | 3001560 | 39771487672 | 1704 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N |  | -90.0768 | 30.0019 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 93 | 2020 | 1323549802 | Yes | EAST ORLEANS | THDR | 95 | 2020-02-05 | 8835 | SBKR | 621 | 4081848423 | 621 | ENOI | 6 | 93 | ECNS | Equipment Failure - Connector Sleeve | N | crew tripped due to down wire due to failed kearney coonection | -90.044 | 29.9922 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 23 | 2020 | 1325120864 | Yes | EAST ORLEANS | FAIR | 95 | 2020-03-05 | 2185 | LFUS | LFUS | 00000000000 | 2211 | ENOI | 6 | 23 | UNKN | Inspected Unknown | N | refused u/g lat..checked trans ..holding |  |  | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 3 | 2020 | 1326228392 | Yes | EAST ORLEANS | FAIR | 95 | 2020-04-02 | 285 | TFUS | 1307146 | 4073147859 | 622 | ENOI | 6 | 3 | AOTH | Animal - Other (Describe in Remarks Field) | N | Animal caused transformer fuse to blow. Cust back in lights. | -90.0467 | 29.9767 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 53 | 2020 | 1328281315 | Yes | ORLEANS | THDR | 95 | 2020-04-18 | 5035 | LFUS | 33992 | 3981445947 | 2147 | ENOI | 1 | 53 | EARM | Equipment Failure - Crossarm | N | Crew on site replacing arm | -90.0767 | 29.9244 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 30 | 2020 | 1332262706 | Yes | ORLEANS | FAIR | 95 | 2020-06-04 | 2850 | LFUS | 84239 | 3940545840 | 2147 | ENOI | 1 | 30 | UNKN | Inspected Unknown | N | refused ok | -90.0896 | 29.9216 | NP | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 6 | 2020 | 1333098000 | Yes | EAST ORLEANS | FAIR | 95 | 2020-06-15 | 570 | TFUS | 66883 | 40820476016 | 614 | ENOI | 6 | 6 | VHCL | Vehicle | N | dumpped truck hit service line ripped it down and broke open wire secondary burned insulation fell on customer vehicle and burned his paint off but i picked up open wire and and cut down service that was hit | -90.0441 | 29.9697 | NP | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 1 | 2020 | 1322322442 | Yes | EAST ORLEANS | THDR | 96 | 2020-01-11 | 96 | LFUS | 83983 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | vines took out b phase on terminal pole-cleared vines and refused b phase ok-voltage ok-cust back on swalsh1 1-11-20 swalsh1 | -90.0377 | 30.0062 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 5 | 2020 | 1328110621 | Yes | EAST ORLEANS | FAIR | 96 | 2020-04-16 | 480 | TFUS | 1087299 | 42802502570 | 2216 | ENOI | 6 | 5 | UNKN | Inspected Unknown | N | refused sand fuse in valt..good volt | -89.9807 | 30.042 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 120 | 2020 | 1328608621 | Yes | EAST ORLEANS | WIND | 96 | 2020-04-22 | 11520 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 120 | VHCL | Vehicle | N | Crew on site replacing broken pole | -90.0356 | 29.9933 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Substation Breaker | Public Damage | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 6 | 2020 | 1332215038 | Yes | ORLEANS | FAIR | 96 | 2020-06-03 | 576 | TFUS | 69023 | 40146485975 | 1704 | ENOI | 1 | 6 | UNKN | Inspected Unknown | N | unknown what took out transforner, was tested ok, refused ok,. transformer does have animal guard. | -90.0651 | 29.9971 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 6 | 2020 | 1321686189 | Yes | EAST ORLEANS | FAIR | 97 | 2020-01-03 | 582 | XFMR | 1373368 | 43960512098 | 2217 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N | bad transformer | -89.9437 | 30.0677 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 1 | 2020 | 1331002598 | Yes | ORLEANS | FAIR | 97 | 2020-05-20 | 97 | SERV | METER | 38994475708 | 2011 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter off remotely call AMOC turned meter on | -90.102 | 29.9693 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 1 | 2020 | 1331565781 | Yes | ORLEANS | FAIR | 97 | 2020-05-26 | 97 | SERV | SERVICE COND | 38665462793 | 1927 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.1127 | 29.9339 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 11 | 2020 | 1323273155 | Yes | ORLEANS | FAIR | 98 | 2020-01-28 | 1078 | TFUS | 61598 | 39294467195 | 2021 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0927 | 29.9459 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 87 | 2020 | 1328325028 | Yes | ORLEANS | RAIN | 98 | 2020-04-19 | 8526 | LFUS | 38032 | 3893546975 | 2015 | ENOI | 1 | 87 | EINS | Equipment Failure - Insulator | N | Changed insulator at eden and salcedo | -90.1038 | 29.953 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 1 | 2020 | 1330684317 | Yes | ORLEANS | THDR | 98 | 2020-05-15 | 98 | LFUS | 22069 | 4020248327 | 627 | ENOI | 1 | 1 | LGHT | Lightning | N | refused b phase on lateral | -90.0634 | 29.9895 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 8 | 2020 | 1331270112 | Yes | ORLEANS | THDR | 98 | 2020-05-23 | 784 | TFUS | 619393 | 3986048910 | 1704 | ENOI | 1 | 8 | LGHT | Lightning | N | transformer refused ok | -90.0742 | 30.0058 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 347 | 2020 | 1321742427 | Yes | EAST ORLEANS | FAIR | 99 | 2020-01-05 | 34353 | VFI | 38268 | 4264649768 | 1602 | ENOI | 6 | 347 | EFLK | Equipment Failure - Fuse Link | N | fault behind lateral 73441 | -89.9934 | 30.0265 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 61 | 2020 | 1328538247 | Yes | ORLEANS | FAIR | 99 | 2020-04-21 | 6039 | LFUS | 33188 | 3971145871 | 2146 | ENOI | 1 | 61 | ASQL | Animal - Squirrel | N | b phase blown; taken out bby squirrel | -90.0798 | 29.9224 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 32 | 2020 | 1323593781 | Yes | EAST ORLEANS | FAIR | 100 | 2020-02-05 | 3200 | LFUS | 27190 | 4450051090 | 2213 | ENOI | 6 | 32 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 1 | 2020 | 1326262368 | Yes | ORLEANS | FAIR | 100 | 2020-04-03 | 100 | SERV | SERVICE COND | 38160462631 | 2013 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad connection at weatherhead | -90.1286 | 29.9335 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 27 | 2020 | 1333647918 | Yes | EAST ORLEANS | THDR | 100 | 2020-06-24 | 2700 | LFUS | 27963 | 4064048886 | 1702 | ENOI | 6 | 27 | EARM | Equipment Failure - Crossarm | N |  | -90.0493 | 30.005 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 555 | 2020 | 1333765610 | Yes | ORLEANS | FAIR | 100 | 2020-06-25 | 55500 | RCLR | 54026 | 3988249289 | 510 | ENOI | 1 | 555 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up on pelita north of prentiss | -90.0733 | 30.0161 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 1 | 2020 | 1323068509 | Yes | ALGIERS ELEC ONLY | FAIR | 101 | 2020-01-21 | 101 | SERV | SERVICE | 4252245651 | W1714 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N |  | -89.9912 | 29.9154 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 12 | 2020 | 1326794775 | Yes | ORLEANS | FAIR | 101 | 2020-04-10 | 1212 | TFUS | 71021 | 39712482456 | 1705 | ENOI | 1 | 12 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0789 | 29.9877 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 23 | 2020 | 1333325959 | Yes | ORLEANS | FAIR | 102 | 2020-06-20 | 2346 | LFUS | 27715 | 3916545880 | 1923 | ENOI | 1 | 23 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Balloons took out B phase lateral | -90.097 | 29.9228 | NP | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 94 | 2020 | 1324247481 | Yes | ALGIERS ELEC ONLY | THDR | 103 | 2020-02-20 | 9682 | RCLR | 1136 | 4182146253 | W0722 | ENOI | 81 | 94 | LGHT | Lightning | N | lighting took out center phase recloser | -90.0129 | 29.9323 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Recloser | Lightning | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 14 | 2020 | 1324202736 | Yes | EAST ORLEANS | RAIN | 103 | 2020-02-20 | 1442 | LFUS | 21695 | 4038148637 | 1708 | ENOI | 6 | 14 | EFLK | Equipment Failure - Fuse Link | N | blown fuse on transformer and lateral taken out by bad weather | -90.0579 | 29.9982 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1 | 2020 | 1325292073 | Yes | EAST ORLEANS | FAIR | 103 | 2020-03-11 | 103 | TFUS | 1213434 | 41139478965 | 621 | ENOI | 6 | 1 | SCHD | Scheduled Interruption | N | Schedule outage. Contractors notified Sewage and Waterboard. | -90.0338 | 29.9775 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 11 | 2020 | 1331463282 | Yes | ORLEANS | FAIR | 103 | 2020-05-26 | 1133 | TFUS | 1000462 | 39789459299 | 2147 | ENOI | 1 | 11 | ASQL | Animal - Squirrel | N | taken out by squirrel refused ok | -90.0773 | 29.9239 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70130 | 5
2020 | 71 | 2020 | 1332270155 | Yes | ORLEANS | FAIR | 103 | 2020-06-04 | 7313 | LFUS | 37635 | 3979848210 | 1705 | ENOI | 1 | 71 | ASQL | Animal - Squirrel | N |  | -90.0763 | 29.9865 | NP | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 50 | 2020 | 1324308301 | Yes | ORLEANS | WIND | 104 | 2020-02-20 | 5200 | LFUS | 44646 | 3853148813 | 410 | ENOI | 1 | 50 | EFLK | Equipment Failure - Fuse Link | N | Refused latteral | -90.116 | 30.0036 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 78 | 2020 | 1324642076 | Yes | EAST ORLEANS | FAIR | 104 | 2020-02-28 | 8112 | LFUS | 27321-F | 4235149906 | 2211 | ENOI | 6 | 78 | UNKN | Inspected Unknown | N | c phase blown; refused and held | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 25 | 2020 | 1324949281 | Yes | EAST ORLEANS | FAIR | 104 | 2020-03-04 | 2600 | LFUS | 50003 | 4068547762 | 622 | ENOI | 6 | 25 | EFLK | Equipment Failure - Fuse Link | N | when refused a phase lateral 50003 lights came back on at this location | -90.0485 | 29.974 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 19 | 2020 | 1325408219 | Yes | EAST ORLEANS | FAIR | 104 | 2020-03-15 | 1976 | TFUS | 60581 | 40900477062 | 622 | ENOI | 6 | 19 | VHCL | Vehicle | N | car hit pole | -90.0416 | 29.9724 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 584 | 2020 | 1328318653 | Yes | ORLEANS | FAIR | 104 | 2020-04-18 | 60736 | OPEN | 3990247381 | 3990247381 | 1511 | ENOI | 1 | 584 | ECNS | Equipment Failure - Connector Sleeve | N | A phase jumper burned open: Isolated & picked up load | -90.0733 | 29.9638 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Open | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70116 | 4
2020 | 3 | 2020 | 1329426889 | Yes | EAST ORLEANS | WIND | 104 | 2020-04-29 | 312 | LFUS | 21238 | 44436494079 | 1203 | ENOI | 6 | 3 | VINE | Vine Growing into Line | N | Lat was taken out during high wind. re fused ok made customer contact MJackson | -89.9294 | 30.018 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 9 | 2020 | 1332121699 | Yes | EAST ORLEANS | FAIR | 104 | 2020-06-01 | 936 | TFUS | 57170 | 40502478854 | 613 | ENOI | 6 | 9 | ASQL | Animal - Squirrel | N | refused | -90.054 | 29.9775 | NP | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 13 | 2020 | 1333073807 | Yes | ORLEANS | FAIR | 104 | 2020-06-15 | 6968 | LFUS | 21921 | 3861648402 | 407 | ENOI | 1 | 13 | EARR | Equipment Failure - Arrestor | N |  | -90.1136 | 29.9922 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 16 | 2020 | 1321759209 | Yes | EAST ORLEANS | FAIR | 105 | 2020-01-06 | 1680 | TFUS | 569328 | 40728487726 | 1702 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N | Crew On Site Working | -90.0467 | 30.0019 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 114 | 2020 | 1323981833 | Yes | ORLEANS | FAIR | 105 | 2020-02-14 | 11970 | LFUS | 21458 | 3906145893 | 1923 | ENOI | 1 | 114 | UNKN | Inspected Unknown | N | refused okk | -90.1004 | 29.9231 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 7 | 2020 | 1325298558 | Yes | ORLEANS | FAIR | 105 | 2020-03-11 | 735 | TFUS | 56899 | 39535483021 | 627 | ENOI | 1 | 7 | EARR | Equipment Failure - Arrestor | N | blown arrestor cleared and refused. per 310 | -90.0845 | 29.9892 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 3
2020 | 37 | 2020 | 1329238465 | Yes | ORLEANS | RAIN | 105 | 2020-04-28 | 3885 | LFUS | 44646 | 3853148813 | 410 | ENOI | 1 | 37 | SLAK | Slack Conductor / Loose Connection | N | found slack span in front of 247 26th st. refused ok got together during storm. per 310 | -90.1159 | 30.0035 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 3 | 2020 | 1329485598 | Yes | EAST ORLEANS | THDR | 105 | 2020-04-29 | 315 | LFUS | 76989 | 4242050231 | 2211 | ENOI | 6 | 3 | VLGL | Tree/Limb Growing Inside R.O.W. | N | A&B phase blown due to tree limb fell across phases. Made customer contact MJackson | -89.9927 | 30.0413 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 413 | 2020 | 1333584625 | Yes | ORLEANS | THDR | 105 | 2020-06-23 | 43365 | LFUS | 27700 | 4030447510 | 614 | ENOI | 1 | 413 | LGHT | Lightning | N | refused | -90.0603 | 29.9673 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 7 | 2020 | 1334030555 | Yes | ORLEANS | FAIR | 105 | 2020-06-29 | 735 | TFUS | 78564 | 38489463105 | 1926 | ENOI | 1 | 7 | EFSW | Equipment Failure - Fuse Switch | N |  | -90.1184 | 29.9349 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 140 | 2020 | 1323713292 | Yes | ORLEANS | FAIR | 106 | 2020-02-08 | 14840 | LFUS | 37734 | 4029548586 | 1708 | ENOI | 1 | 140 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | b phase only | -90.0603 | 29.9969 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 3 | 2020 | 1328337251 | Yes | EAST ORLEANS | FAIR | 106 | 2020-04-19 | 318 | TFUS | 1307146 | 4073147859 | 622 | ENOI | 6 | 3 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Removed debris off wire | -90.0467 | 29.9767 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 536 | 2020 | 1331028744 | Yes | ORLEANS | FAIR | 106 | 2020-05-20 | 56816 | DIS | 23879 | 3956947403 | 907 | ENOI | 1 | 536 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | suspect balloons root cause with phase slap afterwards: See breaker case | -90.0838 | 29.9646 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Other | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 76 | 2020 | 1333991456 | Yes | ORLEANS | FAIR | 106 | 2020-06-29 | 8056 | LFUS | 91343 | 3828347053 | 2013 | ENOI | 1 | 76 | EMER | Emergency Switching | N | broken crossarm | -90.1246 | 29.9551 | NP | 210557 | Jan1 to Yesterday | Other | Line Fuse | Emergency Switching | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 1 | 2020 | 1323546098 | Yes | EAST ORLEANS | RAIN | 107 | 2020-02-05 | 107 | LFUS | 83983 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | John Domangue cleared vines on pole and refused lateral per OC | -90.0377 | 30.0062 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 10 | 2020 | 1328302045 | Yes | ORLEANS | FAIR | 107 | 2020-04-18 | 1070 | TFUS | 18352 | 38939487697 | 403 | ENOI | 1 | 10 | LGHT | Lightning | N | refused ok. per 310 | -90.1032 | 30.0023 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 134 | 2020 | 1323441474 | Yes | EAST ORLEANS | FAIR | 108 | 2020-02-03 | 14472 | LFUS | 21152 | 4051147776 | 623 | ENOI | 6 | 134 | SCHD | Scheduled Interruption | N | crew onsite making repairs | -90.0538 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 123 | 2020 | 1325285548 | Yes | ORLEANS | FAIR | 108 | 2020-03-11 | 13284 | LFUS | 38033 | 3893046944 | 2015 | ENOI | 1 | 123 | EARM | Equipment Failure - Crossarm | N | changed crossarm. refused lateral. per 310 | -90.1043 | 29.9522 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 27 | 2020 | 1326179860 | Yes | ORLEANS | FAIR | 108 | 2020-04-01 | 2916 | LFUS | 177730 | 3854948315 | 408 | ENOI | 1 | 27 | ECNS | Equipment Failure - Connector Sleeve | N | RISER CAME OUT OF SWITCH PUT RISER BACK IN SWITCH | -90.1157 | 29.9899 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 30 | 2020 | 1322330888 | Yes | ORLEANS | THDR | 109 | 2020-01-11 | 3270 | LFUS | 27906 | 38475463265 | 1926 | ENOI | 1 | 30 | LGHT | Lightning | N | lightning took out c phase of lateral 27906 refused ok rbiles | -90.1186 | 29.9353 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 1 | 2020 | 1326232086 | Yes | ORLEANS | FAIR | 109 | 2020-04-02 | 109 | SERV | SERVICE COND | 3986147400 | 907 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | repaired bad UG block | -90.0746 | 29.9643 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 6 | 2020 | 1333164128 | Yes | ORLEANS | FAIR | 109 | 2020-06-17 | 654 | TFUS | 57973 | 39667488116 | 1704 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0803 | 30.0031 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 26 | 2020 | 1321808505 | Yes | ORLEANS | FAIR | 110 | 2020-01-07 | 2860 | LFUS | 37703 | 3947445909 | 2147 | ENOI | 1 | 26 | ASQL | Animal - Squirrel | N | got across lateral and blew 2 phases | -90.0873 | 29.9236 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 9 | 2020 | 1323304403 | Yes | ORLEANS | FAIR | 110 | 2020-01-29 | 990 | TFUS | 1361517 | 38447493598 | 409 | ENOI | 1 | 9 | EFSW | Equipment Failure - Fuse Switch | N | no comments | -90.1185 | 30.0186 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 6 | 2020 | 1323312030 | Yes | ORLEANS | FAIR | 110 | 2020-01-29 | 660 | TFUS | 1417271 | 39826488565 | 1704 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | fuse link corroded and broke. replaced and reenergized ok. | -90.0752 | 30.0044 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 1 | 2020 | 1325381288 | Yes | EAST ORLEANS | FAIR | 110 | 2020-03-14 | 110 | LFUS | 17169 | 41375485531 | 616 | ENOI | 6 | 1 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused lateral | -90.025 | 29.997 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 2410 | 2020 | 1328242641 | Yes | ORLEANS | THDR | 110 | 2020-04-18 | 265100 | SBKR | 2147 | 4012946119 | 2147 | ENOI | 1 | 2410 | EARM | Equipment Failure - Crossarm | N | Opened mid point switch. still patrolling | -90.0666 | 29.929 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 17 | 2020 | 1330207494 | Yes | ORLEANS | FAIR | 110 | 2020-05-09 | 1870 | TFUS | 60031 | 38934473379 | 2017 | ENOI | 1 | 17 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.1039 | 29.9629 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 5
2020 | 1 | 2020 | 1331008899 | Yes | ORLEANS | FAIR | 110 | 2020-05-20 | 110 | SERV | SERVICE | 39306476587 | 912 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.0921 | 29.9715 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 21 | 2020 | 1333627284 | Yes | ORLEANS | THDR | 110 | 2020-06-24 | 2310 | TFUS | 1002544 | 39508462370 | 2146 | ENOI | 1 | 21 | SCHD | Scheduled Interruption | N | crew had to repair secondary arm | -90.086 | 29.9326 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70113 | 6
2020 | 8 | 2020 | 1325298095 | Yes | ORLEANS | FAIR | 111 | 2020-03-11 | 888 | TFUS | 73749 | 39960488721 | 1704 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | crew has trans. out for repairs | -90.0709 | 30.0047 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 11 | 2020 | 1333126912 | Yes | EAST ORLEANS | FAIR | 111 | 2020-06-16 | 1221 | LFUS | 25844 | 4162647810 | 2325 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Crew On Site Working | -90.0187 | 29.975 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 9 | 2020 | 1334018406 | Yes | ORLEANS | FAIR | 111 | 2020-06-29 | 999 | TFUS | 1650346 | 38124468101 | 2014 | ENOI | 1 | 9 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -90.1297 | 29.9486 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 6 | 2020 | 1323291673 | Yes | ORLEANS | FAIR | 112 | 2020-01-29 | 672 | TFUS | 16216 | 3989349266 | 510 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | refused transformer ( Dloc. # 39896492416 ) taken out by weather, lateral was still in | -90.073 | 30.0155 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 75 | 2020 | 1323552613 | Yes | ORLEANS | WIND | 112 | 2020-02-05 | 8400 | DIS | 25426 | 3895046772 | 1553 | ENOI | 1 | 75 | EMER | Emergency Switching | N | Taken out for safety to replace burnt cross-arm & repair damaged phase | -90.1036 | 29.9474 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70125 | 2
2020 | 97 | 2020 | 1323767376 | Yes | EAST ORLEANS | FAIR | 112 | 2020-02-10 | 10864 | LFUS | 26127 | 4386451333 | 2223 | ENOI | 6 | 97 | SCHD | Scheduled Interruption | N | Contractor had outage for reliability work | -89.9466 | 30.0712 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 18 | 2020 | 1326816365 | Yes | ORLEANS | FAIR | 112 | 2020-04-11 | 2016 | TFUS | 1400854 | 39268479955 | 912 | ENOI | 1 | 18 | AOTH | Animal - Other (Describe in Remarks Field) | N | crow | -90.0931 | 29.9809 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 9 | 2020 | 1328475686 | Yes | ORLEANS | THDR | 112 | 2020-04-20 | 1008 | TFUS | 60379 | 39506479343 | 1705 | ENOI | 1 | 9 | LGHT | Lightning | N | Lightning; out from storm last night | -90.0856 | 29.9791 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 2110 | 2020 | 1330788429 | Yes | ORLEANS | FAIR | 112 | 2020-05-16 | 334706 | DIS | 23013 | 3947147058 | 1513 | ENOI | 1 | 2110 | EPRI | Equipment Failure - Primary Conductor | N | target on a phase exit cable bet MH 10-545 to MH3-54 | -90.0871 | 29.9551 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 67 | 2020 | 1332933772 | Yes | EAST ORLEANS | FAIR | 112 | 2020-06-11 | 7504 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 67 | ASQL | Animal - Squirrel | N | refused | -89.959 | 30.0234 | NP | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 45 | 2020 | 1333588583 | Yes | ORLEANS | THDR | 112 | 2020-06-23 | 5040 | LFUS | 36644 | 4028748693 | 1708 | ENOI | 1 | 45 | LGHT | Lightning | N | refused | -90.0607 | 29.9999 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 42 | 2020 | 1322269743 | Yes | ALGIERS ELEC ONLY | RAIN | 113 | 2020-01-11 | 4746 | LFUS | 5002 | 4141446606 | W1725 | ENOI | 81 | 42 | ETRD | Equipment Failure - Transformer | N | back n now bad pot brizzut | -90.0259 | 29.942 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 6 | 2020 | 1328538517 | Yes | ORLEANS | FAIR | 113 | 2020-04-21 | 678 | TFUS | 17319 | 39682493252 | 510 | ENOI | 1 | 6 | UNKN | Inspected Unknown | N | blown fuse; refused ok | -90.0796 | 30.0174 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 111 | 2020 | 1333880469 | Yes | ORLEANS | FAIR | 113 | 2020-06-26 | 12543 | LFUS | 21442 | 3868446213 | 1926 | ENOI | 1 | 111 | EARM | Equipment Failure - Crossarm | N | back in | -90.1121 | 29.9321 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 11 | 2020 | 1323610473 | Yes | ORLEANS | WIND | 114 | 2020-02-06 | 1254 | TFUS | 74399 | 40386478720 | 1709 | ENOI | 1 | 11 | LGHT | Lightning | N | refused transformer taken out by weather | -90.0577 | 29.9772 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70116 | 2
2020 | 48 | 2020 | 1323655644 | Yes | EAST ORLEANS | WIND | 114 | 2020-02-07 | 5472 | LFUS | 52377 | 4268250430 | 2215 | ENOI | 6 | 48 | ESEC | Secondary/Service Conductor | N |  | -89.9844 | 30.0466 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 70 | 2020 | 1325512369 | Yes | ORLEANS | FAIR | 114 | 2020-03-18 | 7980 | LFUS | 92823 | 3906745843 | 1923 | ENOI | 1 | 70 | ASQL | Animal - Squirrel | N | CLEARED BIRD INSTALLED BIRD GUARD | -90.1003 | 29.9218 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 2 | 2020 | 1326130727 | Yes | ORLEANS | FAIR | 114 | 2020-03-31 | 228 | TFUS | 57149 | 39014474170 | 912 | ENOI | 1 | 2 | SLAK | Slack Conductor / Loose Connection | N | slack span at gravier and s clark | -90.1013 | 29.9651 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 1 | 2020 | 1329813568 | Yes | ORLEANS | FAIR | 114 | 2020-05-03 | 114 | SERV | SERVICE | 38887458254 | 1921 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | PID in progress HW replaced damage service | -90.1058 | 29.9215 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 20 | 2020 | 1333643806 | Yes | ORLEANS | THDR | 114 | 2020-06-24 | 2280 | LFUS | 33642 | 3853646279 | 1926 | ENOI | 1 | 20 | SCHD | Scheduled Interruption | N | crew on site | -90.117 | 29.9339 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 26 | 2020 | 1323662339 | Yes | EAST ORLEANS | THDR | 115 | 2020-02-07 | 2990 | LFUS | 37094 | 4106547707 | 611 | ENOI | 6 | 26 | EARR | Equipment Failure - Arrestor | N | failed lightning arrestor on lateral/cleared/refused lateral | -90.0364 | 29.9723 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 8 | 2020 | 1328475576 | Yes | EAST ORLEANS | THDR | 115 | 2020-04-20 | 920 | TFUS | 62115 | 40549488407 | 1702 | ENOI | 6 | 8 | LGHT | Lightning | N | blown fuse on transformer; refused | -90.0522 | 30.0037 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 88 | 2020 | 1329776884 | Yes | ORLEANS | FAIR | 115 | 2020-05-02 | 13685 | LFUS | 21073 | 3876146762 | 1916 | ENOI | 1 | 88 | EARM | Equipment Failure - Crossarm | N | Replaced broken braces - B PHASE ONLY | -90.1095 | 29.9473 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 5
2020 | 1 | 2020 | 1332548786 | Yes | ORLEANS | THDR | 115 | 2020-06-07 | 115 | TFUS | 1355697 | 38590472530 | 2015 | ENOI | 1 | 1 | VLGL | Tree/Limb Growing Inside R.O.W. | N |  | -90.1147 | 29.9607 | NP | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 124 | 2020 | 1323665502 | Yes | EAST ORLEANS | FAIR | 116 | 2020-02-07 | 14384 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 124 | EFLK | Equipment Failure - Fuse Link | N | crew restored lateral | -90.0337 | 29.9718 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 7 | 2020 | 1323939896 | Yes | ORLEANS | FAIR | 117 | 2020-02-13 | 819 | XFMR | 1349264 | 38517477512 | 2026 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N | crew to change transformer | -90.1169 | 29.9743 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 1 | 2020 | 1329002900 | Yes | ORLEANS | FAIR | 117 | 2020-04-25 | 117 | SERV | METER | 39235459460 | 1923 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | bad ami meter | -90.0949 | 29.9245 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 20 | 2020 | 1325845296 | Yes | EAST ORLEANS | FAIR | 118 | 2020-03-26 | 2360 | LFUS | 25602 | 4319850532 | 2214 | ENOI | 6 | 20 | FOTH | Fire - Other (Describe in Remarks Field) | N | transformer caught firer, crew on site to repair | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 3 | 2020 | 1329090957 | Yes | ORLEANS | FAIR | 118 | 2020-04-27 | 354 | DIS | 23834 | 3957947276 | 1511 | ENOI | 1 | 3 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0834 | 29.9609 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 46 | 2020 | 1330168149 | Yes | ORLEANS | THDR | 118 | 2020-05-08 | 7788 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 46 | LGHT | Lightning | N | weather b phase taken out by lightning | -90.0879 | 29.975 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 3 | 2020 | 1331380316 | Yes | EAST ORLEANS | FAIR | 118 | 2020-05-25 | 354 | TFUS | 1161472 | 5041254760 | 1204 | ENOI | 6 | 3 | VOHL | Overhanging Limb | N | removed, spliced out and back on | -89.7383 | 30.1633 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 5
2020 | 42 | 2020 | 1325194517 | Yes | EAST ORLEANS | FAIR | 119 | 2020-03-08 | 4998 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 42 | ASQL | Animal - Squirrel | N | squrriel took out overhead lateral switch refused lateral road out underground lights back on and holdin n good voltage | -89.9561 | 30.0595 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 65 | 2020 | 1333585727 | Yes | ORLEANS | THDR | 119 | 2020-06-23 | 7735 | LFUS | 27792 | 3925145879 | 1923 | ENOI | 1 | 65 | LGHT | Lightning | N |  | -90.0945 | 29.9228 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 107 | 2020 | 1323849876 | Yes | EAST ORLEANS | FAIR | 120 | 2020-02-12 | 12840 | LFUS | 21798 | 4382851374 | 2223 | ENOI | 6 | 107 | SCHD | Scheduled Interruption | N |  | -89.9477 | 30.0724 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 24 | 2020 | 1325246985 | Yes | ORLEANS | FAIR | 120 | 2020-03-10 | 2880 | TFUS | 1002541 | 39724459733 | 2147 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | Scheduled Interruption; 601-910-1304 | -90.0794 | 29.9251 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 203 | 2020 | 1326341850 | Yes | ORLEANS | FAIR | 120 | 2020-04-05 | 24360 | LFUS | 97107 | 4016948726 | 1704 | ENOI | 1 | 203 | EARM | Equipment Failure - Crossarm | N |  | -90.0642 | 30.0006 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 1 | 2020 | 1326751623 | Yes | ORLEANS | THDR | 120 | 2020-04-10 | 120 | TFUS | 1096585 | 3929646618 | 2021 | ENOI | 1 | 1 | LGHT | Lightning | N | weather, refused | -90.0927 | 29.943 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70113 | 4
2020 | 74 | 2020 | 1330165160 | Yes | ORLEANS | THDR | 120 | 2020-05-08 | 8880 | LFUS | 27707 | 3919647432 | 912 | ENOI | 1 | 74 | EARM | Equipment Failure - Crossarm | N | Broken cross arm replaced | -90.0954 | 29.9654 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 30 | 2020 | 1331066380 | Yes | EAST ORLEANS | FAIR | 120 | 2020-05-21 | 3720 | LFUS | 21612 | 4048848961 | 1702 | ENOI | 6 | 30 | EPRI | Equipment Failure - Primary Conductor | N | primary down | -90.0543 | 30.007 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 2 | 2020 | 1333522911 | Yes | ORLEANS | FAIR | 120 | 2020-06-23 | 240 | TFUS | 69114 | 38585476539 | 2026 | ENOI | 1 | 2 | ASQL | Animal - Squirrel | N | squirrel on tf blown fuse refused ok | -90.1146 | 29.9717 | NP | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 9 | 2020 | 1323073215 | Yes | EAST ORLEANS | FAIR | 121 | 2020-01-21 | 1089 | TFUS | 64100 | 43284495685 | 1611 | ENOI | 6 | 9 | SCHD | Scheduled Interruption | N | crew opened for safety to transfer pole | -89.9656 | 30.0229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 122 | 2020 | 1323630435 | Yes | EAST ORLEANS | THDR | 121 | 2020-02-06 | 14762 | LFUS | 21152 | 4051147776 | 623 | ENOI | 6 | 122 | SCHD | Scheduled Interruption | N |  | -90.0538 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 13 | 2020 | 1326013533 | Yes | ORLEANS | FAIR | 121 | 2020-03-29 | 1573 | TFUS | 1531175 | 38472473660 | 2016 | ENOI | 1 | 13 | VINE | Vine Growing into Line | N | removed and refused | -90.1185 | 29.9639 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 3
2020 | 14 | 2020 | 1329158231 | Yes | EAST ORLEANS | FAIR | 121 | 2020-04-28 | 1694 | TFUS | 527849 | 40963476191 | 611 | ENOI | 6 | 14 | SCHD | Scheduled Interruption | N | back on | -90.0395 | 29.9701 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 120 | 2020 | 1326788132 | Yes | ORLEANS | THDR | 122 | 2020-04-10 | 14640 | LFUS | 27697 | 3980948243 | 1705 | ENOI | 1 | 120 | EPOL | Equipment Failure - Pole | N | broke pole | -90.0758 | 29.9876 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 511 | 2020 | 1330496581 | Yes | EAST ORLEANS | FAIR | 122 | 2020-05-13 | 62342 | VFI | 27422 | 4366350629 | 2213 | ENOI | 6 | 511 | EPRI | Equipment Failure - Primary Conductor | N | bad primary in between cub# 388 to cub # 569 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 96 | 2020 | 1330491982 | Yes | EAST ORLEANS | FAIR | 122 | 2020-05-13 | 11712 | SWIT | 27036 | 4381950738 | 2213 | ENOI | 6 | 96 | EPRI | Equipment Failure - Primary Conductor | N | bad cable from cub #388 to cub #569 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 7 | 2020 | 1334011350 | Yes | ORLEANS | FAIR | 122 | 2020-06-29 | 854 | TFUS | 58654 | 38998465345 | 1925 | ENOI | 1 | 7 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -90.1022 | 29.9408 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 16 | 2020 | 1323614486 | Yes | EAST ORLEANS | RAIN | 123 | 2020-02-06 | 1968 | TFUS | 1155554 | 40524474979 | 2347 | ENOI | 6 | 16 | VOHL | Overhanging Limb | N | removed palm limbs off of transformer reuse ok customer back in lights | -90.0536 | 29.9667 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 17 | 2020 | 1331066690 | Yes | EAST ORLEANS | FAIR | 123 | 2020-05-21 | 2091 | TFUS | 68781 | 40477489476 | 1702 | ENOI | 6 | 17 | EPRI | Equipment Failure - Primary Conductor | N | primary down | -90.0546 | 30.0068 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 5 | 2020 | 1323263389 | Yes | EAST ORLEANS | FAIR | 124 | 2020-01-28 | 620 | TFUS | 1087299 | 42802502570 | 2216 | ENOI | 6 | 5 | VHCL | Vehicle | N | someoned bumped cubicle and knocked out c phase | -89.9807 | 30.042 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 12 | 2020 | 1323289932 | Yes | ALGIERS ELEC ONLY | FAIR | 124 | 2020-01-29 | 1488 | XFMR | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | ETRD | Equipment Failure - Transformer | N | bad 100by in rear of 6315 brighton pl, rc 1-29-20 | -89.9867 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 57 | 2020 | 1323673353 | Yes | EAST ORLEANS | FAIR | 124 | 2020-02-07 | 7068 | LFUS | 37150 | 40855477822 | 622 | ENOI | 6 | 57 | ECNS | Equipment Failure - Connector Sleeve | N | made new kearney connection repair at trans. | -90.0431 | 29.9745 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 3 | 2020 | 1323734811 | Yes | ORLEANS | FAIR | 124 | 2020-02-09 | 372 | TFUS | 32116 | 39340459980 | 2147 | ENOI | 1 | 3 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons. refused ok RELATED TO TKT# 1323734811 (AKS) | -90.0915 | 29.9259 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 77 | 2020 | 1326526483 | Yes | ORLEANS | FAIR | 124 | 2020-04-08 | 9548 | LFUS | 21478 | 3908246060 | 1924 | ENOI | 1 | 77 | ECON | Equipment Failure - Connector / Sleeve | N | replaced hot line clamp and stirrup for lateral b phase. per 310 | -90.0997 | 29.9276 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 72 | 2020 | 1330839655 | Yes | EAST ORLEANS | FAIR | 124 | 2020-05-17 | 8928 | LFUS | 27691 | 4298950696 | 2215 | ENOI | 6 | 72 | HEMC | Mis-Coordination (Describe in remarks) | N | transformer fuse blown; refused transformer and sub lateral and main lateral | -89.9747 | 30.054 | 19-YTD20 | 210557 | Jan1 to Yesterday | Human Error | Line Fuse | Human Error | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 43 | 2020 | 1331066593 | Yes | EAST ORLEANS | FAIR | 124 | 2020-05-21 | 5332 | LFUS | 21623 | 4049048938 | 1702 | ENOI | 6 | 43 | EPRI | Equipment Failure - Primary Conductor | N | primary down | -90.0543 | 30.0064 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 4 | 2020 | 1333711757 | Yes | ORLEANS | FAIR | 124 | 2020-06-25 | 496 | TFUS | 1002081 | 40095462381 | 2142 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N |  | -90.0675 | 29.9323 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 8 | 2020 | 1321649001 | Yes | EAST ORLEANS | THDR | 125 | 2020-01-02 | 1000 | TFUS | 1137669 | 41102491707 | 501 | ENOI | 6 | 8 | EPRI | Equipment Failure - Primary Conductor | N | Crew on the way to repair burned up riser | -90.0348 | 30.0126 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 25 | 2020 | 1323220694 | Yes | ORLEANS | FAIR | 125 | 2020-01-26 | 3125 | LFUS | 27940 | 3927945767 | 1922 | ENOI | 1 | 25 | VINE | Vine Growing into Line | N | Vines. Refused ok Veg ticket created Jmulle2 | -90.0935 | 29.9194 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 77 | 2020 | 1324812511 | Yes | EAST ORLEANS | FAIR | 125 | 2020-03-03 | 9625 | LFUS | 37101 | 4159049958 | 1010 | ENOI | 6 | 77 | SCHD | Scheduled Interruption | N | crew completed work | -90.0193 | 30.0341 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 1420 | 2020 | 1331029587 | Yes | ORLEANS | FAIR | 125 | 2020-05-20 | 177500 | DIS | 23739 | 3970447578 | 907 | ENOI | 1 | 1420 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Suspect balloons was root cause with phase slap afterwards: See breaker case | -90.0794 | 29.9693 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Other | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 1 | 2020 | 1332641764 | Yes | EAST ORLEANS | RAIN | 125 | 2020-06-08 | 125 | TFUS | RXBS2559 | 41338496115 | 1002 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | repaired riser on switch customer back on | -90.027 | 30.0244 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 84 | 2020 | 1324375554 | Yes | ORLEANS | FAIR | 126 | 2020-02-22 | 10584 | LFUS | 21671 | 3979148836 | 1704 | ENOI | 1 | 84 | ETRD | Equipment Failure - Transformer | N | crew replaced xfmr | -90.0762 | 30.0038 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 5 | 2020 | 1331267147 | Yes | ORLEANS | THDR | 126 | 2020-05-23 | 630 | XFMR | 78198 | 38798463576 | 1927 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | CHANGED TRANSFORMER | -90.1085 | 29.9359 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 30 | 2020 | 1332295679 | Yes | ORLEANS | FAIR | 126 | 2020-06-04 | 3780 | LFUS | 89174 | 3907846707 | 1922 | ENOI | 1 | 30 | VINE | Vine Growing into Line | N | Vines took out transformer & apparent flashover also took out lateral | -90.0995 | 29.9454 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 25 | 2020 | 1321769814 | Yes | EAST ORLEANS | FAIR | 128 | 2020-01-06 | 3200 | LFUS | 25370 | 4385351220 | 2217 | ENOI | 6 | 25 | EPRI | Equipment Failure - Primary Conductor | N | Switched out bad cable between V-24 to TP 25370 | -89.9472 | 30.0681 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 1 | 2020 | 1333063372 | Yes | ORLEANS | FAIR | 128 | 2020-06-14 | 128 | SERV | METER | 38315467599 | 2013 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | AMI meter opened internaly amock won t answer changed out meter | -90.1237 | 29.9473 | NP | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 63 | 2020 | 1325327742 | Yes | ORLEANS | FAIR | 130 | 2020-03-12 | 8190 | LFUS | 21302 | 3972447286 | 1511 | ENOI | 1 | 63 | EARR | Equipment Failure - Arrestor | N | refused lateral 21302 b and c phase | -90.0788 | 29.9612 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 75 | 2020 | 1325948510 | Yes | ORLEANS | FAIR | 130 | 2020-03-28 | 9750 | LFUS | 27715 | 3916545880 | 1922 | ENOI | 1 | 75 | VLFL | Tree On Line Outside R.O.W | N | removed and refused | -90.097 | 29.9228 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 5 | 2020 | 1328830984 | Yes | EAST ORLEANS | THDR | 130 | 2020-04-23 | 650 | TFUS | 60539 | 41083487388 | 616 | ENOI | 6 | 5 | ECON | Equipment Failure - Connector / Sleeve | N | Hot leg connection burned at the pole.Also had to refuse stinger pot. Customer back in lights. Made customer contact, he verified that all equipment is up and running. | -90.0353 | 30.0007 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 149 | 2020 | 1332065414 | Yes | EAST ORLEANS | FAIR | 130 | 2020-05-31 | 19370 | LFUS | 26215 | 4280450443 | 2216 | ENOI | 6 | 149 | ETRD | Equipment Failure - Transformer | N | Crew to replace bad padmount | -89.9806 | 30.0469 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 27 | 2020 | 1332545286 | Yes | ORLEANS | THDR | 130 | 2020-06-07 | 3510 | DIS | 25810 | 3982647107 | 1543 | ENOI | 1 | 27 | UNKN | Inspected Unknown | N | Storm | -90.0759 | 29.9563 | NP | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Other | DLIN | B | Council District B | Jay Banks | 70112 | 6
2020 | 7 | 2020 | 1332688125 | Yes | ORLEANS | FAIR | 130 | 2020-06-08 | 910 | TFUS | 61621 | 38708466353 | 1916 | ENOI | 1 | 7 | EARM | Equipment Failure - Crossarm | N | broken crossarms and downed secondary | -90.1112 | 29.9438 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 6
2020 | 124 | 2020 | 1333125835 | Yes | EAST ORLEANS | FAIR | 130 | 2020-06-16 | 16120 | LFUS | 17971 | 4163749296 | 1001 | ENOI | 6 | 124 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | Contractor in the past put switch riser on C phase instead of B Phase like its engineered for. It has since been corrected | -90.0176 | 30.016 | NP | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 12 | 2020 | 1323222467 | Yes | ORLEANS | RAIN | 131 | 2020-01-26 | 1572 | TFUS | 18346 | 38366491158 | 409 | ENOI | 1 | 12 | AOTH | Animal - Other (Describe in Remarks Field) | N | bird droppings on top tformer cleaned off the droppings tformer refused good everyone back in lights | -90.1211 | 30.0119 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 1 | 2020 | 1323479576 | Yes | EAST ORLEANS | FAIR | 131 | 2020-02-03 | 131 | TFUS | 1177611 | 4066949720 | 508 | ENOI | 6 | 1 | UNKN | Inspected Unknown | N | fuse blown on a phase | -90.0482 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70148 | 2
2020 | 37 | 2020 | 1330693066 | Yes | EAST ORLEANS | FAIR | 131 | 2020-05-15 | 4847 | LFUS | 26048 | 4353050960 | 2217 | ENOI | 6 | 37 | ASQL | Animal - Squirrel | N | Had squirrels at the base of the pole. Inspected line and energized main lateral. Also had to pick up had to pick up several spans of down service wire. Follow up needed. | -89.9574 | 30.061 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 7 | 2020 | 1325957496 | Yes | ORLEANS | FAIR | 132 | 2020-03-28 | 924 | TFUS | 617927 | 39144457916 | 1922 | ENOI | 1 | 7 | ASQL | Animal - Squirrel | N | refused due to squirel | -90.0978 | 29.9203 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 96 | 2020 | 1326694368 | Yes | ORLEANS | THDR | 132 | 2020-04-09 | 12672 | LFUS | F05614 | 39978464632 | 2137 | ENOI | 1 | 96 | LGHT | Lightning | N | teken out by weather refused ok | -90.0713 | 29.9386 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 58 | 2020 | 1330693033 | Yes | EAST ORLEANS | FAIR | 132 | 2020-05-15 | 7656 | LFUS | 24738 | 4346351051 | 2223 | ENOI | 6 | 58 | ASQL | Animal - Squirrel | N | Had squirrels at the base of the pole. Inspected line and energized main lateral. Also had to pick up had to pick up several spans of down service wire. Follow | -89.9595 | 30.0636 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 3 | 2020 | 1322474174 | Yes | ALGIERS ELEC ONLY | RAIN | 133 | 2020-01-12 | 399 | TFUS | BY174123 | 4405545113 | W1715 | ENOI | 81 | 3 | EFSW | Equipment Failure - Fuse Switch | N | top riser on switch burnt in clear made repairs cust back in lights jthom15 | -89.943 | 29.9001 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 8 | 2020 | 1324142737 | Yes | ORLEANS | FAIR | 133 | 2020-02-19 | 1064 | TFUS | 21729 | 38502489222 | 410 | ENOI | 1 | 8 | EMER | Emergency Switching | N | Out for safety of crew to replace pole | -90.117 | 30.0065 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Emergency Switching | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 116 | 2020 | 1324305126 | Yes | ALGIERS ELEC ONLY | WIND | 133 | 2020-02-20 | 15428 | LFUS | 34312 | 4265245351 | W1712 | ENOI | 81 | 116 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | hot line clamp burnt off stirrup, replaced and repaired, cust lights restored | -89.9868 | 29.9072 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 2
2020 | 13 | 2020 | 1325095835 | Yes | EAST ORLEANS | FAIR | 133 | 2020-03-05 | 1729 | TFUS | 26061 | 40975490857 | 501 | ENOI | 6 | 13 | EARM | Equipment Failure - Crossarm | N | RELI WORK | -90.0388 | 30.0103 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 7 | 2020 | 1332578227 | Yes | ORLEANS | FAIR | 133 | 2020-06-07 | 931 | XFMR | 613015 | 38896493950 | 402 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N | bad transformer crew replaced | -90.1043 | 30.0193 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 1 | 2020 | 1332889191 | Yes | EAST ORLEANS | BLNK | 133 | 2020-06-10 | 133 | TFUS | 1075630 | 4159047990 | 612 | ENOI | 6 | 1 | EPRI | Equipment Failure - Primary Conductor | N | see click | -90.0197 | 29.98 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 7 | 2020 | 1323001850 | Yes | ALGIERS ELEC ONLY | FAIR | 134 | 2020-01-19 | 938 | XFMR | 1417734 | 4264345881 | W1713 | ENOI | 81 | 7 | ETRD | Equipment Failure - Transformer | N | Nick Carroll crew (Ollie Hull, Benjamin Clayborn, Brad Barrios) | -89.9873 | 29.9217 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 745 | 2020 | 1323559097 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 | 73010 | DIS | 25215 | 4103247998 | 621 | ENOI | 6 | 745 | ECNS | Equipment Failure - Connector Sleeve | N | crew picking up wire due to a failed kearney connection | -90.0374 | 29.9803 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 198 | 2020 | 1323558838 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 | 26928 | DIS | 25301 | 4100148012 | 621 | ENOI | 6 | 198 | ECNS | Equipment Failure - Connector Sleeve | N | crew onsite making repairs: Wire burned down due to a failed kearney connection | -90.0384 | 29.9808 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 1 | 2020 | 1323548792 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 | 134 | TFUS | 1483809 | 40334487975 | 1702 | ENOI | 6 | 1 | LGHT | Lightning | N | refused transformer taken out by molding falling across switch | -90.0592 | 30.0025 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 67 | 2020 | 1326108189 | Yes | ORLEANS | FAIR | 135 | 2020-03-31 | 9045 | LFUS | 27675 | 3910546720 | 1922 | ENOI | 1 | 67 | VINE | Vine Growing into Line | N | rermoved vines, refused lateral | -90.0987 | 29.9458 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 19 | 2020 | 1329100712 | Yes | ORLEANS | FAIR | 135 | 2020-04-27 | 2565 | TFUS | 64298 | 39633458845 | 2147 | ENOI | 1 | 19 | UNKN | Inspected Unknown | N | refused ok | -90.0822 | 29.9228 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 17 | 2020 | 1321917083 | Yes | EAST ORLEANS | FAIR | 136 | 2020-01-10 | 2312 | LFUS | 23780 | 42465497468 | 1602 | ENOI | 6 | 17 | UNKN | Inspected Unknown | N | Changed **TFUS 1298164 * 17 to LFUS 1298164 * 17** --- Refused B phase in cub 167 sw 23780--Inspected unknown jvickna | -89.9915 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 14 | 2020 | 1329935577 | Yes | ORLEANS | FAIR | 136 | 2020-05-05 | 1904 | XFMR | 64432 | 39635478518 | 1705 | ENOI | 1 | 14 | ETRD | Equipment Failure - Transformer | N | bad transformer crew replaced | -90.0816 | 29.9767 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 57 | 2020 | 1333431194 | Yes | ORLEANS | THDR | 136 | 2020-06-22 | 7752 | LFUS | 33223 | 3874248657 | 408 | ENOI | 1 | 57 | VINE | Vine Growing into Line | N |  | -90.1094 | 29.9993 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 28 | 2020 | 1323400798 | Yes | EAST ORLEANS | FOGG | 137 | 2020-02-01 | 3836 | LFUS | 27891 | 4156747196 | 2346 | ENOI | 6 | 28 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons on line; refused a phase | -90.0208 | 29.9582 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 1450 | 2020 | 1325389344 | Yes | ORLEANS | FAIR | 137 | 2020-03-14 | 198650 | SBKR | 1914 | 3909545669 | 1914 | ENOI | 1 | 1450 | ECNS | Equipment Failure - Connector Sleeve | N | Fdr trip/closed & A phase was single phasing due to blown jumper that burned pri dn. @ Arrabella & Camp Sts | -90.0993 | 29.9169 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 29 | 2020 | 1329769508 | Yes | EAST ORLEANS | FAIR | 137 | 2020-05-02 | 3973 | LFUS | 21794 | 4337850707 | 2217 | ENOI | 6 | 29 | EFLK | Equipment Failure - Fuse Link | N | Refused lateral customer back on | -89.9624 | 30.054 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 18 | 2020 | 1329769335 | Yes | EAST ORLEANS | FAIR | 137 | 2020-05-02 | 2466 | LFUS | 71456 | 4335750736 | 2217 | ENOI | 6 | 18 | EFLK | Equipment Failure - Fuse Link | N | Patrolled lateral refused lateral still holding | -89.963 | 30.0548 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 167 | 2020 | 1332520121 | Yes | ORLEANS | FAIR | 138 | 2020-06-07 | 23046 | LFUS | 21369 | 3997847553 | 1712 | ENOI | 1 | 167 | VLFL | Tree On Line Outside R.O.W | N | Trees took out lateral switch refused ok | -90.0709 | 29.9686 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70116 | 6
2020 | 65 | 2020 | 1322523814 | Yes | EAST ORLEANS | FAIR | 139 | 2020-01-12 | 9035 | LFUS | 25724 | 4319150521 | 2214 | ENOI | 6 | 65 | EPRI | Equipment Failure - Primary Conductor | N | bad cable between cub 60 and vault 100 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 879 | 2020 | 1326691569 | Yes | ORLEANS | THDR | 139 | 2020-04-09 | 122181 | LFUS | F24069 | 3887447985 | 903 | ENOI | 1 | 879 | LGHT | Lightning | N | refused lateral 27794 all three phases,refused lateral at voisin and general diaz sidewalk phase,lateral 27962 refused b phase. | -90.1057 | 29.9807 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 22 | 2020 | 1326709672 | Yes | EAST ORLEANS | THDR | 139 | 2020-04-10 | 3058 | LFUS | 27716 | 43330494366 | 1611 | ENOI | 6 | 22 | EFLK | Equipment Failure - Fuse Link | N | Refused lateral sw 27716 B&C phase | -89.9643 | 30.0193 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 21 | 2020 | 1333619879 | Yes | EAST ORLEANS | THDR | 139 | 2020-06-24 | 2919 | LFUS | 28002 | 4146247489 | 2347 | ENOI | 6 | 21 | EARM | Equipment Failure - Crossarm | N |  | -90.0241 | 29.9663 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 1 | 2020 | 1323003961 | Yes | ORLEANS | FAIR | 140 | 2020-01-19 | 140 | SECO | SECONDARY | 38600465860 | 1554 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | bad jumper on secondary wire | -90.1147 | 29.9424 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Secondary Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 1 | 2020 | 1323217578 | Yes | ORLEANS | FAIR | 140 | 2020-01-26 | 140 | SERV | SERVICE | 39316462677 | 1924 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Repaired neutral at weatherhead | -90.0921 | 29.9333 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 50 | 2020 | 1323588929 | Yes | EAST ORLEANS | THDR | 140 | 2020-02-05 | 7000 | DIS | 23818 | 4352749766 | 1608 | ENOI | 6 | 50 | EMER | Emergency Switching | N | crew to replace pole | -89.9557 | 30.0225 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 144 | 2020 | 1324656883 | Yes | ORLEANS | FAIR | 140 | 2020-02-28 | 20160 | LFUS | 86144 | 3898146691 | 1925 | ENOI | 1 | 144 | EARM | Equipment Failure - Crossarm | N | broken cross arm replaced | -90.1027 | 29.9451 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 2
2020 | 8 | 2020 | 1330245404 | Yes | ORLEANS | FAIR | 140 | 2020-05-10 | 1120 | TFUS | 1349191 | 38430468283 | 2016 | ENOI | 1 | 8 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Taken out by balloon refused ok | -90.1198 | 29.949 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 45 | 2020 | 1333004464 | Yes | EAST ORLEANS | FAIR | 140 | 2020-06-13 | 6300 | LFUS | 27991 | 4125647540 | 611 | ENOI | 6 | 45 | VHCL | Vehicle | N | car hit pole; isolated pole by opening sub-lateral cut-outs RELATED TO TKT# 1333005336 (A.STEWART) | -90.0303 | 29.9676 | NP | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 20 | 2020 | 1325196222 | Yes | ALGIERS ELEC ONLY | FAIR | 141 | 2020-03-08 | 2820 | LFUS | 5587 | 4283245716 | W1714 | ENOI | 81 | 20 | ASQL | Animal - Squirrel | N | squirrel took out lateral customers are back in lights | -89.9812 | 29.9172 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 6 | 2020 | 1325216942 | Yes | ORLEANS | FAIR | 141 | 2020-03-09 | 846 | TFUS | 77907 | 38636459349 | 1927 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Outage for crane to lift generator at 1311 Jefferson Ave | -90.1138 | 29.9243 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 38 | 2020 | 1331247338 | Yes | ORLEANS | FAIR | 141 | 2020-05-23 | 5358 | LFUS | 21686 | 39696476310 | 907 | ENOI | 1 | 38 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | blown lateral C phase blown cause was balloons | -90.0796 | 29.9708 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 102 | 2020 | 1332687929 | Yes | ORLEANS | RAIN | 141 | 2020-06-08 | 14382 | DIS | 25385 | 3860746363 | 1926 | ENOI | 1 | 102 | VLGL | Tree/Limb Growing Inside R.O.W. | N | picked up down primary wireTREE CAUSED C PHASE TO BURN DOWN, TREE LIMB WAS REMOVED | -90.1144 | 29.9362 | NP | 210557 | Jan1 to Yesterday | Vegetation | Disconnect Switch | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 1 | 2020 | 1321749621 | Yes | ORLEANS | COLD | 142 | 2020-01-05 | 142 | SERV | SERVICE | 38103461220 | 2013 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed **TFUS 549754 * 10 to SERV 549754 * 10** --- bad connection at weather head abengst | -90.1306 | 29.9298 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 1 | 2020 | 1323520258 | Yes | EAST ORLEANS | FAIR | 142 | 2020-02-04 | 142 | SERV | SERVICE | 43572495525 | 1601 | ENOI | 6 | 1 | VHCL | Vehicle | N | truck hit service line..hold meter#AM11175406 removed service ..meter pan pulled off wall. RELATED TO TKT# 1323511838, 1323512749 (AKS) | -89.9566 | 30.0223 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Service Conductor | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 414 | 2020 | 1325315642 | Yes | EAST ORLEANS | FAIR | 142 | 2020-03-12 | 58788 | VFI | 27422 | 4366350629 | 2213 | ENOI | 6 | 414 | VHCL | Vehicle | N | Vehicle damaged cub. #504 at I-10 service rd & paris rd | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Vacuum Fault Interrupter | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 11 | 2020 | 1329925513 | Yes | ORLEANS | FAIR | 142 | 2020-05-05 | 1562 | TFUS | 1000489 | 39821458800 | 2147 | ENOI | 1 | 11 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0764 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 5
2020 | 12 | 2020 | 1325174086 | Yes | EAST ORLEANS | FAIR | 143 | 2020-03-07 | 1716 | TFUS | 55984 | 41031480720 | 621 | ENOI | 6 | 12 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | talked to chris boweers need to get transformer at location they have a 50 kv two blocks away feeding this house and voltage is dropping a little so gonna get a job drawn up to hang new pot and cut epoxilators in secondary | -90.0372 | 29.9826 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 23 | 2020 | 1329716247 | Yes | EAST ORLEANS | FAIR | 143 | 2020-05-01 | 3289 | LFUS | 36878F | 4369350043 | 1609 | ENOI | 6 | 23 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | serviceman cleared grass from cub 488 refused okay | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 14 | 2020 | 1330680910 | Yes | ORLEANS | THDR | 143 | 2020-05-15 | 2002 | LFUS | 38173 | 39395475907 | 1513 | ENOI | 1 | 14 | LGHT | Lightning | N | refused lateral | -90.0892 | 29.9696 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 1 | 2020 | 1332846802 | Yes | EAST ORLEANS | FAIR | 143 | 2020-06-09 | 143 | SERV | SERVICE COND | 42511502901 | 2215 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | changed connections at pole; good voltage | -89.9896 | 30.0431 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 9 | 2020 | 1324727347 | Yes | ORLEANS | FAIR | 144 | 2020-03-01 | 1296 | TFUS | 1546252 | 38696482632 | 903 | ENOI | 1 | 9 | EARR | Equipment Failure - Arrestor | N | changed arrestor | -90.1112 | 29.9884 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 8 | 2020 | 1331963304 | Yes | ORLEANS | FAIR | 144 | 2020-05-28 | 1152 | TFUS | 1342953 | 4020349326 | 503 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | crew changing out secondary arm | -90.0632 | 30.017 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 19 | 2020 | 1323119085 | Yes | EAST ORLEANS | FAIR | 145 | 2020-01-22 | 2755 | LFUS | 25651 | 4338850670 | 2214 | ENOI | 6 | 19 | EELB | Equipment Failure - Elbow | N | bad ebow crew chad.. | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 8 | 2020 | 1326568665 | Yes | EAST ORLEANS | FAIR | 145 | 2020-04-09 | 1160 | LFUS | 38442 | 4205447637 | 2346 | ENOI | 6 | 8 | EPOL | Equipment Failure - Pole | N | customers back on | -90.005 | 29.9702 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 12 | 2020 | 1330901890 | Yes | EAST ORLEANS | FAIR | 145 | 2020-05-18 | 1740 | TFUS | 1365684 | 40615480141 | 613 | ENOI | 6 | 12 | EARM | Equipment Failure - Crossarm | N | changed secondary arm | -90.0505 | 29.9811 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 5
2020 | 76 | 2020 | 1332042762 | Yes | ORLEANS | FAIR | 145 | 2020-05-30 | 11020 | LFUS | 27749 | 3881148017 | 2011 | ENOI | 1 | 76 | EARR | Equipment Failure - Arrestor | N | Arrestor, replaced | -90.1073 | 29.9816 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 50 | 2020 | 1331565281 | Yes | EAST ORLEANS | THDR | 146 | 2020-05-26 | 7300 | LFUS | 68289 | 40680483837 | 1708 | ENOI | 6 | 50 | LGHT | Lightning | N | weather | -90.0482 | 29.9912 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 12 | 2020 | 1332556343 | Yes | ORLEANS | THDR | 146 | 2020-06-07 | 1752 | TFUS | 1046933 | 40201493395 | 503 | ENOI | 1 | 12 | CORR | Corrosion | N |  | -90.0632 | 30.0174 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 1 | 2020 | 1333166463 | Yes | ORLEANS | FAIR | 146 | 2020-06-17 | 146 | TFUS | 1305459 | 38300465286 | 2014 | ENOI | 1 | 1 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1241 | 29.9408 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 76 | 2020 | 1322200807 | Yes | ORLEANS | THDR | 147 | 2020-01-11 | 11172 | LFUS | 27822 | 3801346713 | B0527 | ENOI | 1 | 76 | VLFL | Tree On Line Outside R.O.W | N | crew repaired shield wire damaged by tree | -90.1331 | 29.946 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 1 | 2020 | 1323248173 | Yes | ORLEANS | FAIR | 147 | 2020-01-27 | 147 | SERV | SERVICE | 39402478092 | 912 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | spliced service and made new connections at weatherhead | -90.0889 | 29.9758 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 4 | 2020 | 1326113204 | Yes | EAST ORLEANS | FAIR | 147 | 2020-03-31 | 588 | TFUS | 72871 | 42018475443 | 2346 | ENOI | 6 | 4 | EFSW | Equipment Failure - Fuse Switch | N | replaced transformer switch, customer back on: Flashover caused feeder to trip/close | -90.0062 | 29.9676 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 1 | 2020 | 1333572692 | Yes | EAST ORLEANS | THDR | 147 | 2020-06-23 | 147 | SERV | METER | 41600492214 | 1010 | ENOI | 6 | 1 | MTEX | Meter Exchange | N | changed meter | -90.019 | 30.0139 | NP | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 1 | 2020 | 1323640712 | Yes | EAST ORLEANS | WIND | 148 | 2020-02-06 | 148 | SERV | SERVICE | 41140473283 | 2347 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Had to replace bad hot leg on the pole. Back in lights. Will need a crew to cut limbs off of a palm tree. The branches are brushing against the primary. 2068575 | -90.0342 | 29.9619 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 12 | 2020 | 1326817592 | Yes | ORLEANS | FAIR | 148 | 2020-04-11 | 1776 | TFUS | 28686 | 38486470894 | 2015 | ENOI | 1 | 12 | AOTH | Animal - Other (Describe in Remarks Field) | N | crow | -90.1181 | 29.9561 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 4
2020 | 105 | 2020 | 1329512455 | Yes | EAST ORLEANS | THDR | 148 | 2020-04-29 | 15540 | LFUS | 32139 | 4098847474 | 622 | ENOI | 6 | 105 | SCHD | Scheduled Interruption | N | crew is onsite making repairs | -90.0389 | 29.9661 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 66 | 2020 | 1330666974 | Yes | EAST ORLEANS | THDR | 148 | 2020-05-15 | 9768 | LFUS | 27850 | 4092947726 | 622 | ENOI | 6 | 66 | LGHT | Lightning | N | weather, back in | -90.0407 | 29.973 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70117 | 5
2020 | 6 | 2020 | 1333237263 | Yes | EAST ORLEANS | FAIR | 148 | 2020-06-18 | 888 | XFMR | 19087 | 41572499268 | 2212 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N |  | -90.0196 | 30.0332 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 1 | 2020 | 1325083907 | Yes | ALGIERS ELEC ONLY | THDR | 149 | 2020-03-05 | 149 | TFUS | C29425 | 4380545475 | W1715 | ENOI | 81 | 1 | LGHT | Lightning | N | bad weather took out svc talk with cust svc is back on | -89.9503 | 29.9102 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 82 | 2020 | 1325394070 | Yes | ORLEANS | FAIR | 149 | 2020-03-14 | 12218 | DIS | 23638 | 3852145850 | 1914 | ENOI | 1 | 82 | ECNS | Equipment Failure - Connector Sleeve | N | jumper burned up and phase on ground | -90.1174 | 29.9222 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 35 | 2020 | 1329100216 | Yes | ORLEANS | FAIR | 149 | 2020-04-27 | 5215 | LFUS | 37696 | 3962045874 | 1911 | ENOI | 1 | 35 | UNKN | Inspected Unknown | N | refused ok | -90.0828 | 29.9224 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 42 | 2020 | 1333933077 | Yes | ORLEANS | FAIR | 149 | 2020-06-27 | 6258 | OPEN | 3947547564 | 3947547564 | 907 | ENOI | 1 | 42 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0867 | 29.9689 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Open | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70119 | 6
2020 | 7 | 2020 | 1325174097 | Yes | ALGIERS ELEC ONLY | FAIR | 150 | 2020-03-07 | 1050 | TFUS | BY88991 | 4215745928 | W1726 | ENOI | 81 | 7 | ASQL | Animal - Squirrel | N | squirrel took out transformer refuse customer back in lights | -90.0023 | 29.9231 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 1 | 2020 | 1326989627 | Yes | EAST ORLEANS | WIND | 150 | 2020-04-12 | 150 | TFUS | 1336630 | 4107349839 | 1001 | ENOI | 6 | 1 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | repaiired brace..refused a phase.. | -90.0353 | 30.0308 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 19 | 2020 | 1329244026 | Yes | EAST ORLEANS | THDR | 150 | 2020-04-28 | 2850 | LFUS | 27222 | 4250450158 | 2211 | ENOI | 6 | 19 | EELB | Equipment Failure - Elbow | N | replaced elbow | -89.9902 | 30.0392 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 29 | 2020 | 1330015752 | Yes | ORLEANS | FAIR | 150 | 2020-05-07 | 4350 | LFUS | 27933 | 4002247569 | 1712 | ENOI | 1 | 29 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons were tangled in b and c phase causing the lat fuse to blow. balloons removed and fuses replaced HW | -90.0693 | 29.9688 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 23 | 2020 | 1331406298 | Yes | EAST ORLEANS | RAIN | 150 | 2020-05-25 | 3450 | TFUS | 65808 | 40616476870 | 622 | ENOI | 6 | 23 | EFLK | Equipment Failure - Fuse Link | N | refused transformer | -90.0504 | 29.972 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 5
2020 | 64 | 2020 | 1325394344 | Yes | ORLEANS | FAIR | 151 | 2020-03-14 | 9664 | LFUS | 55660 | 3855645645 | 1927 | ENOI | 1 | 64 | EPRI | Equipment Failure - Primary Conductor | N | phase down and jumper burned | -90.1162 | 29.9165 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 205 | 2020 | 1332109656 | Yes | ORLEANS | FAIR | 151 | 2020-06-01 | 30955 | LFUS | 97107 | 4016948726 | 1704 | ENOI | 1 | 205 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | lot of mylar ballons took out lateral, sub lateral and tfuse; cleared balloons and refused | -90.0642 | 30.0006 | NP | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 11 | 2020 | 1324618796 | Yes | EAST ORLEANS | FAIR | 152 | 2020-02-27 | 1672 | TFUS | 60528 | 41062476942 | 611 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0363 | 29.972 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 82 | 2020 | 1326137283 | Yes | ORLEANS | WIND | 152 | 2020-03-31 | 12464 | LFUS | 27672 | 3968747354 | 1511 | ENOI | 1 | 82 | VLFL | Tree On Line Outside R.O.W | N | top of tree broke and fell across latrerial burning down a phase and blowing fuse on b and c phase. crew cut tree away and picked up a phase | -90.08 | 29.9631 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 4 | 2020 | 1326149381 | Yes | EAST ORLEANS | FAIR | 152 | 2020-03-31 | 608 | TFUS | 696585 | 41858470225 | 2346 | ENOI | 6 | 4 | VOHL | Overhanging Limb | N | Cut tree limbs. Need follow up | -90.0116 | 29.9534 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 165 | 2020 | 1326691948 | Yes | ORLEANS | THDR | 152 | 2020-04-09 | 25080 | LFUS | 27704 | 3847746872 | 2016 | ENOI | 1 | 165 | LGHT | Lightning | N | taken out by weather refused ok | -90.1188 | 29.9503 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 4 | 2020 | 1329995258 | Yes | ORLEANS | FAIR | 152 | 2020-05-06 | 608 | TFUS | 23082 | 38455485577 | 410 | ENOI | 1 | 4 | ASQL | Animal - Squirrel | N | Taken out by squirrel refused ok | -90.1185 | 29.9967 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 66 | 2020 | 1331283420 | Yes | ORLEANS | FAIR | 152 | 2020-05-24 | 10032 | LFUS | 21463 | 3920545882 | 1923 | ENOI | 1 | 66 | VLGL | Tree/Limb Growing Inside R.O.W. | N | limb on line C phase blown refused ok | -90.0959 | 29.923 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 872 | 2020 | 1333630661 | Yes | EAST ORLEANS | THDR | 152 | 2020-06-24 | 85816 | DIS | 25329 | 4325550890 | 2223 | ENOI | 6 | 872 | ESLV | Equipment Failure - Automatic Sleeve | N | wire down primary at branch and haynes : Possible lightning strike? | -89.9655 | 30.0597 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 47 | 2020 | 1323159950 | Yes | ORLEANS | FAIR | 153 | 2020-01-23 | 7191 | LFUS | 28009 | 3863545809 | 1913 | ENOI | 1 | 47 | SCHD | Scheduled Interruption | N | crew was out there on a schduled outage | -90.1137 | 29.9209 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 19 | 2020 | 1331835563 | Yes | EAST ORLEANS | FAIR | 153 | 2020-05-27 | 2907 | LFUS | 21216 | 4109648387 | 626 | ENOI | 6 | 19 | EOSC | Equipment Failure - Shield Conductor | N | repaired | -90.0352 | 29.991 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 974 | 2020 | 1323655936 | Yes | EAST ORLEANS | WIND | 154 | 2020-02-07 | 149996 | RCLR | 38677 | 4119947436 | 2347 | ENOI | 6 | 974 | EARM | Equipment Failure - Crossarm | N | insulator off arm at location | -90.034 | 29.9673 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 16 | 2020 | 1324017985 | Yes | ORLEANS | FAIR | 154 | 2020-02-15 | 2464 | XFMR | 1375593 | 3988249289 | 510 | ENOI | 1 | 16 | HECO | Human Error - Company (Describe in Remarks Field) | N | trans. 1375593 was out taken out by bell contractor ont on scene rclr was in | -90.0733 | 30.0162 | 19-YTD20 | 210557 | Jan1 to Yesterday | Human Error | Transformer | Human Error | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1 | 2020 | 1332012128 | Yes | EAST ORLEANS | FAIR | 154 | 2020-05-29 | 154 | SERV | SERVICE | 42119501342 | 2212 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | burnt wire in hand hole repaired | -90.0023 | 30.0389 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 1 | 2020 | 1332548001 | Yes | EAST ORLEANS | RAIN | 154 | 2020-06-07 | 154 | SERV | SERVICE | 43804496816 | 1601 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | BAD CONNECTION IN TRANSFORMER | -89.9494 | 30.0258 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 37 | 2020 | 1330703024 | Yes | EAST ORLEANS | FAIR | 155 | 2020-05-15 | 5735 | LFUS | 26048 | 4353050960 | 2217 | ENOI | 6 | 37 | EOSC | Equipment Failure - Shield Conductor | N | the shield fell into primary causing the primary dead end to come apart; made repairs and customers back in lights | -89.9574 | 30.061 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 306 | 2020 | 1323587389 | Yes | EAST ORLEANS | THDR | 156 | 2020-02-05 | 47736 | DIS | D01643 | 4356849760 | 1601 | ENOI | 6 | 306 | EMER | Emergency Switching | N | taken out for safety to replace burnt pole | -89.9557 | 30.0225 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 10 | 2020 | 1329566140 | Yes | EAST ORLEANS | THDR | 156 | 2020-04-29 | 1560 | TFUS | 61091 | 40429488201 | 1702 | ENOI | 6 | 10 | LGHT | Lightning | N | wather | -90.056 | 30.0032 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 37 | 2020 | 1324999233 | Yes | ORLEANS | RAIN | 157 | 2020-03-04 | 5809 | TFUS | 62327 | 39423465450 | 1925 | ENOI | 1 | 37 | EFSW | Equipment Failure - Fuse Switch | N | refused lfus at magnolia and first | -90.0887 | 29.9409 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 3
2020 | 2 | 2020 | 1327038835 | Yes | ORLEANS | THDR | 157 | 2020-04-12 | 314 | TFUS | 1546470 | 4013246071 | 1911 | ENOI | 1 | 2 | SLAK | Slack Conductor / Loose Connection | N | Primary and guy wire close installed spacer | -90.0664 | 29.9278 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 4 | 2020 | 1332055787 | Yes | ORLEANS | FAIR | 157 | 2020-05-31 | 628 | XFMR | 1482256 | 38319483226 | 412 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.1228 | 29.9902 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 51 | 2020 | 1323295246 | Yes | EAST ORLEANS | RAIN | 159 | 2020-01-29 | 8262 | DIS | 23316 | 4124747804 | 621 | ENOI | 6 | 51 | EARM | Equipment Failure - Crossarm | N | broke arm at disc. 25291 | -90.0308 | 29.975 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 62 | 2020 | 1332522083 | Yes | ORLEANS | FAIR | 159 | 2020-06-07 | 9858 | LFUS | 21184 | 3802346703 | B0527 | ENOI | 1 | 62 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Tree on lateral trimmed tree | -90.1327 | 29.9458 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 62 | 2020 | 1332554335 | Yes | ORLEANS | THDR | 159 | 2020-06-07 | 9858 | LFUS | 21370 | 4003647425 | 1512 | ENOI | 1 | 62 | VOHL | Overhanging Limb | N | B phase on lateral blown do to vegitation | -90.0691 | 29.9649 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 4 | 2020 | 1328795242 | Yes | ORLEANS | FAIR | 160 | 2020-04-23 | 640 | XFMR | 56163 | 39891486338 | 1703 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N |  | -90.0732 | 29.9982 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 35 | 2020 | 1329390864 | Yes | ORLEANS | THDR | 160 | 2020-04-29 | 5600 | LFUS | 21643 | 3970248481 | 1703 | ENOI | 1 | 35 | LGHT | Lightning | N |  | -90.0793 | 29.9941 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 16 | 2020 | 1329386395 | Yes | EAST ORLEANS | THDR | 160 | 2020-04-29 | 2560 | TFUS | 1522654 | 42381492895 | 1607 | ENOI | 6 | 16 | VLFL | Tree On Line Outside R.O.W | N | Service man MJackson fixed hot leg on pole fix service to the house and refused transfomer. Due to ploe rocked when tree fell | -89.9942 | 30.0156 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 12 | 2020 | 1330225085 | Yes | ORLEANS | FAIR | 160 | 2020-05-10 | 1920 | TFUS | 61865 | 39010464161 | 1925 | ENOI | 1 | 12 | ASQL | Animal - Squirrel | N | squirrel got across top side of xfmr cleared squirrel refused xfmr | -90.1019 | 29.9376 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 126 | 2020 | 1321765323 | Yes | EAST ORLEANS | FAIR | 161 | 2020-01-06 | 14154 | SWIT | 25111 | 4246449716 | 1602 | ENOI | 6 | 126 | ESWC | Switching Cabinet | N | Crew replacing bad switching cabinet | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 42 | 2020 | 1329427605 | Yes | ORLEANS | THDR | 161 | 2020-04-29 | 6762 | LFUS | 36644 | 4028748693 | 1708 | ENOI | 1 | 42 | LGHT | Lightning | N | 1 span #6 primary down - crew to pick up | -90.0607 | 29.9999 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 128 | 2020 | 1330727105 | Yes | EAST ORLEANS | FAIR | 161 | 2020-05-15 | 20608 | LFUS | 37121 | 4082247647 | 622 | ENOI | 6 | 128 | EPOL | Equipment Failure - Pole | N | crew replaced pole, customers back on | -90.044 | 29.9708 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 5
2020 | 1 | 2020 | 1330948760 | Yes | ORLEANS | FAIR | 161 | 2020-05-19 | 161 | SERV | METER | 38629461970 | 1926 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | had to change out meter | -90.1139 | 29.9317 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 162 | 2020 | 1323291398 | Yes | EAST ORLEANS | RAIN | 162 | 2020-01-29 | 26244 | RCLR | 23282 | 4122747950 | 621 | ENOI | 6 | 162 | EARM | Equipment Failure - Crossarm | N | broke crossarm at disc. 25291 | -90.0313 | 29.979 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 9 | 2020 | 1323561274 | Yes | EAST ORLEANS | THDR | 162 | 2020-02-05 | 1458 | TFUS | 73957 | 41821479083 | 612 | ENOI | 6 | 9 | LGHT | Lightning | N | weather | -90.0125 | 29.9777 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 22 | 2020 | 1326841490 | Yes | ORLEANS | FAIR | 162 | 2020-04-11 | 3564 | TFUS | 61864 | 39252460479 | 1924 | ENOI | 1 | 22 | EPOL | Equipment Failure - Pole | N | crew made repairs | -90.0942 | 29.9273 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 6 | 2020 | 1328795239 | Yes | ORLEANS | FAIR | 162 | 2020-04-23 | 972 | XFMR | 56611 | 39891486118 | 1703 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N |  | -90.0736 | 29.9976 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 24 | 2020 | 1330269146 | Yes | EAST ORLEANS | FAIR | 162 | 2020-05-11 | 3888 | LFUS | 17838 | 4086349242 | 505 | ENOI | 6 | 24 | ASQL | Animal - Squirrel | N | Refused B phase on lateral 17838 and transformer fuse by 4225 Mithra | -90.0422 | 30.0145 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 69 | 2020 | 1333120481 | Yes | ORLEANS | FAIR | 162 | 2020-06-16 | 11178 | LFUS | 21484 | 3923146070 | 1924 | ENOI | 1 | 69 | EFSW | Equipment Failure - Fuse Switch | N | Replaced bad switch | -90.095 | 29.928 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 48 | 2020 | 1333583790 | Yes | ORLEANS | THDR | 162 | 2020-06-23 | 7776 | LFUS | 28068 | 3960648669 | 1703 | ENOI | 1 | 48 | LGHT | Lightning | N | refused | -90.0821 | 29.9993 | NP | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 12 | 2020 | 1323710068 | Yes | ORLEANS | FAIR | 163 | 2020-02-08 | 1956 | TFUS | 59131 | 39328458518 | 1923 | ENOI | 1 | 12 | ECON | Equipment Failure - Connector / Sleeve | N | there is a lead on the transformer heating up will return after hours to replace lead. per 310 | -90.092 | 29.9219 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 26 | 2020 | 1325141261 | Yes | EAST ORLEANS | FAIR | 163 | 2020-03-06 | 4238 | LFUS | 17532 | 4097349099 | 501 | ENOI | 6 | 26 | SCHD | Scheduled Interruption | N | Crew On Site Working | -90.0389 | 30.0107 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 4 | 2020 | 1332513277 | Yes | ORLEANS | FAIR | 163 | 2020-06-06 | 652 | TFUS | 63605 | 39128467547 | 2021 | ENOI | 1 | 4 | ECNS | Equipment Failure - Connector Sleeve | N | Transformer riser came off. Replaced ok | -90.0978 | 29.9469 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 7 | 2020 | 1334126447 | Yes | EAST ORLEANS | FAIR | 163 | 2020-06-30 | 1141 | TFUS | 62245 | 42974505373 | 2215 | ENOI | 6 | 7 | FOBJ | Foreign Objects (Describe in Remarks Field) | N |  | -89.9752 | 30.0497 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 15 | 2020 | 1325563441 | Yes | ORLEANS | FAIR | 164 | 2020-03-19 | 2460 | SUBN | 1510 | 3951746984 | 1510 | ENOI | 1 | 15 | EPRI | Equipment Failure - Primary Conductor | N | primary cable faiure on 1510 breaker didnt relay out causing master to open up | -90.0856 | 29.953 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 3
2020 | 31 | 2020 | 1325563182 | NO | ORLEANS | FAIR | 164 | 2020-03-19 | 5084 | SUBN | 1543 | 3950646993 | 1543 | ENOI | 1 | 31 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0859 | 29.9532 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | B | Council District B | Jay Banks | 70113 | 3
2020 | 9 | 2020 | 1325564822 | NO | ORLEANS | FAIR | 164 | 2020-03-19 | 1476 | SUBN | 1542 | 3950746992 | 1542 | ENOI | 1 | 9 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0859 | 29.9532 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | B | Council District B | Jay Banks | 70113 | 3
2020 | 2 | 2020 | 1325563358 | NO | ORLEANS | FAIR | 164 | 2020-03-19 | 328 | SUBN | 1509 | 3951846983 | 1509 | ENOI | 1 | 2 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0855 | 29.953 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | B | Council District B | Jay Banks | 70113 | 3
2020 | 1 | 2020 | 1325563310 | NO | ORLEANS | FAIR | 164 | 2020-03-19 | 164 | SUBN | 1515 | 3952146981 | 1515 | ENOI | 1 | 1 | BKRO | Breaker - Oil | N | Trip coil on 1510 breaker failed to clear fault causing master to open up | -90.0855 | 29.9529 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation | Equipment Failure | TRANS | B | Council District B | Jay Banks | 70113 | 3
2020 | 1 | 2020 | 1325783682 | Yes | EAST ORLEANS | FAIR | 164 | 2020-03-25 | 164 | XFMR | 1239193 | 4142249180 | 1010 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | crew changed out bad pot | -90.0245 | 30.0128 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 3
2020 | 15 | 2020 | 1323070035 | Yes | ALGIERS ELEC ONLY | FAIR | 165 | 2020-01-21 | 2475 | TFUS | 1203436 | 4255145618 | W1714 | ENOI | 81 | 15 | UNKN | Inspected Unknown | N |  | -89.9903 | 29.9145 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 55 | 2020 | 1324520081 | Yes | EAST ORLEANS | FAIR | 165 | 2020-02-26 | 9075 | LFUS | 21423 | 4262649350 | 1604 | ENOI | 6 | 55 | EFSW | Equipment Failure - Fuse Switch | N | repared riser and switch, customer back in | -89.9863 | 30.0172 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1 | 2020 | 1325740262 | Yes | ORLEANS | FAIR | 165 | 2020-03-24 | 165 | TFUS | 1413402 | 39529481986 | 1705 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | tops side riser on lateral switch brokerepaired riser and changed c phase switch | -90.0848 | 29.9864 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 3
2020 | 23 | 2020 | 1331116716 | Yes | EAST ORLEANS | FAIR | 165 | 2020-05-22 | 3795 | TFUS | 80377 | 42895502009 | 2216 | ENOI | 6 | 23 | ESWC | Switching Cabinet | N | back on | -89.9775 | 30.0405 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 12 | 2020 | 1333943636 | Yes | EAST ORLEANS | FAIR | 165 | 2020-06-27 | 1980 | TFUS | 1468356 | 40718480225 | 613 | ENOI | 6 | 12 | ESEC | Secondary/Service Conductor | N |  | -90.0472 | 29.9814 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 198 | 2020 | 1323563948 | Yes | EAST ORLEANS | THDR | 166 | 2020-02-05 | 32868 | DIS | 25215 | 4103247998 | 611 | ENOI | 6 | 198 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up wire | -90.0374 | 29.9803 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 38 | 2020 | 1329433498 | Yes | ORLEANS | THDR | 166 | 2020-04-29 | 6308 | LFUS | 21572 | 3881948253 | 903 | ENOI | 1 | 38 | LGHT | Lightning | N | refused b phase taken out by lightning | -90.1071 | 29.9879 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 661 | 2020 | 1325566005 | Yes | EAST ORLEANS | FAIR | 167 | 2020-03-19 | 110387 | VFI | 27120 | 4243049745 | 1610 | ENOI | 6 | 661 | EPRI | Equipment Failure - Primary Conductor | N | primary ug cable fail | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 100 | 2020 | 1326691444 | Yes | ORLEANS | THDR | 167 | 2020-04-09 | 16700 | LFUS | 17525 | 3836348870 | 410 | ENOI | 1 | 100 | LGHT | Lightning | N | refused ok taken out by weather | -90.1214 | 30.0051 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 64 | 2020 | 1329433580 | Yes | ORLEANS | THDR | 167 | 2020-04-29 | 10688 | LFUS | 27794 | 3880948210 | 903 | ENOI | 1 | 64 | LGHT | Lightning | N | refused a phase taken out by lightning | -90.1073 | 29.987 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 15 | 2020 | 1331496483 | Yes | ORLEANS | THDR | 167 | 2020-05-26 | 2505 | TFUS | 29345 | 39798487477 | 1704 | ENOI | 1 | 15 | EARM | Equipment Failure - Crossarm | N | Changed broken feeder arm | -90.0759 | 30.0014 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 2 | 2020 | 1323550570 | Yes | ORLEANS | THDR | 168 | 2020-02-05 | 336 | TFUS | 29325 | 39377470287 | 1553 | ENOI | 1 | 2 | LGHT | Lightning | N | weather | -90.0899 | 29.9543 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70113 | 2
2020 | 159 | 2020 | 1330498884 | Yes | EAST ORLEANS | FAIR | 169 | 2020-05-13 | 26871 | LFUS | 26296 | 4381351016 | 2213 | ENOI | 6 | 159 | EPRI | Equipment Failure - Primary Conductor | N | bad cable form cub 388 to 569 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 12 | 2020 | 1333933704 | Yes | ORLEANS | FAIR | 169 | 2020-06-27 | 2028 | LFUS | L21373 | 40070476003 | 1712 | ENOI | 1 | 12 | EFLK | Equipment Failure - Fuse Link | N | fuse blew on later and caused jumper to burn up on xfmr | -90.0679 | 29.9699 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 9 | 2020 | 1330689839 | Yes | ORLEANS | FAIR | 170 | 2020-05-15 | 1530 | TFUS | 530324 | 3839845814 | 1914 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1213 | 29.9211 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 85 | 2020 | 1333481087 | Yes | ORLEANS | FAIR | 170 | 2020-06-22 | 14450 | LFUS | 27623 | 3826946524 | 2014 | ENOI | 1 | 85 | EARM | Equipment Failure - Crossarm | N | Bad crossarm at St Charles and pine crew replaced | -90.1252 | 29.9408 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 30 | 2020 | 1326693406 | Yes | ORLEANS | THDR | 171 | 2020-04-09 | 5130 | TFUS | 1401920 | 3975245866 | 2146 | ENOI | 1 | 30 | EFSW | Equipment Failure - Fuse Switch | N | repaired jumper on trans refused ok | -90.0785 | 29.9222 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 11 | 2020 | 1332554354 | Yes | ORLEANS | THDR | 171 | 2020-06-07 | 1881 | TFUS | 58719 | 39648477283 | 907 | ENOI | 1 | 11 | EFSW | Equipment Failure - Fuse Switch | N | Replaced riser on transformer switch | -90.0812 | 29.9733 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 2 | 2020 | 1332849300 | Yes | EAST ORLEANS | FAIR | 171 | 2020-06-09 | 342 | XFMR | 1125301 | 4355849783 | 1601 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N | crew changed out submersible transformer | -89.9569 | 30.0286 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 1 | 2020 | 1326182998 | Yes | EAST ORLEANS | FAIR | 172 | 2020-04-01 | 172 | SERV | METER | 40674486532 | 1710 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N | AMI meter has a defect, installed new meter 8197302 sn89900430 reading 00000 | -90.0484 | 29.9986 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 2 | 2020 | 1323217943 | Yes | EAST ORLEANS | FAIR | 173 | 2020-01-26 | 346 | TFUS | 32086 | 44464496384 | 1601 | ENOI | 6 | 2 | ASQL | Animal - Squirrel | N | squirrel took out transformer feeding building refused transfomre got great voltage now no one is here its a commercial customer closed today | -89.9283 | 30.0244 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 1 | 2020 | 1332281834 | Yes | EAST ORLEANS | FAIR | 173 | 2020-06-04 | 173 | SERV | SERVICE | 00000000000 | 611 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N | Replaced missing meter customer back in lights |  |  | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 5 | 2020 | 1329930285 | Yes | ORLEANS | FAIR | 174 | 2020-05-05 | 870 | XFMR | 1596406 | 3858348778 | 407 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | changed bad xfmr | -90.1146 | 30.0027 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 83 | 2020 | 1331259716 | Yes | ORLEANS | THDR | 174 | 2020-05-23 | 14442 | LFUS | 21366 | 4001347443 | 1512 | ENOI | 1 | 83 | EARM | Equipment Failure - Crossarm | N | broken x arm | -90.0698 | 29.9654 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70116 | 5
2020 | 14 | 2020 | 1332522095 | Yes | EAST ORLEANS | FAIR | 174 | 2020-06-07 | 2436 | LFUS | 21258 | 4189950117 | 2212 | ENOI | 6 | 14 | VLFL | Tree On Line Outside R.O.W | N | removed and refused | -90.0092 | 30.0385 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 1 | 2020 | 1323087626 | Yes | EAST ORLEANS | FAIR | 175 | 2020-01-21 | 175 | TFUS | 65841 | 46077507365 | 1204 | ENOI | 6 | 1 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.8769 | 30.054 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 14 | 2020 | 1329560681 | Yes | ORLEANS | THDR | 175 | 2020-04-29 | 2450 | TFUS | 1343359 | 39217462742 | 1925 | ENOI | 1 | 14 | LGHT | Lightning | N | weather | -90.0954 | 29.9336 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 11 | 2020 | 1326701516 | Yes | EAST ORLEANS | THDR | 176 | 2020-04-10 | 1936 | TFUS | 68407 | 42375493507 | 1607 | ENOI | 6 | 11 | EFSW | Equipment Failure - Fuse Switch | N | Wire broke on top of switch repaired | -89.9943 | 30.0172 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 12 | 2020 | 1327021461 | Yes | ORLEANS | WIND | 176 | 2020-04-12 | 2112 | TFUS | 55737 | 40223487314 | 1704 | ENOI | 1 | 12 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Taken out by tree repaired | -90.0627 | 30.0007 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 60 | 2020 | 1330155962 | Yes | ORLEANS | THDR | 176 | 2020-05-08 | 10560 | LFUS | 37784 | 3981748046 | 1709 | ENOI | 1 | 60 | EARM | Equipment Failure - Crossarm | N | REPAIRED CROSSARM | -90.0757 | 29.9822 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 5
2020 | 91 | 2020 | 1332778700 | Yes | EAST ORLEANS | FAIR | 177 | 2020-06-09 | 16107 | TFUS | 507029 | 41783501450 | 2212 | ENOI | 6 | 91 | EFLK | Equipment Failure - Fuse Link | N | refused lateral on pole and cubical a phase - lateral fuse not predictable, can't get customer ct | -90.0131 | 30.0393 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 124 | 2020 | 1328286127 | Yes | ORLEANS | THDR | 179 | 2020-04-18 | 22196 | LFUS | 27615 | 3972747795 | 615 | ENOI | 1 | 124 | EARM | Equipment Failure - Crossarm | N | changed crossarm | -90.0786 | 29.9753 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 35 | 2020 | 1332910098 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-10 | 6265 | LFUS | 37102 | 4308850547 | 2215 | ENOI | 6 | 35 | EFLK | Equipment Failure - Fuse Link | N | refused | -89.9715 | 30.0497 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 1 | 2020 | 1332984099 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-12 | 179 | TFUS | 1272291 | 41915477388 | 2347 | ENOI | 6 | 1 | ASQL | Animal - Squirrel | N | Refused C phase transformer taken out by squirrel | -90.0095 | 29.9729 | NP | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 9 | 2020 | 1333011431 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-13 | 1611 | LFUS | 57582 | 4198347797 | 2325 | ENOI | 6 | 9 | VINE | Vine Growing into Line | N | cleared vines refused ok | -90.0072 | 29.9745 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 15 | 2020 | 1333708534 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-25 | 2685 | XFMR | 69605 | 40694489268 | 1702 | ENOI | 6 | 15 | ETRD | Equipment Failure - Transformer | N | bad transformer lid blown off oil on ground call ervironmental called crew Chad Gould | -90.0476 | 30.0061 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 376 | 2020 | 1333929364 | Yes | EAST ORLEANS | FAIR | 179 | 2020-06-27 | 67304 | LFUS | 27045 | 4279549796 | 2211 | ENOI | 6 | 376 | AOTH | Animal - Other (Describe in Remarks Field) | N | closed vfi s 26140 & 26135; crew still investigating cause of outage: Rat got into cub 8 | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 76 | 2020 | 1331065683 | Yes | EAST ORLEANS | FAIR | 180 | 2020-05-21 | 13680 | LFUS | 21750 | 4237949491 | 1604 | ENOI | 6 | 76 | UNKN | Inspected Unknown | N | refused lateral; lights back on | -89.9943 | 30.021 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 914 | 2020 | 1328243630 | Yes | ORLEANS | THDR | 181 | 2020-04-18 | 165434 | RCLR | 24210 | 3918445893 | 1923 | ENOI | 1 | 914 | EARM | Equipment Failure - Crossarm | N | broken cross arm | -90.0965 | 29.9232 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 119 | 2020 | 1329824949 | Yes | ORLEANS | FAIR | 181 | 2020-05-04 | 21539 | LFUS | 21073 | 3876146762 | 1916 | ENOI | 1 | 119 | EMER | Emergency Switching | N | crew replacing cross arm on S Rocheblave | -90.1095 | 29.9473 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Emergency Switching | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 5
2020 | 114 | 2020 | 1332793735 | Yes | ORLEANS | FAIR | 181 | 2020-06-09 | 20634 | LFUS | 76997 | 39933478674 | 907 | ENOI | 1 | 114 | SCHD | Scheduled Interruption | N |  | -90.0722 | 29.9771 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 6 | 2020 | 1333764141 | Yes | ORLEANS | FAIR | 181 | 2020-06-25 | 1086 | XFMR | 698206 | 40011464683 | 2137 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | crew replacing pot | -90.07 | 29.9387 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 6
2020 | 24 | 2020 | 1323314806 | Yes | ORLEANS | FAIR | 182 | 2020-01-29 | 4368 | TFUS | 1533023 | 39840459058 | 2147 | ENOI | 1 | 24 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | no comments | -90.0758 | 29.9232 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 117 | 2020 | 1333309416 | Yes | EAST ORLEANS | FAIR | 182 | 2020-06-20 | 21294 | LFUS | 38367 | 4079449113 | 501 | ENOI | 6 | 117 | ASQL | Animal - Squirrel | N | w | -90.0445 | 30.011 | NP | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 18 | 2020 | 1325327776 | Yes | ORLEANS | FAIR | 183 | 2020-03-12 | 3294 | TFUS | 1001093 | 39848461464 | 2132 | ENOI | 1 | 18 | VLGL | Tree/Limb Growing Inside R.O.W. | N | need vegetation ticket made for tree under transformer bank, tested, refused ok KC | -90.0755 | 29.9298 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 96 | 2020 | 1324527282 | Yes | ORLEANS | FAIR | 184 | 2020-02-26 | 17664 | OPEN | 3908445887 | 3908445887 | 1917 | ENOI | 1 | 96 | SCHD | Scheduled Interruption | N | Contract crew replacing rotten pole | -90.0996 | 29.9229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Open | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 6 | 2020 | 1324616559 | Yes | EAST ORLEANS | FAIR | 184 | 2020-02-27 | 1104 | TFUS | 1417774 | 41010475194 | 611 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0382 | 29.9672 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 3 | 2020 | 1324727607 | Yes | ORLEANS | FAIR | 184 | 2020-03-01 | 552 | LFUS | 22199 | 4008346242 | 2142 | ENOI | 1 | 3 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.068 | 29.9324 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 5 | 2020 | 1325277031 | Yes | EAST ORLEANS | FAIR | 184 | 2020-03-10 | 920 | TFUS | 75064 | 41670475701 | 2325 | ENOI | 6 | 5 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused trans..installed animal guard | -90.0175 | 29.9685 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 102 | 2020 | 1330445255 | Yes | ORLEANS | FAIR | 184 | 2020-05-13 | 18768 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 102 | SCHD | Scheduled Interruption | N | Outage to replace cross arm | -90.0879 | 29.975 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 23 | 2020 | 1332494416 | Yes | EAST ORLEANS | FAIR | 187 | 2020-06-06 | 4301 | LFUS | 37022 | 4107847270 | 2347 | ENOI | 6 | 23 | EARM | Equipment Failure - Crossarm | N | crew repaired broke crossarm | -90.0359 | 29.9604 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 7 | 2020 | 1325289126 | Yes | EAST ORLEANS | FAIR | 188 | 2020-03-11 | 1316 | XFMR | 20698 | 40362493030 | 506 | ENOI | 6 | 7 | ETRD | Equipment Failure - Transformer | N | crew to change | -90.0582 | 30.0164 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 243 | 2020 | 1325616344 | Yes | ORLEANS | FAIR | 188 | 2020-03-21 | 45684 | DIS | 23445 | 3898647498 | 903 | ENOI | 1 | 243 | EINS | Equipment Failure - Insulator | N | Open for safety to pickup phase that burned down from failed oinsulator at D"hemecourt & Cortez | -90.1022 | 29.9673 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 3
2020 | 3 | 2020 | 1323025386 | Yes | ORLEANS | FAIR | 189 | 2020-01-20 | 567 | TFUS | 32466 | 39602493949 | 509 | ENOI | 1 | 3 | ESEC | Secondary/Service Conductor | N | transformer back in and secondary picked back up | -90.0821 | 30.0192 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 95 | 2020 | 1328242037 | Yes | ORLEANS | THDR | 189 | 2020-04-18 | 17955 | LFUS | F05614 | 39978464632 | 2137 | ENOI | 1 | 95 | EARM | Equipment Failure - Crossarm | N | crossarm brace fell on jumper. cleared and refused lateral | -90.0713 | 29.9386 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 84 | 2020 | 1328276701 | Yes | EAST ORLEANS | THDR | 189 | 2020-04-18 | 15876 | LFUS | 31589 | 40579484677 | 1710 | ENOI | 6 | 84 | LGHT | Lightning | N | found transformer and lateral switch blown at location. cust stated lightning hit pole with transformer. refused lateral and transformer. chk voltage. all lights back on, | -90.0517 | 29.9935 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 143 | 2020 | 1330576602 | Yes | EAST ORLEANS | FAIR | 189 | 2020-05-14 | 27027 | LFUS | 21614 | 4038048940 | 1702 | ENOI | 6 | 143 | EARM | Equipment Failure - Crossarm | N | crew replaced broke arm | -90.0578 | 30.0066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 66 | 2020 | 1325285495 | Yes | ORLEANS | FAIR | 190 | 2020-03-11 | 12540 | OPEN | 3971445987 | 3971445987 | 2147 | ENOI | 1 | 66 | SCHD | Scheduled Interruption | N | back to normal | -90.0797 | 29.9255 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Open | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 3
2020 | 11 | 2020 | 1326459620 | Yes | ORLEANS | FAIR | 190 | 2020-04-07 | 2090 | TFUS | 62936 | 39103468355 | 2021 | ENOI | 1 | 11 | EONE | Equipment Failure - Neutral / Shield Conductor | N | bad neutral connection on the transformer. per 310 | -90.0986 | 29.949 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 89 | 2020 | 1329232321 | Yes | ORLEANS | THDR | 190 | 2020-04-28 | 16910 | LFUS | 37943 | 3839445846 | 1914 | ENOI | 1 | 89 | VLFL | Tree On Line Outside R.O.W | N | tree on line | -90.1215 | 29.9221 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 4
2020 | 11 | 2020 | 1333165798 | Yes | EAST ORLEANS | FAIR | 190 | 2020-06-17 | 2090 | TFUS | 58868 | 41114475406 | 611 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0347 | 29.9678 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 2 | 2020 | 1333711300 | Yes | ORLEANS | FAIR | 190 | 2020-06-25 | 380 | TFUS | 66182 | 39386460688 | 2147 | ENOI | 1 | 2 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.09 | 29.928 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 67 | 2020 | 1324839571 | Yes | ORLEANS | FAIR | 191 | 2020-03-03 | 12797 | LFUS | 28115 | 3865446377 | 1927 | ENOI | 1 | 67 | EARM | Equipment Failure - Crossarm | N | changed x arms | -90.1129 | 29.9365 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 20 | 2020 | 1328876112 | Yes | ORLEANS | FAIR | 191 | 2020-04-23 | 3820 | TFUS | 498854 | 38093471229 | B0527 | ENOI | 1 | 20 | VINE | Vine Growing into Line | N | REMOVED REFUSED | -90.1305 | 29.9572 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 6 | 2020 | 1333648486 | Yes | EAST ORLEANS | THDR | 191 | 2020-06-24 | 1146 | XFMR | 74204 | 40497479460 | 613 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N |  | -90.0541 | 29.9792 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 1 | 2020 | 1323988573 | Yes | ORLEANS | FAIR | 193 | 2020-02-15 | 193 | SECO | METER | 39437478935 | 912 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | cust AMI mtr was opened AMOC doesnt work weekends and DOC doesnt have control to close mtr so changed mtr to mtr#8180313 sn-34644421 r-00000 KC | -90.0878 | 29.978 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Secondary Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 2
2020 | 66 | 2020 | 1326691664 | Yes | ORLEANS | THDR | 193 | 2020-04-09 | 12738 | LFUS | 28068 | 3960648669 | 1703 | ENOI | 1 | 66 | LGHT | Lightning | N | taken out by weather refused ok | -90.0821 | 29.9993 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 210 | 2020 | 1330349740 | Yes | EAST ORLEANS | FAIR | 193 | 2020-05-11 | 40530 | DIS | 25785 | 4140347427 | 622 | ENOI | 6 | 210 | EPRI | Equipment Failure - Primary Conductor | N | Cerw on the way to make repairs | -90.0217 | 29.9642 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 6 | 2020 | 1331039050 | Yes | ORLEANS | FAIR | 193 | 2020-05-21 | 1158 | TFUS | 69592 | 39446475774 | 1513 | ENOI | 1 | 6 | AOTH | Animal - Other (Describe in Remarks Field) | N | trasnsformer out refused ok per RBILES transformer taken out by bird | -90.0876 | 29.9694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70119 | 5
2020 | 11 | 2020 | 1333262323 | Yes | ORLEANS | FAIR | 193 | 2020-06-19 | 2123 | TFUS | 1254921 | 39399464952 | 1915 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons took lateral out cleared refused ok - lfus not in gis | -90.0896 | 29.9397 | NP | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70113 | 6
2020 | 8 | 2020 | 1324984786 | Yes | EAST ORLEANS | FAIR | 194 | 2020-03-04 | 1552 | LFUS | 27757 | 4126947853 | 621 | ENOI | 6 | 8 | EPRI | Equipment Failure - Primary Conductor | N | wire down | -90.0297 | 29.9764 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 3
2020 | 58 | 2020 | 1324464499 | Yes | EAST ORLEANS | FAIR | 195 | 2020-02-25 | 11310 | LFUS | 24738 | 4346351051 | 2223 | ENOI | 6 | 58 | VHCL | Vehicle | N | car hit pole RELATED TO AMFM 1324463382 | -89.9595 | 30.0636 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 397 | 2020 | 1328252072 | Yes | ORLEANS | THDR | 195 | 2020-04-18 | 77415 | DIS | 24403 | 3964845844 | 2147 | ENOI | 1 | 397 | EARM | Equipment Failure - Crossarm | N |  | -90.0819 | 29.9217 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 142 | 2020 | 1324538266 | Yes | ORLEANS | FAIR | 197 | 2020-02-26 | 27974 | LFUS | 27985 | 3909645896 | 1917 | ENOI | 1 | 142 | SCHD | Scheduled Interruption | N | Contract crew replacing pole at the intersection of Chestnut and Milan | -90.0993 | 29.9232 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 70 | 2020 | 1324538399 | Yes | ORLEANS | FAIR | 197 | 2020-02-26 | 13790 | LFUS | 27759 | 3909745885 | 1917 | ENOI | 1 | 70 | SCHD | Scheduled Interruption | N | Contract crew replacing pole at the intersection of Chestnut and Milan | -90.0993 | 29.9229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 62 | 2020 | 1329268983 | Yes | ORLEANS | THDR | 197 | 2020-04-28 | 12214 | LFUS | 27741 | 3918647289 | 2025 | ENOI | 1 | 62 | LGHT | Lightning | N | b phase came down; picked up and refused | -90.096 | 29.9616 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 6 | 2020 | 1333643921 | Yes | ORLEANS | THDR | 198 | 2020-06-24 | 1188 | XFMR | 57049 | 40292486217 | 1708 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | completed | -90.0605 | 29.9977 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 12 | 2020 | 1323298113 | Yes | ALGIERS ELEC ONLY | FAIR | 199 | 2020-01-29 | 2388 | TFUS | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | SCHD | Scheduled Interruption | N | CREW OUTAGE | -89.9867 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 9 | 2020 | 1324416282 | Yes | ORLEANS | FAIR | 199 | 2020-02-24 | 1791 | TFUS | 1000615 | 39768462508 | 2135 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | repairs to secondary | -90.078 | 29.9328 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 122 | 2020 | 1328258228 | Yes | ORLEANS | THDR | 199 | 2020-04-18 | 24278 | DIS | 24113 | 3942345968 | 1923 | ENOI | 1 | 122 | EMER | Emergency Switching | N | Crew on site replacing cross arms | -90.0864 | 29.9264 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 105 | 2020 | 1333887668 | Yes | ORLEANS | FAIR | 199 | 2020-06-26 | 20895 | LFUS | 21436 | 3886145950 | 1921 | ENOI | 1 | 105 | EARM | Equipment Failure - Crossarm | N | repaired | -90.1065 | 29.9247 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 18 | 2020 | 1323561267 | Yes | EAST ORLEANS | THDR | 200 | 2020-02-05 | 3600 | LFUS | 62285 | 4180447921 | 612 | ENOI | 6 | 18 | LGHT | Lightning | N |  | -90.0131 | 29.9781 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 271 | 2020 | 1332092492 | Yes | ORLEANS | FAIR | 200 | 2020-06-01 | 54200 | LFUS | 21522 | 3894446708 | 1925 | ENOI | 1 | 271 | VHCL | Vehicle | N | broke pole caused by truck picking up dumpters RELATED TO TKT#1332088960 (A.STEWART) | -90.1038 | 29.9457 | NP | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 15 | 2020 | 1323063051 | Yes | ORLEANS | FAIR | 201 | 2020-01-21 | 3015 | SWIT | V10-17 | 38818496158 | 401 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | recable job | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Switch | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70124 | 1
2020 | 105 | 2020 | 1330348208 | Yes | EAST ORLEANS | FAIR | 201 | 2020-05-11 | 21105 | DIS | 25786 | 4155947419 | 2345 | ENOI | 6 | 105 | EPRI | Equipment Failure - Primary Conductor | N | Crew on the way to make repairs | -90.0217 | 29.9642 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 53 | 2020 | 1325275264 | Yes | EAST ORLEANS | FAIR | 202 | 2020-03-10 | 10706 | LFUS | 27864 | 4079547423 | 623 | ENOI | 6 | 53 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | refused c phase..moulding on phase..clear | -90.0451 | 29.9648 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70117 | 3
2020 | 3 | 2020 | 1323198606 | Yes | EAST ORLEANS | FAIR | 203 | 2020-01-25 | 609 | TFUS | 1460718 | 40760480182 | 622 | ENOI | 6 | 3 | EARM | Equipment Failure - Crossarm | N | replaced crossarm arm on dead end pole | -90.046 | 29.9811 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 14 | 2020 | 1323899529 | Yes | ORLEANS | FAIR | 203 | 2020-02-12 | 2842 | TFUS | 72350 | 38822482342 | 903 | ENOI | 1 | 14 | ECNS | Equipment Failure - Connector Sleeve | N | picked up span of primary that fell due to the hot tap connection | -90.107 | 29.9875 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 33 | 2020 | 1330668483 | Yes | EAST ORLEANS | THDR | 203 | 2020-05-15 | 6699 | LFUS | 17848 | 4076649426 | 508 | ENOI | 6 | 33 | LGHT | Lightning | N | weather, back on | -90.0452 | 30.0198 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 72 | 2020 | 1325830344 | Yes | EAST ORLEANS | FAIR | 204 | 2020-03-25 | 14688 | LFUS | 24766 | 4440350119 | 1608 | ENOI | 6 | 72 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | "B" phase Indoor pothead in walk-in vault on Granville Dr. failed & burnt other 2 phases Isolated vlt, & restored lateral | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 103 | 2020 | 1326693120 | Yes | ORLEANS | THDR | 204 | 2020-04-09 | 21012 | LFUS | 21813 | 3928146648 | 2021 | ENOI | 1 | 103 | LGHT | Lightning | N | taken out by weather refused ok | -90.0932 | 29.9438 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 18 | 2020 | 1326832748 | Yes | ORLEANS | FAIR | 204 | 2020-04-11 | 3672 | XFMR | 1400854 | 39268479955 | 912 | ENOI | 1 | 18 | SCHD | Scheduled Interruption | N | changed out transf. | -90.0931 | 29.9809 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 222 | 2020 | 1325175289 | Yes | ORLEANS | FAIR | 205 | 2020-03-07 | 45510 | DIS | 23482 | 3876045869 | 1917 | ENOI | 1 | 222 | EMER | Emergency Switching | N | opened for safety of crew to epair broke x am for clearance | -90.1099 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 14 | 2020 | 1327097573 | Yes | EAST ORLEANS | THDR | 205 | 2020-04-12 | 2870 | TFUS | 71144 | 40620477716 | 622 | ENOI | 6 | 14 | LGHT | Lightning | N | weather refused okay | -90.0503 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 16 | 2020 | 1334100790 | Yes | ORLEANS | FAIR | 205 | 2020-06-30 | 3280 | LFUS | F05707 | 3854546260 | 1926 | ENOI | 1 | 16 | SCHD | Scheduled Interruption | N | Derek Cain 504 444 6056 (18 Rosa Parks)...jcoo12 | -90.1166 | 29.9334 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 1 | 2020 | 1326457737 | Yes | ORLEANS | FAIR | 206 | 2020-04-07 | 206 | SERV | SERVICE | 39383458105 | 1922 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | trimmed tree, changed connections at the pole per 310 | -90.0902 | 29.9208 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 16 | 2020 | 1323046635 | Yes | ORLEANS | FAIR | 208 | 2020-01-20 | 3328 | TFUS | 729472 | 38920475976 | 903 | ENOI | 1 | 16 | ECON | Equipment Failure - Connector / Sleeve | N | changed out connections at weather head. | -90.1041 | 29.9701 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 1 | 2020 | 1323653145 | Yes | EAST ORLEANS | WIND | 210 | 2020-02-06 | 210 | LFUS | 61838 | 4107349839 | 1001 | ENOI | 6 | 1 | EFSW | Equipment Failure - Fuse Switch | N | refused lateral 61838 b/c phases only customer back on | -90.0354 | 30.031 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1 | 2020 | 1327238091 | Yes | EAST ORLEANS | THDR | 210 | 2020-04-12 | 210 | SERV | SERVICE | 42713494067 | 1604 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | hot leg burned off at squeeze on open wire secondary. replaced all three connections at pole. had customer verify all lights and applicances back on. | -89.9836 | 30.0187 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 19 | 2020 | 1329397914 | Yes | EAST ORLEANS | RAIN | 210 | 2020-04-29 | 3990 | LFUS | 25651 | 4338850670 | 2214 | ENOI | 6 | 19 | EELB | Equipment Failure - Elbow | N | Replaced elbow at location CGould | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 1 | 2020 | 1330788026 | Yes | ORLEANS | FAIR | 210 | 2020-05-16 | 210 | PRIM | 3844246320 | 3844246320 | 2024 | ENOI | 1 | 1 | ASQL | Animal - Squirrel | N | squirrel took out xfmr; refused and lights back on | -90.1198 | 29.9351 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Primary Meter | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 5
2020 | 5 | 2020 | 1333646550 | Yes | ORLEANS | THDR | 210 | 2020-06-24 | 1050 | LFUS | 56819 | 3829546523 | 2014 | ENOI | 1 | 5 | VLFL | Tree On Line Outside R.O.W | N | Tree pinned down primary back energized | -90.1243 | 29.9405 | NP | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 75 | 2020 | 1321820126 | Yes | EAST ORLEANS | FAIR | 211 | 2020-01-07 | 15825 | LFUS | 27348 | 4264949768 | 1602 | ENOI | 6 | 75 | EPRI | Equipment Failure - Primary Conductor | N | bad cable from cubicle 6 to vault 1 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 16 | 2020 | 1321829805 | Yes | ORLEANS | FAIR | 211 | 2020-01-08 | 3376 | TFUS | 53182 | 38684487237 | 408 | ENOI | 1 | 16 | FOTH | Fire - Other (Describe in Remarks Field) | N | fire at location burnt wire down, transformer back in | -90.1114 | 30.0011 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 7 | 2020 | 1323232948 | Yes | ORLEANS | FAIR | 211 | 2020-01-27 | 1477 | TFUS | 59936 | 38748467302 | 1916 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1099 | 29.9463 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 1
2020 | 3 | 2020 | 1325286019 | Yes | EAST ORLEANS | FAIR | 211 | 2020-03-11 | 633 | TFUS | 1242332 | 42902506464 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | crew has an outage set up for today | -89.9774 | 30.0527 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 8 | 2020 | 1330880818 | Yes | EAST ORLEANS | FAIR | 211 | 2020-05-18 | 1688 | TFUS | 1146111 | 40338489518 | 1702 | ENOI | 6 | 8 | SCHD | Scheduled Interruption | N | crew working on pole | -90.0591 | 30.0068 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 10 | 2020 | 1331268020 | Yes | EAST ORLEANS | THDR | 211 | 2020-05-23 | 2110 | XFMR | 53581 | 41458499139 | 1010 | ENOI | 6 | 10 | ETRD | Equipment Failure - Transformer | N | crew to change bad transformer | -90.0232 | 30.033 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 75 | 2020 | 1323576846 | Yes | ORLEANS | THDR | 212 | 2020-02-05 | 15900 | LFUS | 27869 | 3847346112 | 1917 | ENOI | 1 | 75 | LGHT | Lightning | N | weather | -90.1188 | 29.9292 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 197 | 2020 | 1330667652 | Yes | ORLEANS | THDR | 212 | 2020-05-15 | 41764 | LFUS | F99218 | 4021947492 | 1712 | ENOI | 1 | 197 | LGHT | Lightning | N | refused a and c phase taken out b weather | -90.0631 | 29.9669 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | C | Council District C | Kristin Palmer | 70116 | 5
2020 | 460 | 2020 | 1323115884 | Yes | ALGIERS ELEC ONLY | FAIR | 213 | 2020-01-22 | 97980 | LFUS | 1105 | 4195645775 | W0712 | ENOI | 81 | 460 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | L1105 was blown as well as subL34242, cause balloons on switch, rc 1-22-20 | -90.009 | 29.919 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 11 | 2020 | 1323716666 | Yes | EAST ORLEANS | FAIR | 214 | 2020-02-08 | 2354 | TFUS | 1417733 | 40381486047 | 1708 | ENOI | 6 | 11 | EARR | Equipment Failure - Arrestor | N | refuse b phase ..cleared arrester | -90.0577 | 29.9973 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 4 | 2020 | 1333205602 | Yes | EAST ORLEANS | FAIR | 214 | 2020-06-17 | 856 | XFMR | 1003345 | 42188497835 | 2212 | ENOI | 6 | 4 | ETRD | Equipment Failure - Transformer | N | CHANGED TRANSFORMER | -90.0003 | 30.0292 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 1 | 2020 | 1322951627 | Yes | ALGIERS ELEC ONLY | FAIR | 215 | 2020-01-18 | 215 | SERV | METER | 4164146240 | W0725 | ENOI | 81 | 1 | MTEX | Meter Exchange | N | stolen meter, mtr change ticket to be made, rc | -90.0187 | 29.9319 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 269 | 2020 | 1323986713 | Yes | EAST ORLEANS | FAIR | 215 | 2020-02-15 | 57835 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 269 | EELB | Equipment Failure - Elbow | N | crew replaced bad elbow, customers back on now | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 52 | 2020 | 1328352970 | Yes | ORLEANS | FAIR | 215 | 2020-04-19 | 11180 | LFUS | 21569 | 3903748059 | 904 | ENOI | 1 | 52 | EARM | Equipment Failure - Crossarm | N | crossarm broke changed out lateral arm and switches | -90.1004 | 29.9827 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 172 | 2020 | 1329397017 | Yes | EAST ORLEANS | THDR | 215 | 2020-04-29 | 36980 | LFUS | 25610 | 4335750498 | 2214 | ENOI | 6 | 172 | EELB | Equipment Failure - Elbow | N | Replace elbows at location CGould | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 2 | 2020 | 1322467215 | Yes | ALGIERS ELEC ONLY | RAIN | 216 | 2020-01-12 | 432 | TFUS | BY174099 | 4417845173 | W1715 | ENOI | 81 | 2 | EFSW | Equipment Failure - Fuse Switch | N | top riser on switch burnt in the clear made repairs cust back in light jthom15 | -89.9391 | 29.9017 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 29 | 2020 | 1329133998 | Yes | EAST ORLEANS | FAIR | 216 | 2020-04-28 | 6264 | LFUS | 82569 | 4192847736 | 2347 | ENOI | 6 | 29 | ASQL | Animal - Squirrel | N | Refused c phase lat cut out customers back in | -90.009 | 29.9728 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 4
2020 | 1 | 2020 | 1330426684 | Yes | ORLEANS | FAIR | 217 | 2020-05-12 | 217 | SERV | SERVICE | 39132463733 | 1925 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | AMI meter opened remotely called amoc and turned on | -90.0981 | 29.9364 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 11 | 2020 | 1330563121 | Yes | ORLEANS | FAIR | 217 | 2020-05-14 | 2387 | TFUS | 1254921 | 39399464952 | 1915 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | replaced broken lateral switch and removed some milar baloons - lateral fuse not in gis | -90.0896 | 29.9397 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 169 | 2020 | 1331547225 | Yes | ORLEANS | THDR | 218 | 2020-05-26 | 36842 | LFUS | 21462 | 3916245912 | 1923 | ENOI | 1 | 169 | EFSW | Equipment Failure - Fuse Switch | N | crew changed switch | -90.0971 | 29.9237 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 211 | 2020 | 1323138909 | Yes | ALGIERS ELEC ONLY | THDR | 219 | 2020-01-23 | 46209 | RCLR | 33772 | 4313545406 | W1715 | ENOI | 81 | 211 | EINS | Equipment Failure - Insulator | N | BCLEME1 | -89.9719 | 29.9085 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 50 | 2020 | 1323623756 | Yes | EAST ORLEANS | FAIR | 219 | 2020-02-06 | 10950 | LFUS | 21126 | 4120947834 | 621 | ENOI | 6 | 50 | ECNS | Equipment Failure - Connector Sleeve | N | riser on switch broke, repaired, customers back on | -90.0319 | 29.9758 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 34 | 2020 | 1326708697 | Yes | EAST ORLEANS | THDR | 219 | 2020-04-09 | 7446 | LFUS | 37119 | 4089647831 | 622 | ENOI | 6 | 34 | EARM | Equipment Failure - Crossarm | N | Broken crossarm on Clouet and N. Johnson | -90.0417 | 29.9759 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 41 | 2020 | 1333689041 | Yes | EAST ORLEANS | FAIR | 219 | 2020-06-24 | 8979 | LFUS | 23024 | 4187250055 | 2212 | ENOI | 6 | 41 | EELB | Equipment Failure - Elbow | N | made up new elbow | -90.01 | 30.0367 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 11 | 2020 | 1323304450 | Yes | ORLEANS | FAIR | 220 | 2020-01-29 | 2420 | DIS | 25476 | 3861947481 | 2011 | ENOI | 1 | 11 | EMER | Emergency Switching | N | SHIELD WIRE DOWN | -90.1137 | 29.9669 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 3 | 2020 | 1333955834 | Yes | EAST ORLEANS | FAIR | 220 | 2020-06-28 | 660 | TFUS | 73813 | 41970477030 | 2347 | ENOI | 6 | 3 | VINE | Vine Growing into Line | N | cleared vines off of pole and refused pot | -90.0079 | 29.972 | NP | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 21 | 2020 | 1328352964 | Yes | ORLEANS | FAIR | 222 | 2020-04-19 | 4662 | LFUS | 21568 | 3904648072 | 904 | ENOI | 1 | 21 | EARM | Equipment Failure - Crossarm | N | Crew on the way to replace cross arms | -90.1001 | 29.9831 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 30 | 2020 | 1325942615 | Yes | EAST ORLEANS | FAIR | 224 | 2020-03-28 | 6720 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 30 | CFIM | Cable Failure in manhole | N | isolated b phase from V-15 to cub-22. identified hole in cable in submersible vault-15. | -89.9561 | 30.0595 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 1 | 2020 | 1333015636 | Yes | ORLEANS | FAIR | 225 | 2020-06-13 | 225 | SERV | METER | 38554457177 | 1913 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | meter was opened up, disc. was worked and no install was completed | -90.1164 | 29.9184 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 14 | 2020 | 1333793221 | Yes | EAST ORLEANS | THDR | 225 | 2020-06-25 | 3150 | TFUS | 52647 | 40497491301 | 502 | ENOI | 6 | 14 | LGHT | Lightning | N | weather, back on | -90.0537 | 30.0114 | NP | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 11 | 2020 | 1323088737 | Yes | EAST ORLEANS | FAIR | 226 | 2020-01-21 | 2486 | TFUS | 23813 | 40482495074 | 506 | ENOI | 6 | 11 | ECON | Equipment Failure - Connector / Sleeve | N | burnt trans lead ..replaced | -90.0541 | 30.0221 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 125 | 2020 | 1323111678 | Yes | ORLEANS | FAIR | 227 | 2020-01-22 | 28375 | LFUS | 21686 | 3971247620 | 907 | ENOI | 1 | 125 | VHCL | Vehicle | N | dump truck hit pole PID IN PROGRESS (Unable to to find info on dump truck that hit the pole) | -90.0791 | 29.9705 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 41 | 2020 | 1328276688 | Yes | ORLEANS | THDR | 227 | 2020-04-18 | 9307 | LFUS | 17789 | 3901648762 | 403 | ENOI | 1 | 41 | ETRD | Equipment Failure - Transformer | N | transformer bad took out lateral troubleshooter got lateral in and crew changed transformer | -90.1008 | 30.0021 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 43 | 2020 | 1333665571 | Yes | EAST ORLEANS | THDR | 227 | 2020-06-24 | 9761 | LFUS | 21799 | 4392951465 | 2223 | ENOI | 6 | 43 | ETRD | Equipment Failure - Transformer | N | BAD TRANSFORMERS AT BASS | -89.9445 | 30.0749 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 12 | 2020 | 1323088224 | Yes | EAST ORLEANS | FAIR | 228 | 2020-01-21 | 2736 | TFUS | 1048655 | 43916511664 | 2217 | ENOI | 6 | 12 | EABS | Equipment Failure - Air Break / Disconnect Switch | N | outage is due to crew picking up wire on curran. avon park is inside isolated portion of feeder thats under clearance | -89.945 | 30.0667 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 20 | 2020 | 1332069340 | Yes | EAST ORLEANS | FAIR | 228 | 2020-05-31 | 4560 | XFMR | 1372130 | 42791504916 | 2216 | ENOI | 6 | 20 | ETRD | Equipment Failure - Transformer | N |  | -89.981 | 30.0484 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 862 | 2020 | 1328324917 | Yes | ORLEANS | THDR | 230 | 2020-04-19 | 198260 | RCLR | 24783 | 3885346462 | 1926 | ENOI | 1 | 862 | LGHT | Lightning | N | refused | -90.1067 | 29.9388 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Recloser | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 19 | 2020 | 1331388519 | Yes | ORLEANS | RAIN | 230 | 2020-05-25 | 4370 | TFUS | 66611 | 40298485353 | 1708 | ENOI | 1 | 19 | EFSW | Equipment Failure - Fuse Switch | N | replaced bad switch at location | -90.0603 | 29.9954 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 46 | 2020 | 1332520170 | Yes | ORLEANS | RAIN | 230 | 2020-06-07 | 10580 | LFUS | 27898 | 3992248185 | 1709 | ENOI | 1 | 46 | EARM | Equipment Failure - Crossarm | N | Bad crossarm at industry and republic crew replaced | -90.0725 | 29.986 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 30 | 2020 | 1323555868 | Yes | EAST ORLEANS | THDR | 231 | 2020-02-05 | 6930 | LFUS | 82569 | 4192847736 | 2347 | ENOI | 6 | 30 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up wire | -90.0091 | 29.9728 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 55 | 2020 | 1323610634 | Yes | EAST ORLEANS | THDR | 232 | 2020-02-06 | 12760 | LFUS | 23476 | 4333250949 | 2223 | ENOI | 6 | 55 | LGHT | Lightning | N | weasther | -89.9637 | 30.0609 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 86 | 2020 | 1326578592 | Yes | EAST ORLEANS | FAIR | 232 | 2020-04-09 | 19952 | LFUS | 21116 | 4094548019 | 621 | ENOI | 6 | 86 | VHCL | Vehicle | N | vehicle hit and broke pole, wires down, crew repaired | -90.0402 | 29.981 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 35 | 2020 | 1333666539 | Yes | EAST ORLEANS | THDR | 232 | 2020-06-24 | 8120 | LFUS | 26127 | 4386451333 | 2223 | ENOI | 6 | 35 | ETRD | Equipment Failure - Transformer | N | replaced | -89.9467 | 30.0711 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 27 | 2020 | 1331092394 | Yes | EAST ORLEANS | FAIR | 233 | 2020-05-22 | 6291 | LFUS | 25735-F | 4282650283 | 2216 | ENOI | 6 | 27 | EPRI | Equipment Failure - Primary Conductor | N | FLDIncomplete Remarks: 2020-05-22-05:00 000027027- map 33 C phase hot to v42..arcoss crew brian.. | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 115 | 2020 | 1332564727 | Yes | EAST ORLEANS | FAIR | 235 | 2020-06-07 | 27025 | RCLR | 37793 | 4946452184 | 1204 | ENOI | 6 | 115 | EPRI | Equipment Failure - Primary Conductor | N | found wire down; cleared and closed back in | -89.7692 | 30.0928 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 6
2020 | 8 | 2020 | 1332967321 | Yes | EAST ORLEANS | FAIR | 235 | 2020-06-11 | 1880 | XFMR | 64977 | 41183479325 | 621 | ENOI | 6 | 8 | ETRD | Equipment Failure - Transformer | N |  | -90.0326 | 29.9786 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 606 | 2020 | 1328259542 | Yes | ORLEANS | THDR | 236 | 2020-04-18 | 143016 | DIS | 27016 | 39528460309 | 2147 | ENOI | 1 | 606 | EARM | Equipment Failure - Crossarm | N | Crew on site replacing cross arms | -90.0864 | 29.9264 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 7 | 2020 | 1326310714 | Yes | ORLEANS | FAIR | 237 | 2020-04-04 | 1659 | TFUS | 55743 | 40138487847 | 1704 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0654 | 30.0023 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 6 | 2020 | 1326310722 | Yes | ORLEANS | FAIR | 238 | 2020-04-04 | 1428 | TFUS | 71373 | 40139487707 | 1704 | ENOI | 1 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0654 | 30.0019 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 5 | 2020 | 1333619723 | Yes | EAST ORLEANS | THDR | 238 | 2020-06-24 | 1190 | TFUS | 73782 | 41446474331 | 2347 | ENOI | 6 | 5 | EARM | Equipment Failure - Crossarm | N | changed x arm | -90.0246 | 29.9649 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 4 | 2020 | 1333999630 | Yes | ORLEANS | FAIR | 238 | 2020-06-29 | 952 | TFUS | 63555 | 39493460432 | 2147 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N |  | -90.0867 | 29.9273 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 370 | 2020 | 1333407075 | Yes | EAST ORLEANS | THDR | 239 | 2020-06-22 | 88430 | LFUS | 27045 | 4279549796 | 2211 | ENOI | 6 | 370 | AOTH | Animal - Other (Describe in Remarks Field) | N | VFI 248 opened tripped closed okay Found rat nest & switch flashed over in cub # 8 R.S. I-10 up of Plaza Dr. | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 23 | 2020 | 1322735698 | Yes | EAST ORLEANS | FAIR | 240 | 2020-01-14 | 5520 | TFUS | 67500 | 40484476639 | 623 | ENOI | 6 | 23 | SCHD | Scheduled Interruption | N | ppole transfer | -90.0547 | 29.9714 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 9 | 2020 | 1327356631 | Yes | ORLEANS | FAIR | 240 | 2020-04-13 | 2160 | LFUS | 13221 | 38376479437 | 400 | ENOI | 1 | 9 | UNKN | Inspected Unknown | N | b phase blow on lateral | -90.1213 | 29.9798 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 28 | 2020 | 1323337190 | Yes | ORLEANS | FAIR | 241 | 2020-01-30 | 6748 | SWIT | 7 | 38833494311 | 401 | ENOI | 1 | 28 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Switch | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70124 | 1
2020 | 72 | 2020 | 1333587831 | Yes | EAST ORLEANS | FAIR | 241 | 2020-06-23 | 17352 | LFUS | 77900 | 4157249422 | 1010 | ENOI | 6 | 72 | ECNS | Equipment Failure - Connector Sleeve | N | repaired jumper conn | -90.02 | 30.0194 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 17 | 2020 | 1322615999 | Yes | ORLEANS | FAIR | 242 | 2020-01-13 | 4114 | DIS | 27125 | 38503474755 | 2011 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | outage required to safely replace rotten xarms located at the intersection of Olive and Leonidas | -90.1174 | 29.9667 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 5 | 2020 | 1323823115 | Yes | EAST ORLEANS | FAIR | 242 | 2020-02-11 | 1694 | XFMR | 1049527 | 4184247070 | 2346 | ENOI | 6 | 5 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.0122 | 29.9546 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 7 | 2020 | 1324387775 | Yes | EAST ORLEANS | FAIR | 242 | 2020-02-23 | 1694 | TFUS | 527839 | 42532504275 | 2215 | ENOI | 6 | 7 | ASQL | Animal - Squirrel | N | refused pot; lights back on | -89.989 | 30.0469 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 144 | 2020 | 1330348082 | Yes | EAST ORLEANS | FAIR | 242 | 2020-05-11 | 8496 | DIS | 23562 | 4155947419 | 622 | ENOI | 6 | 144 | EPRI | Equipment Failure - Primary Conductor | N | Crew on the way to make repairs | -90.0217 | 29.9642 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 5
2020 | 10 | 2020 | 1323571541 | Yes | EAST ORLEANS | THDR | 243 | 2020-02-05 | 2430 | TFUS | 1358844 | 44417501345 | 1205 | ENOI | 6 | 10 | AOTH | Animal - Other (Describe in Remarks Field) | N | rat took out b phase lateral in cubicle 82- refused ok-cust back on | -89.9296 | 30.0381 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 6 | 2020 | 1326691838 | Yes | ORLEANS | THDR | 243 | 2020-04-09 | 1458 | TFUS | 1187 | 38678484927 | 408 | ENOI | 1 | 6 | LGHT | Lightning | N | taken out by weather refused ok | -90.1115 | 29.9947 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 1 | 2020 | 1331943395 | Yes | ORLEANS | FAIR | 244 | 2020-05-28 | 244 | XFMR | 68185 | 38827477293 | 2026 | ENOI | 1 | 1 | ETRD | Equipment Failure - Transformer | N | Changed out transformer everyone back in lights, mismatch customers | -90.107 | 29.9736 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 5
2020 | 401 | 2020 | 1328235772 | Yes | ORLEANS | RAIN | 245 | 2020-04-18 | 98245 | DIS | 24655 | 3943947293 | 1513 | ENOI | 1 | 401 | ECAP | Equipment Failure - Capacitor | N | step retore | -90.0879 | 29.9616 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 276 | 2020 | 1321835001 | Yes | EAST ORLEANS | FAIR | 247 | 2020-01-08 | 68172 | LFUS | 26252 | 4360850642 | 2214 | ENOI | 6 | 276 | ETRD | Equipment Failure - Transformer | N | crew to replace | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 12 | 2020 | 1329816432 | Yes | ORLEANS | FAIR | 248 | 2020-05-03 | 2976 | LFUS | 17733 | 3864448471 | 408 | ENOI | 1 | 12 | VHCL | Vehicle | N | crew replacing broken pole | -90.1125 | 29.9942 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 4 | 2020 | 1333522572 | Yes | EAST ORLEANS | FAIR | 248 | 2020-06-23 | 992 | XFMR | 23303 | 41680496592 | 1001 | ENOI | 6 | 4 | ETRD | Equipment Failure - Transformer | N |  | -90.0162 | 30.0259 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 3 | 2020 | 1323037426 | Yes | EAST ORLEANS | FAIR | 249 | 2020-01-20 | 747 | XFMR | 1193965 | 42845504050 | 2216 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | bad transformer, crew in route | -89.9791 | 30.0459 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 278 | 2020 | 1332457581 | Yes | EAST ORLEANS | FAIR | 250 | 2020-06-06 | 69500 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 278 | SCHD | Scheduled Interruption | N | #6 copper | -90.0335 | 29.9718 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 60 | 2020 | 1334033560 | Yes | EAST ORLEANS | FAIR | 251 | 2020-06-29 | 15060 | LFUS | 25734 | 4328950589 | 2214 | ENOI | 6 | 60 | EPRI | Equipment Failure - Primary Conductor | N | Failed lateral cable on "B" phase vlt 118 Sw. 25734 was carrying all of "B" phase at the time up to switch 25724 Crew made repairs | -97.0758 | 27.9067 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 4 | 2020 | 1325394235 | Yes | ORLEANS | FAIR | 252 | 2020-03-14 | 1008 | DIS | 23922 | 3846845651 | 1927 | ENOI | 1 | 4 | ECNS | Equipment Failure - Connector Sleeve | N | primary down and jumper burned @ Arrabella & Camp Sts | -90.1192 | 29.9167 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 20 | 2020 | 1323636140 | Yes | EAST ORLEANS | WIND | 253 | 2020-02-06 | 5060 | LFUS | 75618 | 4081847779 | 622 | ENOI | 6 | 20 | VINE | Vine Growing into Line | N | vine pole..clear..refused lateral.. | -90.0441 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 95 | 2020 | 1327056099 | Yes | EAST ORLEANS | THDR | 253 | 2020-04-12 | 24035 | LFUS | 27876 | 4359749690 | 1601 | ENOI | 6 | 95 | SLAK | Slack Conductor / Loose Connection | N | Crew installed spacers | -89.9558 | 30.0259 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 43 | 2020 | 1331260411 | Yes | EAST ORLEANS | THDR | 253 | 2020-05-23 | 10879 | LFUS | 31644 | 4115547434 | 2347 | ENOI | 6 | 43 | LGHT | Lightning | N | refused ok | -90.0336 | 29.965 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | C | Council District C | Kristin Palmer | 70117 | 5
2020 | 1 | 2020 | 1332906762 | Yes | EAST ORLEANS | FAIR | 255 | 2020-06-10 | 255 | XFMR | 1546002 | 43485495078 | 1612 | ENOI | 6 | 1 | ETRD | Equipment Failure - Transformer | N | replaced transformer | -89.9593 | 30.0211 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 6 | 2020 | 1326148987 | Yes | EAST ORLEANS | FAIR | 256 | 2020-03-31 | 1536 | XFMR | 569607 | 43481509717 | 2217 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N | Crew on the way to repair submersible | -89.9588 | 30.0614 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 9 | 2020 | 1329246239 | Yes | EAST ORLEANS | THDR | 256 | 2020-04-28 | 2304 | TFUS | 78585 | 40983474510 | 622 | ENOI | 6 | 9 | EARM | Equipment Failure - Crossarm | N | fire dept put lat x arm out..temp safe will turn ticket.. | -90.039 | 29.9657 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 4
2020 | 1 | 2020 | 1330510309 | Yes | EAST ORLEANS | FAIR | 257 | 2020-05-13 | 257 | SERV | SERVICE | 42819495980 | 1604 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | repaired | -89.9804 | 30.0239 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 9 | 2020 | 1326905599 | Yes | ORLEANS | WIND | 259 | 2020-04-12 | 2331 | TFUS | 56582 | 39533474552 | 907 | ENOI | 1 | 9 | EARM | Equipment Failure - Crossarm | N | secondary arm replaced | -90.0848 | 29.9659 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 3 | 2020 | 1329343316 | Yes | EAST ORLEANS | THDR | 259 | 2020-04-29 | 777 | TFUS | 31958 | 41345479463 | 621 | ENOI | 6 | 3 | EARR | Equipment Failure - Arrestor | N | crew is enroute to repair cable | -90.027 | 29.9789 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 9 | 2020 | 1332922746 | Yes | EAST ORLEANS | FAIR | 259 | 2020-06-10 | 2331 | XFMR | 24516 | 41644492034 | 1001 | ENOI | 6 | 9 | ETRD | Equipment Failure - Transformer | N |  | -90.0174 | 30.0134 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 6
2020 | 4 | 2020 | 1321831987 | Yes | EAST ORLEANS | FAIR | 260 | 2020-01-08 | 1040 | TFUS | 79575 | 42517501966 | 2212 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N |  | -89.9896 | 30.0404 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 24 | 2020 | 1325530057 | Yes | EAST ORLEANS | FAIR | 260 | 2020-03-19 | 6240 | TFUS | 3005286 | 42615493129 | 1604 | ENOI | 6 | 24 | VINE | Vine Growing into Line | N | cleared vines and refused transformer 300528 | -89.9867 | 30.0162 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 68 | 2020 | 1328311357 | Yes | ORLEANS | FAIR | 260 | 2020-04-18 | 17680 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 68 | EARM | Equipment Failure - Crossarm | N | Repaired crossarm at 828 hagan | -90.0878 | 29.975 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 71 | 2020 | 1329258577 | Yes | EAST ORLEANS | THDR | 261 | 2020-04-28 | 18531 | LFUS | 27162 | 4203949893 | 2211 | ENOI | 6 | 71 | EELB | Equipment Failure - Elbow | N | changed out bad elbow in front of 7143 mayo blvd | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 4 | 2020 | 1324041039 | Yes | ORLEANS | FAIR | 264 | 2020-02-16 | 1056 | XFMR | 549347 | 38505459883 | 1914 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | bad xfmr, changed xfmr | -90.1178 | 29.9259 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 2
2020 | 3 | 2020 | 1325880626 | Yes | EAST ORLEANS | FAIR | 265 | 2020-03-26 | 795 | XFMR | 1149816 | 42899504160 | 2216 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | changed out transf. | -89.9775 | 30.0462 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 9 | 2020 | 1332161825 | Yes | EAST ORLEANS | FAIR | 265 | 2020-06-02 | 2385 | TFUS | 1049544 | 41845474743 | 2347 | ENOI | 6 | 9 | VHCL | Vehicle | N | vehicle hit pole | -90.0119 | 29.9657 | NP | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 3 | 2020 | 1333933571 | Yes | EAST ORLEANS | FAIR | 265 | 2020-06-27 | 795 | TFUS | 58599 | 40450482323 | 613 | ENOI | 6 | 3 | ASQL | Animal - Squirrel | N | Refused transformer taken out by squirrel | -90.0556 | 29.9869 | NP | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 25 | 2020 | 1323557034 | Yes | EAST ORLEANS | THDR | 266 | 2020-02-05 | 6650 | LFUS | 34975 | 4151047208 | 2346 | ENOI | 6 | 25 | LGHT | Lightning | N | refuse b phase | -90.0226 | 29.9585 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 10 | 2020 | 1326692771 | Yes | ORLEANS | THDR | 266 | 2020-04-09 | 2660 | TFUS | 1205965 | 38703472254 | 2011 | ENOI | 1 | 10 | LGHT | Lightning | N | taken out by weather refused ok | -90.1113 | 29.9599 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 45 | 2020 | 1330681584 | Yes | ORLEANS | FAIR | 266 | 2020-05-15 | 11970 | LFUS | 17901 | 3974049424 | 510 | ENOI | 1 | 45 | EARM | Equipment Failure - Crossarm | N | Brokwdead end arm at duplesis and aviators crew repaired | -90.0777 | 30.0198 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 69 | 2020 | 1332264706 | Yes | ORLEANS | FAIR | 266 | 2020-06-04 | 18354 | LFUS | 21455 | 3935745789 | 1922 | ENOI | 1 | 69 | EARM | Equipment Failure - Crossarm | N | crew needs to replace single phase cross arm | -90.0909 | 29.9201 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 16 | 2020 | 1333634617 | Yes | EAST ORLEANS | THDR | 267 | 2020-06-24 | 4272 | XFMR | 78347 | 40490475901 | 623 | ENOI | 6 | 16 | ETRD | Equipment Failure - Transformer | N |  | -90.0544 | 29.9695 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 83 | 2020 | 1326693094 | Yes | ORLEANS | THDR | 270 | 2020-04-09 | 22410 | LFUS | 27672 | 3968747354 | 1511 | ENOI | 1 | 83 | LGHT | Lightning | N | taken out by weather refused ok | -90.08 | 29.9631 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70112 | 4
2020 | 11 | 2020 | 1330841866 | Yes | EAST ORLEANS | FAIR | 270 | 2020-05-17 | 2970 | XFMR | 1052320 | 4374351056 | 2217 | ENOI | 6 | 11 | ETRD | Equipment Failure - Transformer | N | crew change out submersible transformer | -89.9506 | 30.0636 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 5
2020 | 111 | 2020 | 1333588099 | Yes | ORLEANS | THDR | 270 | 2020-06-23 | 29970 | LFUS | 17745 | 3856249404 | 409 | ENOI | 1 | 111 | ECNS | Equipment Failure - Connector Sleeve | N | primary jumper broke, repaired and customer back in | -90.1147 | 30.0198 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 41 | 2020 | 1325282371 | Yes | ALGIERS ELEC ONLY | FAIR | 272 | 2020-03-11 | 11152 | LFUS | 5916 | 4177346429 | W0726 | ENOI | 81 | 41 | ECNS | Equipment Failure - Connector Sleeve | N |  | -90.0146 | 29.9372 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70114 | 3
2020 | 40 | 2020 | 1326693224 | Yes | EAST ORLEANS | THDR | 272 | 2020-04-09 | 10880 | LFUS | 21769 | 4296949346 | 1611 | ENOI | 6 | 40 | EFLK | Equipment Failure - Fuse Link | N | Refuse lateral 21769 b&amp;amp;c phases customer back in | -89.9756 | 30.0169 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 6 | 2020 | 1327885181 | Yes | ORLEANS | FAIR | 272 | 2020-04-15 | 1632 | TFUS | 52109 | 38371491817 | 409 | ENOI | 1 | 6 | VOHL | Overhanging Limb | N | tree branch got across transformer; trimmed dead branches and refused | -90.1209 | 30.0137 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 98 | 2020 | 1324448213 | Yes | ORLEANS | FAIR | 274 | 2020-02-24 | 26852 | LFUS | F05614 | 39978464632 | 2137 | ENOI | 1 | 98 | EARM | Equipment Failure - Crossarm | N | crossarms replaced | -90.0713 | 29.9386 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 1 | 2020 | 1324635782 | Yes | ORLEANS | FAIR | 274 | 2020-02-27 | 274 | XFMR | 1087045 | 3914247399 | 912 | ENOI | 1 | 1 | ETRD | Equipment Failure - Transformer | N | crew changed out xfmr | -90.0972 | 29.9645 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 2
2020 | 42 | 2020 | 1333689652 | Yes | EAST ORLEANS | THDR | 274 | 2020-06-24 | 11508 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 42 | EPRI | Equipment Failure - Primary Conductor | N | Failed cable in vault #4 isolated going to vlt. #3 | -89.9561 | 30.0595 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 5 | 2020 | 1330911972 | Yes | EAST ORLEANS | FAIR | 275 | 2020-05-18 | 1375 | TFUS | 73565 | 42153493209 | 1604 | ENOI | 6 | 5 | ESEC | Secondary/Service Conductor | N | SERVICEMAN CALLED THE DOC AND REQUESTED TICKET FOR VEGETATION - GAVE EMPTY LOT ADDRESS | -90.0013 | 30.0164 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 5
2020 | 7 | 2020 | 1332913133 | Yes | ORLEANS | FAIR | 276 | 2020-06-10 | 1932 | XFMR | 74477 | 39811487372 | 1704 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N | CHANGED OUT TRANSFORMER | -90.0756 | 30.001 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 26 | 2020 | 1323911490 | Yes | ALGIERS ELEC ONLY | FAIR | 277 | 2020-02-13 | 7202 | TFUS | BY78432 | 4057647060 | W0715 | ENOI | 81 | 26 | VINE | Vine Growing into Line | N | serviceman removed vines from transformer (pwd) | -90.0521 | 29.9548 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 172 | 2020 | 1323119101 | Yes | EAST ORLEANS | FAIR | 278 | 2020-01-22 | 47816 | LFUS | 25610 | 4335750498 | 2214 | ENOI | 6 | 172 | EELB | Equipment Failure - Elbow | N | bad elbow | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 1138 | 2020 | 1328288893 | Yes | ORLEANS | RAIN | 278 | 2020-04-18 | 316364 | DIS | 63257 | 39639473127 | 1511 | ENOI | 1 | 1138 | ECNS | Equipment Failure - Connector Sleeve | N | jumper sleeve burnt up, crew replaced | -90.0819 | 29.9621 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70112 | 4
2020 | 5 | 2020 | 1328475910 | Yes | EAST ORLEANS | FAIR | 279 | 2020-04-20 | 1395 | TFUS | 1125645 | 43513495761 | 1612 | ENOI | 6 | 5 | ESEC | Secondary/Service Conductor | N | serparated open wire secondary tangled in tree; refused transformer | -89.9585 | 30.023 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 11 | 2020 | 1334126825 | Yes | ORLEANS | FAIR | 279 | 2020-06-30 | 3069 | TFUS | 33479 | 38480492907 | 411 | ENOI | 1 | 11 | EARM | Equipment Failure - Crossarm | N | Bad crossarm repaired | -90.1174 | 30.0168 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 68 | 2020 | 1323384442 | Yes | ORLEANS | FAIR | 280 | 2020-02-01 | 19040 | LFUS | 17674 | 4020349326 | 503 | ENOI | 1 | 68 | EARM | Equipment Failure - Crossarm | N | Broken crossarm caused lateral outage also caused 1 span of lateral to burn down at sleeve. | -90.0632 | 30.0171 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 10 | 2020 | 1328634738 | Yes | EAST ORLEANS | WIND | 280 | 2020-04-22 | 2800 | TFUS | 75706 | 4086548444 | 612 | ENOI | 6 | 10 | VHCL | Vehicle | N | Had to leave transformer out for safety to replace broken pole, PID CHG to NO, related to #1328608621 (DGault) | -90.0424 | 29.9925 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70126 | 4
2020 | 965 | 2020 | 1329525099 | Yes | ORLEANS | THDR | 281 | 2020-04-29 | 271165 | DIS | 39544 | 38598459792 | 1917 | ENOI | 1 | 965 | EMER | Emergency Switching | N | Broken cross arm at location....switching was done to isolate....repaired arm and switched back in | -90.1148 | 29.9256 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 4
2020 | 31 | 2020 | 1333203281 | Yes | EAST ORLEANS | FAIR | 281 | 2020-06-17 | 8711 | LFUS | 25724 | 4319150521 | 2214 | ENOI | 6 | 31 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 9 | 2020 | 1326691934 | Yes | EAST ORLEANS | THDR | 282 | 2020-04-09 | 2538 | TFUS | 54886 | 42273502070 | 2211 | ENOI | 6 | 9 | EFSW | Equipment Failure - Fuse Switch | N | Wire broke on top of switch repaired | -89.9974 | 30.0409 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 3 | 2020 | 1326696357 | Yes | EAST ORLEANS | THDR | 282 | 2020-04-10 | 846 | XFMR | 1324626 | 40667491561 | 502 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | Bad transformer 50 Kva | -90.0485 | 30.0125 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 8 | 2020 | 1333072397 | Yes | EAST ORLEANS | FAIR | 282 | 2020-06-15 | 2256 | XFMR | 64157 | 41009476922 | 611 | ENOI | 6 | 8 | ETRD | Equipment Failure - Transformer | N | replaced transformer | -90.0379 | 29.9721 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 26 | 2020 | 1323427511 | Yes | ORLEANS | FAIR | 283 | 2020-02-02 | 7358 | LFUS | 21189 | 3800546584 | B0527 | ENOI | 1 | 26 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1335 | 29.9423 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 12 | 2020 | 1331172961 | Yes | ORLEANS | FAIR | 283 | 2020-05-22 | 3396 | TFUS | 58903 | 39972475467 | 1712 | ENOI | 1 | 12 | FOTH | Fire - Other (Describe in Remarks Field) | N | 2 alarm fire | -90.0711 | 29.9684 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 5 | 2020 | 1329550751 | Yes | ORLEANS | THDR | 285 | 2020-04-29 | 1425 | TFUS | 59457 | 39625475328 | 907 | ENOI | 1 | 5 | FTNU | Foreign Trouble - Neighboring Utility | N | att&t knocked down primary RELATED TO TKT#1329589613 (A.STEWART) | -90.0821 | 29.968 | 19-YTD20 | 210557 | Jan1 to Yesterday | Foreign Trouble | Transformer Fuse | Foreign Trouble | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 97 | 2020 | 1325778061 | Yes | ORLEANS | FAIR | 286 | 2020-03-25 | 27742 | LFUS | 38032 | 3893546975 | 2015 | ENOI | 1 | 97 | FOTH | Fire - Other (Describe in Remarks Field) | N | lateral is out due to a fire | -90.1038 | 29.953 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 1 | 2020 | 1333027393 | Yes | ORLEANS | FAIR | 287 | 2020-06-13 | 287 | SERV | METER | 38306468034 | 2013 | ENOI | 1 | 1 | EMET | Equipment Failure - Metering | N | change out bad ami meter | -90.124 | 29.9485 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 6
2020 | 1 | 2020 | 1324683772 | Yes | EAST ORLEANS | FAIR | 289 | 2020-02-29 | 289 | SECO | SERVICE | 40861490898 | 501 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.0422 | 30.0105 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Secondary Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 4 | 2020 | 1325850439 | Yes | EAST ORLEANS | FAIR | 289 | 2020-03-26 | 1156 | ELBO | 43284504925 | 43284504925 | 2214 | ENOI | 6 | 4 | ETRD | Equipment Failure - Transformer | N | burnt transformer replaced | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Elbow | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 104 | 2020 | 1328231576 | Yes | EAST ORLEANS | FAIR | 289 | 2020-04-18 | 30056 | LFUS | 27803 | 4055548010 | 613 | ENOI | 6 | 104 | EARM | Equipment Failure - Crossarm | N |  | -90.0523 | 29.981 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 1 | 2020 | 1328478124 | Yes | EAST ORLEANS | FAIR | 289 | 2020-04-20 | 289 | TFUS | 64068 | 40338487485 | 1702 | ENOI | 6 | 1 | EARR | Equipment Failure - Arrestor | N | cleared blown arrestor and refused transformer | -90.0593 | 30.0012 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 4
2020 | 89 | 2020 | 1332519399 | Yes | EAST ORLEANS | RAIN | 289 | 2020-06-07 | 25721 | LFUS | 27327 | 4260850041 | 2216 | ENOI | 6 | 89 | EELB | Equipment Failure - Elbow | N | BAD ELBOW SALEM | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 15 | 2020 | 1325319637 | Yes | EAST ORLEANS | FAIR | 294 | 2020-03-12 | 4410 | LFUS | 27847 | 4291250653 | 2215 | ENOI | 6 | 15 | SCHD | Scheduled Interruption | N | work completed | -89.977 | 30.0529 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 66 | 2020 | 1323551306 | Yes | EAST ORLEANS | THDR | 297 | 2020-02-05 | 19602 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 66 | LGHT | Lightning | N |  | -89.959 | 30.0234 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 73 | 2020 | 1328044401 | Yes | EAST ORLEANS | FAIR | 297 | 2020-04-16 | 21681 | LFUS | 32497 | 4112647692 | 611 | ENOI | 6 | 73 | SCHD | Scheduled Interruption | N | Scheduled Interruption for safety to replace broken pole RELATED TO TKT#1328030710 (AKS) | -90.0346 | 29.972 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 4
2020 | 172 | 2020 | 1326658765 | Yes | EAST ORLEANS | THDR | 300 | 2020-04-09 | 51600 | LFUS | 25610 | 4335750498 | 2214 | ENOI | 6 | 172 | EELB | Equipment Failure - Elbow | N | replaced elbow in submersible xfmr | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 4
2020 | 246 | 2020 | 1333431435 | Yes | ORLEANS | THDR | 302 | 2020-06-22 | 74292 | LFUS | 37780 | 3990648264 | 1709 | ENOI | 1 | 246 | EARM | Equipment Failure - Crossarm | N |  | -90.0728 | 29.9879 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 1 | 2020 | 1323284518 | Yes | EAST ORLEANS | FAIR | 303 | 2020-01-28 | 303 | SERV | SERVICE | 42166494030 | 1607 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | picked up wire, good voltage | -90.001 | 30.0187 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 90 | 2020 | 1323344448 | Yes | EAST ORLEANS | FAIR | 303 | 2020-01-30 | 27270 | LFUS | 27340-F | 4482350242 | 1205 | ENOI | 6 | 90 | ETRD | Equipment Failure - Transformer | N |  | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 14 | 2020 | 1327825400 | Yes | ORLEANS | FAIR | 305 | 2020-04-14 | 4270 | LFUS | 33455 | 3866347238 | 2011 | ENOI | 1 | 14 | EPOL | Equipment Failure - Pole | N | replace | -90.1125 | 29.9602 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 10 | 2020 | 1332146024 | Yes | EAST ORLEANS | FAIR | 305 | 2020-06-02 | 3050 | TFUS | 74547 | 41026476240 | 611 | ENOI | 6 | 10 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0377 | 29.9702 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 6
2020 | 1 | 2020 | 1323436744 | Yes | EAST ORLEANS | FAIR | 307 | 2020-02-03 | 307 | TFUS | 28497 | 41836500134 | 2212 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | replaced jumper connection | -90.0113 | 30.0356 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 44 | 2020 | 1321707115 | Yes | EAST ORLEANS | FAIR | 310 | 2020-01-03 | 13640 | LFUS | 27215 | 4204249890 | 2211 | ENOI | 6 | 44 | EPRI | Equipment Failure - Primary Conductor | N | crew to repair | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 5 | 2020 | 1330425295 | Yes | ORLEANS | FAIR | 310 | 2020-05-12 | 1550 | XFMR | 67437 | 38720465716 | 2016 | ENOI | 1 | 5 | ETRD | Equipment Failure - Transformer | N | changed out bad transformer | -90.1108 | 29.942 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 1 | 2020 | 1322667082 | Yes | ALGIERS ELEC ONLY | FOGG | 311 | 2020-01-13 | 311 | SERV | SERVICE | 4136546563 | W0725 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N | Changed **TFUS BY88464 37 to SERV BY88464 1** --- old service line went bad. changed out line and good voltage checked mtaruc | -90.0274 | 29.9409 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 9 | 2020 | 1324187155 | Yes | ALGIERS ELEC ONLY | FAIR | 311 | 2020-02-20 | 2799 | XFMR | BY98542 | 4159646652 | W0723 | ENOI | 81 | 9 | ETRD | Equipment Failure - Transformer | N | bad transformer at location. | -90.02 | 29.9432 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 192 | 2020 | 1330675315 | Yes | EAST ORLEANS | FAIR | 311 | 2020-05-15 | 59712 | NTWK | NTWK | 00000000000 | 1613 | ENOI | 6 | 192 | VHCL | Vehicle | N | vehicle hit cubicle |  |  | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Network | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 5
2020 | 6 | 2020 | 1326098448 | Yes | ORLEANS | FAIR | 313 | 2020-03-30 | 0 | TFUS | 54894 | 3878546969 | 2015 | ENOI | 1 | 6 | VINE | Vine Growing into Line | N | Cleared vines refused transformer HW | -90.1086 | 29.9528 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70125 | 3
2020 | 41 | 2020 | 1323557039 | Yes | EAST ORLEANS | THDR | 315 | 2020-02-05 | 12915 | LFUS | 31818 | 4164547152 | 2346 | ENOI | 6 | 41 | EPOL | Equipment Failure - Pole | N | refuse latteral | -90.0182 | 29.957 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 74 | 2020 | 1325731096 | Yes | EAST ORLEANS | FAIR | 315 | 2020-03-24 | 23310 | DIS | 22751 | 4654451526 | 1202 | ENOI | 6 | 74 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.862 | 30.0753 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 12 | 2020 | 1323251479 | Yes | ALGIERS ELEC ONLY | FAIR | 317 | 2020-01-27 | 3804 | TFUS | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | EFLK | Equipment Failure - Fuse Link | N | refused blown fuse | -89.9867 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 262 | 2020 | 1323085775 | Yes | EAST ORLEANS | FAIR | 320 | 2020-01-21 | 83840 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 262 | EPRI | Equipment Failure - Primary Conductor | N | wire down in marsh | -89.8028 | 30.0694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 238 | 2020 | 1324044207 | Yes | ORLEANS | FAIR | 320 | 2020-02-16 | 76160 | DIS | 23320 | 38432474479 | 2022 | ENOI | 1 | 238 | VHCL | Vehicle | N | Crew on site replacing broken pole PID IN PROGRESS RELATED TO TKT# 1324040006 (AKS) | -90.1197 | 29.966 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 11 | 2020 | 1332923841 | Yes | ORLEANS | FAIR | 320 | 2020-06-10 | 3520 | XFMR | 77959 | 40130487367 | 1704 | ENOI | 1 | 11 | ETRD | Equipment Failure - Transformer | N | Changed out bad transformer and increased the size do to overload | -90.0656 | 30.001 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 144 | 2020 | 1323293386 | Yes | EAST ORLEANS | RAIN | 321 | 2020-01-29 | 46224 | DIS | 23061 | 4122747782 | 621 | ENOI | 6 | 144 | EARM | Equipment Failure - Crossarm | N | broke crossarm at disc. 25291 | -90.0313 | 29.9745 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 7 | 2020 | 1324840355 | Yes | EAST ORLEANS | FAIR | 322 | 2020-03-03 | 2254 | XFMR | 77496 | 42469500417 | 1605 | ENOI | 6 | 7 | ETRD | Equipment Failure - Transformer | N | CREW CHANGED | -89.9911 | 30.0362 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 9 | 2020 | 1326262782 | Yes | ORLEANS | FAIR | 323 | 2020-04-03 | 2907 | TFUS | 21205 | 38725488458 | 408 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | transferred bell pole and changed xfmr | -90.1099 | 30.0044 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 39 | 2020 | 1332512186 | Yes | EAST ORLEANS | FAIR | 323 | 2020-06-06 | 12597 | LFUS | 25646 | 4272849783 | 1602 | ENOI | 6 | 39 | UNKN | Inspected Unknown | N | lights back on | -97.0758 | 27.9066 | NP | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 6
2020 | 24 | 2020 | 1333169664 | Yes | ORLEANS | FAIR | 323 | 2020-06-17 | 7752 | OPEN | 3942546875 | 3942546875 | 1554 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | Scheduled Interruption Change Pole | -90.0885 | 29.95 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Open | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 1 | 2020 | 1330020010 | Yes | ORLEANS CBD | FAIR | 324 | 2020-05-07 | 324 | TFUS | 571537 | 3968246818 | 1543 | ENOI | 4 | 1 | AOTH | Animal - Other (Describe in Remarks Field) | N | a bird contacted switch in station | -90.0805 | 29.9484 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 1 | 2020 | 1332513575 | Yes | ORLEANS | FAIR | 324 | 2020-06-06 | 324 | SERV | SERVICE COND | 38582458445 | 1913 | ENOI | 1 | 1 | VLGL | Tree/Limb Growing Inside R.O.W. | N | Trees rubbing on service burned phase Fixed ok | -90.1155 | 29.9221 | NP | 210557 | Jan1 to Yesterday | Vegetation | Service Conductor | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 6
2020 | 84 | 2020 | 1328241156 | Yes | ORLEANS | THDR | 328 | 2020-04-18 | 27552 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 84 | EARM | Equipment Failure - Crossarm | N | Cross arm mary have taken out lateral. Refused OK HW | -90.0878 | 29.975 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 4
2020 | 268 | 2020 | 1324358592 | Yes | EAST ORLEANS | FAIR | 329 | 2020-02-21 | 88172 | DIS | 24625 | 4063748581 | 1710 | ENOI | 6 | 268 | EARM | Equipment Failure - Crossarm | N | broken cross arm crew is enroute to replace arm | -90.0497 | 29.9965 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1 | 2020 | 1322323741 | Yes | ALGIERS ELEC ONLY | THDR | 330 | 2020-01-11 | 330 | TFUS | 1543046 | 4141646669 | W1725 | ENOI | 81 | 1 | EMER | Emergency Switching | N | Opened in order for crew to make repairs. per B. rissuto............PC | -90.0258 | 29.9437 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Emergency Switching | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 327 | 2020 | 1328799805 | Yes | ORLEANS | FAIR | 333 | 2020-04-23 | 108891 | OPEN | 4009046539 | 4009046539 | 1826 | ENOI | 1 | 327 | EARM | Equipment Failure - Crossarm | N | Equipment Failure -Broken Crossarm | -90.0676 | 29.9406 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Open | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 4
2020 | 19 | 2020 | 1325273476 | Yes | EAST ORLEANS | FAIR | 334 | 2020-03-10 | 6346 | TFUS | 619075 | 4212449674 | 1610 | ENOI | 6 | 19 | EPRI | Equipment Failure - Primary Conductor | N | bad cable, switched out | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 13 | 2020 | 1333404102 | Yes | EAST ORLEANS | THDR | 334 | 2020-06-22 | 4342 | LFUS | 25370 | 4385351220 | 2217 | ENOI | 6 | 13 | EPRI | Equipment Failure - Primary Conductor | N | bad underground cable V-13 to V-14 | -89.9472 | 30.0681 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 33 | 2020 | 1333591046 | Yes | ORLEANS | THDR | 334 | 2020-06-23 | 11022 | TFUS | 67342 | 39388478514 | 912 | ENOI | 1 | 33 | LGHT | Lightning | N | refused | -90.0895 | 29.977 | NP | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 3 | 2020 | 1324059083 | Yes | EAST ORLEANS | FAIR | 336 | 2020-02-17 | 1008 | TFUS | 62400 | 42950505451 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | Crew opened in order to safely do required work............. | -89.9759 | 30.0498 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 109 | 2020 | 1332937241 | Yes | ORLEANS | FAIR | 338 | 2020-06-11 | 36842 | DIS | 48419 | 3928746821 | 1553 | ENOI | 1 | 109 | SCHD | Scheduled Interruption | N | DSR # 48784 Scheduled Interruption Changing a Pole | -90.0929 | 29.9487 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 63 | 2020 | 1325868359 | Yes | EAST ORLEANS | FAIR | 339 | 2020-03-26 | 21357 | LFUS | 25848 | 4438450346 | 1608 | ENOI | 6 | 63 | EPRI | Equipment Failure - Primary Conductor | N | BAD CABLE | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 20 | 2020 | 1332893096 | Yes | ORLEANS | FAIR | 339 | 2020-06-10 | 6780 | XFMR | 31174 | 38911478917 | 2011 | ENOI | 1 | 20 | LGHT | Lightning | N | CHANGED TRANSFORMER | -90.1045 | 29.9782 | NP | 210557 | Jan1 to Yesterday | Lightning | Transformer | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 45 | 2020 | 1326701220 | Yes | ORLEANS | THDR | 340 | 2020-04-10 | 15300 | LFUS | 27910 | 4001447600 | 1712 | ENOI | 1 | 45 | LGHT | Lightning | N | taken out by weather refused ok | -90.0697 | 29.9698 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70116 | 4
2020 | 16 | 2020 | 1323357585 | Yes | ORLEANS | FAIR | 343 | 2020-01-30 | 5488 | LFUS | 17679 | 38333485489 | 400 | ENOI | 1 | 16 | VHCL | Vehicle | N | SENT TO CLAIMS AS MINIMAL CLAIM. NO CAR AT SCENE | -90.1224 | 29.9964 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 237 | 2020 | 1325285714 | Yes | EAST ORLEANS | FAIR | 344 | 2020-03-11 | 81528 | LFUS | 17998 | 4158049987 | 1010 | ENOI | 6 | 237 | SCHD | Scheduled Interruption | N | crew onsite | -90.0195 | 30.0348 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 581 | 2020 | 1324644436 | Yes | EAST ORLEANS | FAIR | 345 | 2020-02-28 | 200445 | SWIT | 25680 | 4211049707 | 1610 | ENOI | 6 | 581 | EPRI | Equipment Failure - Primary Conductor | N | Bad cable bet sw. # 25680 & # 86561. Picked up cust. from sw. # 25185 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 126 | 2020 | 1332900914 | Yes | EAST ORLEANS | FAIR | 345 | 2020-06-10 | 43470 | LFUS | 17998 | 4158049987 | 2212 | ENOI | 6 | 126 | SCHD | Scheduled Interruption | N |  | -90.0195 | 30.0348 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 9 | 2020 | 1333115830 | Yes | ORLEANS | FAIR | 345 | 2020-06-16 | 3105 | TFUS | 3001548 | 38950457703 | 1921 | ENOI | 1 | 9 | ECON | Equipment Failure - Connector / Sleeve | N | changed conections at pole | -90.1037 | 29.9198 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 37 | 2020 | 1325195154 | Yes | ORLEANS | FAIR | 347 | 2020-03-08 | 12839 | DIS | 24830 | 4009147967 | 615 | ENOI | 1 | 37 | VHCL | Vehicle | N | Crew on site working PID IN PROGRESS KC RELATED TO TKT# 1325193683 (AKS) | -90.0672 | 29.9799 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | D | Council District D | Jared Brossett | 70119 | 3
2020 | 243 | 2020 | 1326698180 | Yes | EAST ORLEANS | THDR | 348 | 2020-04-09 | 84564 | RCLR | 22184 | 4946452184 | 1204 | ENOI | 6 | 243 | EPRI | Equipment Failure - Primary Conductor | N | Wire down 22173 Chef 1/0 primary | -89.7692 | 30.0928 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 5 | 2020 | 1323046317 | Yes | EAST ORLEANS | FAIR | 352 | 2020-01-20 | 1760 | TFUS | 1193973 | 40899482518 | 611 | ENOI | 6 | 5 | ESEC | Secondary/Service Conductor | N | repairs at transformer | -90.0415 | 29.9874 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 1 | 2020 | 1324132625 | Yes | EAST ORLEANS | FAIR | 352 | 2020-02-18 | 352 | SERV | SERVICE | 42512499834 | 2216 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | repaired | -89.99 | 30.0345 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 44 | 2020 | 1328232509 | Yes | EAST ORLEANS | THDR | 354 | 2020-04-18 | 15576 | LFUS | 21745 | 4246649393 | 1607 | ENOI | 6 | 44 | EARM | Equipment Failure - Crossarm | N |  | -89.9914 | 30.0184 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 224 | 2020 | 1321627546 | Yes | ORLEANS | FAIR | 355 | 2020-01-01 | 79520 | LFUS | 28059 | 3928646516 | 1915 | ENOI | 1 | 224 | VHCL | Vehicle | N | car hit pole; 5 broke poles and wire down | -90.0929 | 29.9402 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 24 | 2020 | 1325602730 | Yes | ORLEANS | FAIR | 355 | 2020-03-20 | 8520 | LFUS | 17692 | 3887448776 | 405 | ENOI | 1 | 24 | ETRD | Equipment Failure - Transformer | N | Parrellel Transformers bad and took out lateral troubleshooter got lateral in crew changed out transformers | -90.1053 | 30.0025 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 8 | 2020 | 1332936778 | Yes | ORLEANS | FAIR | 355 | 2020-06-11 | 2840 | DIS | 61181 | 3930846808 | 2021 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption Changing a Pole | -90.0922 | 29.9484 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 136 | 2020 | 1325615894 | Yes | ORLEANS | FAIR | 356 | 2020-03-21 | 48416 | LFUS | 17747 | 3852449417 | 409 | ENOI | 1 | 136 | EARM | Equipment Failure - Crossarm | N | changed out x arm | -90.1161 | 30.0203 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 116 | 2020 | 1333711659 | Yes | EAST ORLEANS | FAIR | 356 | 2020-06-25 | 41296 | LFUS | 32647 | 4123847544 | 611 | ENOI | 6 | 116 | SCHD | Scheduled Interruption | N |  | -90.0309 | 29.9678 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 8 | 2020 | 1323262374 | Yes | ORLEANS | FAIR | 357 | 2020-01-28 | 2856 | TFUS | 62321 | 39300467704 | 2021 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0925 | 29.9471 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 22 | 2020 | 1333523047 | Yes | ORLEANS | FAIR | 358 | 2020-06-23 | 7876 | TFUS | 1351409 | 3972447529 | 907 | ENOI | 1 | 22 | SCHD | Scheduled Interruption | N | crew on site to repair riser on pole | -90.0789 | 29.968 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 86 | 2020 | 1322194593 | Yes | ORLEANS | THDR | 361 | 2020-01-11 | 31046 | LFUS | 27790 | 39932484636 | 1703 | ENOI | 1 | 86 | EARM | Equipment Failure - Crossarm | N | crew replaced crossarm and repaired pole | -90.072 | 29.9935 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 237 | 2020 | 1325210218 | Yes | EAST ORLEANS | FAIR | 361 | 2020-03-09 | 85557 | LFUS | 17998 | 4158049987 | 1010 | ENOI | 6 | 237 | SCHD | Scheduled Interruption | N | Scheduled Interruption; 267-683-0737 | -90.0195 | 30.0348 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 3
2020 | 98 | 2020 | 1326788386 | Yes | EAST ORLEANS | THDR | 362 | 2020-04-10 | 35476 | LFUS | 25980 | 4212449674 | 1610 | ENOI | 6 | 98 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 4
2020 | 2 | 2020 | 1325150169 | Yes | ALGIERS ELEC ONLY | FAIR | 363 | 2020-03-06 | 726 | TFUS | 1016 | 4197946327 | W0726 | ENOI | 81 | 2 | VHCL | Vehicle | N | Crew to pick up wire in which was snagged down stream of this dedvice,...............................PC | -90.008 | 29.9343 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 79 | 2020 | 1331974211 | Yes | ORLEANS | FAIR | 366 | 2020-05-28 | 28914 | OPEN | 4013048427 | 4013048427 | 1708 | ENOI | 1 | 79 | VHCL | Vehicle | N | car hit pole at intersecton of allen & pleasure; broke pole and primary down PID in Progress KC - ALSO SEE #1331969611 (DGAULT) | -90.0657 | 29.9925 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Open | Public Damage | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 55 | 2020 | 1325562835 | Yes | EAST ORLEANS | FAIR | 367 | 2020-03-19 | 20185 | LFUS | 25217 | 4240450217 | 2211 | ENOI | 6 | 55 | EELB | Equipment Failure - Elbow | N | repaired | -89.9932 | 30.0411 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 3
2020 | 425 | 2020 | 1325077072 | Yes | ORLEANS | FAIR | 368 | 2020-03-05 | 156400 | DIS | 14963 | 3844849081 | 410 | ENOI | 1 | 425 | VHCL | Vehicle | N | VehicleHit a Pole Crew Replaced AT&T Pole | -90.1185 | 30.011 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 3
2020 | 81 | 2020 | 1325251365 | Yes | EAST ORLEANS | FAIR | 369 | 2020-03-10 | 29889 | LFUS | 32305 | 4164647339 | 2346 | ENOI | 6 | 81 | VHCL | Vehicle | N | car broke pole | -90.0184 | 29.9622 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 3
2020 | 3 | 2020 | 1333532614 | Yes | EAST ORLEANS | FAIR | 373 | 2020-06-23 | 1119 | TFUS | 3009794 | 49677530926 | 1204 | ENOI | 6 | 3 | TSCF | Transformer Splicing chamber failure | N |  | -89.7622 | 30.1176 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 6
2020 | 176 | 2020 | 1325661916 | Yes | ORLEANS | FAIR | 376 | 2020-03-22 | 66176 | LFUS | 27949 | 3986347312 | 1511 | ENOI | 1 | 176 | VHCL | Vehicle | N | car broke pole PID IN PROGRESS KC RELATED TO TKT# 1325661916 (AKS0 | -90.0745 | 29.962 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 1 | 2020 | 1328108630 | Yes | EAST ORLEANS | FAIR | 377 | 2020-04-16 | 377 | SERV | SERVICE | 48065512163 | 1204 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | bad underground connection in hole | -89.8138 | 30.0666 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 74 | 2020 | 1325244985 | Yes | EAST ORLEANS | FAIR | 378 | 2020-03-10 | 27972 | LFUS | 27692 | 4373349583 | 1601 | ENOI | 6 | 74 | HNWK | Human Error - Non-Entergy Workers (Describe in Rem | N | contractor dug into line and knocked out later; crew replaced xfmr | -89.9517 | 30.023 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 234 | 2020 | 1323299416 | Yes | ORLEANS | FAIR | 384 | 2020-01-29 | 89856 | LFUS | 37908 | 3865747472 | 2017 | ENOI | 1 | 234 | ECNS | Equipment Failure - Connector Sleeve | N | SHIELD WIRE DOWN | -90.1124 | 29.9666 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 10 | 2020 | 1332071241 | Yes | ORLEANS | FAIR | 386 | 2020-05-31 | 3860 | XFMR | 53669 | 38859487011 | 405 | ENOI | 1 | 10 | ETRD | Equipment Failure - Transformer | N | Crew on the way to replace bad transformer | -90.1058 | 30.0004 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 5
2020 | 5 | 2020 | 1323574976 | Yes | EAST ORLEANS | THDR | 389 | 2020-02-05 | 1945 | TFUS | 1543254 | 43598495566 | 1601 | ENOI | 6 | 5 | EPOL | Equipment Failure - Pole | N | crew replacing pole | -89.9557 | 30.0224 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 25 | 2020 | 1333647910 | Yes | EAST ORLEANS | THDR | 389 | 2020-06-24 | 9725 | LFUS | 27931 | 4063848907 | 1702 | ENOI | 6 | 25 | EARM | Equipment Failure - Crossarm | N |  | -90.0494 | 30.0055 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 16 | 2020 | 1323384421 | Yes | EAST ORLEANS | FAIR | 390 | 2020-02-01 | 6240 | TFUS | 617753 | 43842513577 | 2217 | ENOI | 6 | 16 | ESEC | Secondary/Service Conductor | N | manhole burnt up repaired | -89.9472 | 30.0719 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 7 | 2020 | 1323295995 | Yes | ORLEANS | RAIN | 393 | 2020-01-29 | 2751 | TFUS | 1590194 | 39330467050 | 2021 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0917 | 29.9454 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 1 | 2020 | 1323384382 | Yes | EAST ORLEANS | FAIR | 393 | 2020-02-01 | 393 | SERV | SERVICE | 4386451333 | 2217 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | manhole burnt | -89.9466 | 30.0712 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 3 | 2020 | 1325402050 | Yes | ORLEANS | FAIR | 398 | 2020-03-15 | 1194 | XFMR | 510962 | 38488459675 | 1914 | ENOI | 1 | 3 | ETRD | Equipment Failure - Transformer | N |  | -90.1184 | 29.9253 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 3
2020 | 17 | 2020 | 1323248150 | Yes | ORLEANS | FAIR | 399 | 2020-01-27 | 6783 | XFMR | 62309 | 39410465886 | 1915 | ENOI | 1 | 17 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.089 | 29.9421 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 253 | 2020 | 1323053914 | Yes | EAST ORLEANS | FAIR | 401 | 2020-01-21 | 101453 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 253 | ETRD | Equipment Failure - Transformer | N | replaced transformer and lateral back in | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 11 | 2020 | 1324158085 | Yes | EAST ORLEANS | FAIR | 402 | 2020-02-19 | 4422 | DIS | 36981 | 4542049869 | 1202 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Taken out for safety of Transmission crews to repair damaged shield wire from the night before. All customers were notified | -89.8981 | 30.0303 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 40 | 2020 | 1333023090 | Yes | ORLEANS | FAIR | 402 | 2020-06-13 | 16080 | LFUS | 21513 | 3904846397 | 1925 | ENOI | 1 | 40 | EARM | Equipment Failure - Crossarm | N | crew to change x arm | -90.1008 | 29.9371 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 13 | 2020 | 1334095181 | Yes | EAST ORLEANS | FAIR | 404 | 2020-06-30 | 5252 | LFUS | 27847 | 4291250653 | 2215 | ENOI | 6 | 13 | SCHD | Scheduled Interruption | N |  | -89.977 | 30.0529 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 6
2020 | 614 | 2020 | 1323087728 | Yes | EAST ORLEANS | FAIR | 409 | 2020-01-21 | 251126 | RCLR | 85388 | 4373351112 | 2217 | ENOI | 6 | 614 | EPRI | Equipment Failure - Primary Conductor | N | wiredown | -89.951 | 30.0652 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 11 | 2020 | 1332887487 | Yes | EAST ORLEANS | FAIR | 412 | 2020-06-10 | 4532 | XFMR | 31538 | 41660473151 | 2346 | ENOI | 6 | 11 | ETRD | Equipment Failure - Transformer | N | replaced | -90.0177 | 29.9615 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 6
2020 | 4 | 2020 | 1332197352 | Yes | ORLEANS | FAIR | 415 | 2020-06-03 | 1660 | TFUS | 68857 | 39978489265 | 1704 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0704 | 30.0062 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 6
2020 | 237 | 2020 | 1333212662 | Yes | EAST ORLEANS | FAIR | 415 | 2020-06-18 | 98355 | LFUS | 17998 | 4158049987 | 2212 | ENOI | 6 | 237 | SCHD | Scheduled Interruption | N | contract crew | -90.0195 | 30.0348 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 15 | 2020 | 1325285990 | Yes | EAST ORLEANS | FAIR | 420 | 2020-03-11 | 6300 | LFUS | 27847 | 4291250653 | 2215 | ENOI | 6 | 15 | SCHD | Scheduled Interruption | N | crew has an outage set for today | -89.977 | 30.0529 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 4 | 2020 | 1325286004 | Yes | EAST ORLEANS | FAIR | 421 | 2020-03-11 | 1684 | TFUS | 1499229 | 42923506630 | 2215 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | crew has an outage setup for today | -89.9767 | 30.0531 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 15 | 2020 | 1329643305 | Yes | ORLEANS | FAIR | 424 | 2020-04-29 | 6360 | TFUS | 1453518 | 39598457845 | 1911 | ENOI | 1 | 15 | EARM | Equipment Failure - Crossarm | N |  | -90.0833 | 29.9201 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 74 | 2020 | 1327493389 | Yes | EAST ORLEANS | FAIR | 425 | 2020-04-13 | 31450 | DIS | 22751 | 4654451526 | 1202 | ENOI | 6 | 74 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.862 | 30.0753 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 182 | 2020 | 1328248973 | Yes | EAST ORLEANS | THDR | 425 | 2020-04-18 | 77350 | DIS | 24376 | 4269950499 | 2215 | ENOI | 6 | 182 | EPOL | Equipment Failure - Pole | N | Crew on site replacing pole | -89.9837 | 30.0488 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 2 | 2020 | 1332140508 | Yes | EAST ORLEANS | FAIR | 427 | 2020-06-02 | 854 | XFMR | 1454647 | 41446499086 | 1010 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N | crew changed out pot | -90.0234 | 30.0329 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 6
2020 | 10 | 2020 | 1333125945 | Yes | ORLEANS | FAIR | 432 | 2020-06-16 | 4320 | TFUS | 77859 | 39302461416 | 1924 | ENOI | 1 | 10 | EFLK | Equipment Failure - Fuse Link | N | found bad fuse barrel stuck in fiberglass split replaced fuse barrel refused ok | -90.0927 | 29.93 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 6
2020 | 8 | 2020 | 1323642003 | Yes | EAST ORLEANS | WIND | 433 | 2020-02-06 | 3464 | TFUS | 3010148 | 43306495734 | 1611 | ENOI | 6 | 8 | EFLK | Equipment Failure - Fuse Link | N | changed fuse barrel on trans.. | -89.9649 | 30.023 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 10 | 2020 | 1332046475 | Yes | ORLEANS | FAIR | 433 | 2020-05-30 | 4330 | LFUS | 17669 | 3978949022 | 512 | ENOI | 1 | 10 | VLFL | Tree On Line Outside R.O.W | N | removed tree, picked up wire and replaced crossarms | -90.0762 | 30.009 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 41 | 2020 | 1322465744 | Yes | ORLEANS | FAIR | 434 | 2020-01-12 | 17794 | DIS | 14349 | 3982346566 | 2137 | ENOI | 1 | 41 | EMER | Emergency Switching | N | broke pole, crew on site | -90.0761 | 29.9413 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 8 | 2020 | 1333587360 | Yes | ORLEANS | THDR | 434 | 2020-06-23 | 3472 | TFUS | 71038 | 40203480659 | 627 | ENOI | 1 | 8 | EARM | Equipment Failure - Crossarm | N | replaced rotten Wilson rack, spaced out vertical open wire secondary to prevent hot legs from touching | -90.0635 | 29.9824 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 6
2020 | 10 | 2020 | 1330020031 | Yes | ORLEANS | FAIR | 443 | 2020-05-07 | 4430 | TFUS | 62237 | 39248457780 | 1922 | ENOI | 1 | 10 | SCHD | Scheduled Interruption | N | Notified all customers | -90.0946 | 29.9198 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 5
2020 | 15 | 2020 | 1330700447 | Yes | EAST ORLEANS | FAIR | 443 | 2020-05-15 | 6645 | LFUS | 21045 | 4109548720 | 616 | ENOI | 6 | 15 | ETRD | Equipment Failure - Transformer | N | crew changed out bad pot | -90.0352 | 30.0002 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 5
2020 | 1 | 2020 | 1326080547 | Yes | ORLEANS | FAIR | 448 | 2020-03-30 | 448 | SWIT | 27253 | 39597471266 | 1506 | ENOI | 1 | 1 | SCHD | Scheduled Interruption | N | crew replacing cable in Vault # 211 Planned outage | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Switch | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70112 | 3
2020 | 48 | 2020 | 1323636868 | Yes | EAST ORLEANS | WIND | 451 | 2020-02-06 | 21648 | LFUS | 23476 | 4333250949 | 2223 | ENOI | 6 | 48 | EFSW | Equipment Failure - Fuse Switch | N | fuse switch repaired | -89.9637 | 30.0609 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 1290 | 2020 | 1328239789 | Yes | ORLEANS | THDR | 453 | 2020-04-18 | 584370 | DIS | D01640 | 3927347512 | 1513 | ENOI | 1 | 1290 | ECAP | Equipment Failure - Capacitor | N | Cleared twisted phases and cleared cap bank | -90.093 | 29.9676 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 1 | 2020 | 1328582850 | Yes | EAST ORLEANS | FAIR | 453 | 2020-04-22 | 453 | SERV | SERVICE | 44281499767 | 1601 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Need to crew to either locate or run new underground secondary service in the rear. Notified O.C. C. Bowers and you can put Brian Garnett s crew on the job. Made customer contact, advised of crew coming to make repairs. | -89.9339 | 30.0337 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 5 | 2020 | 1329248043 | Yes | EAST ORLEANS | THDR | 455 | 2020-04-28 | 2275 | TFUS | 58802 | 48464512640 | 1204 | ENOI | 6 | 5 | EARM | Equipment Failure - Crossarm | N | broke lateral arm | -89.8012 | 30.0678 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 9 | 2020 | 1325319467 | Yes | EAST ORLEANS | FAIR | 457 | 2020-03-12 | 4113 | TFUS | 1490486 | 46388537189 | 1202 | ENOI | 6 | 9 | ECON | Equipment Failure - Connector / Sleeve | N | bad connections on transformer leads/changed out connections good voltage | -89.8658 | 30.136 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 3
2020 | 36 | 2020 | 1330671279 | Yes | ORLEANS | THDR | 459 | 2020-05-15 | 16524 | DIS | 25403 | 3892346761 | 1553 | ENOI | 1 | 36 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up primary | -90.1043 | 29.9472 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 5
2020 | 263 | 2020 | 1323053986 | Yes | EAST ORLEANS | FAIR | 463 | 2020-01-21 | 121769 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 263 | EPRI | Equipment Failure - Primary Conductor | N | primary wire down | -89.8028 | 30.0694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 110 | 2020 | 1323217422 | Yes | EAST ORLEANS | FAIR | 464 | 2020-01-26 | 51040 | LFUS | 27177 | 4351250071 | 1609 | ENOI | 6 | 110 | ETRD | Equipment Failure - Transformer | N | crew changed out bad transformer | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 109 | 2020 | 1330837213 | Yes | ORLEANS | FAIR | 465 | 2020-05-17 | 50685 | LFUS | 37763 | 4035847763 | 1709 | ENOI | 1 | 109 | EARM | Equipment Failure - Crossarm | N | crew replaced primary arm | -90.0586 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70116 | 5
2020 | 52 | 2020 | 1323254359 | Yes | ORLEANS | FAIR | 481 | 2020-01-27 | 25012 | XFMR | 1413671 | 3986247585 | 907 | ENOI | 1 | 52 | ETRD | Equipment Failure - Transformer | N | bad transformer changed out, good voltager now | -90.0745 | 29.9694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70116 | 1
2020 | 7 | 2020 | 1333971659 | Yes | ORLEANS | FAIR | 481 | 2020-06-28 | 3367 | XFMR | 66932 | 39168466267 | 1922 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N |  | -90.0969 | 29.9433 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 6
2020 | 109 | 2020 | 1332198679 | Yes | EAST ORLEANS | FAIR | 485 | 2020-06-03 | 52865 | LFUS | 21024 | 4046347924 | 613 | ENOI | 6 | 109 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0552 | 29.9787 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 56 | 2020 | 1332142267 | Yes | ORLEANS | FAIR | 491 | 2020-06-02 | 27496 | LFUS | 21027 | 4017847648 | 614 | ENOI | 1 | 56 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0645 | 29.9709 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70116 | 6
2020 | 23 | 2020 | 1323990854 | Yes | EAST ORLEANS | FAIR | 492 | 2020-02-15 | 11316 | LFUS | 21120 | 4107947975 | 621 | ENOI | 6 | 23 | CORR | Corrosion | N | repaired broke jumper | -90.0358 | 29.9798 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 8 | 2020 | 1329239534 | Yes | ORLEANS | THDR | 494 | 2020-04-28 | 3952 | TFUS | 71045 | 40352477036 | 1709 | ENOI | 1 | 8 | EARM | Equipment Failure - Crossarm | N | broke arm on lateral; secured; will make pink ticket to replace HW | -90.0589 | 29.9725 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70116 | 4
2020 | 48 | 2020 | 1328280581 | Yes | ORLEANS | FAIR | 500 | 2020-04-18 | 24000 | LFUS | 21404 | 3867746474 | 1554 | ENOI | 1 | 48 | LGHT | Lightning | N | found broken primary arm at 2620 joseph st. replaced primary arm. | -90.1122 | 29.9391 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 4
2020 | 68 | 2020 | 1326826003 | Yes | ORLEANS | FAIR | 501 | 2020-04-11 | 34068 | LFUS | 21484 | 3923146070 | 1924 | ENOI | 1 | 68 | EPOL | Equipment Failure - Pole | N | replaced broke pole, customers back on | -90.095 | 29.928 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 41 | 2020 | 1333005336 | Yes | EAST ORLEANS | FAIR | 501 | 2020-06-13 | 20541 | LFUS | 37097 | 4127147536 | 611 | ENOI | 6 | 41 | VHCL | Vehicle | N | CAR HIT POLE REPLACE POLE AND TRANSFORMER; RELATED TO TKT# 1333004464 (A.STEWART) | -90.0297 | 29.9676 | NP | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70117 | 6
2020 | 99 | 2020 | 1323233258 | Yes | EAST ORLEANS | FAIR | 507 | 2020-01-27 | 50193 | LFUS | 27653 | 4289350637 | 2215 | ENOI | 6 | 99 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9777 | 30.0523 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 67 | 2020 | 1334006568 | Yes | ORLEANS | FAIR | 507 | 2020-06-29 | 33969 | LFUS | 37983 | 3944047780 | 912 | ENOI | 1 | 67 | SCHD | Scheduled Interruption | N | Contractor on site working | -90.0879 | 29.975 | NP | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 6
2020 | 17 | 2020 | 1325088970 | Yes | ORLEANS | FAIR | 508 | 2020-03-05 | 8653 | DIS | 25353 | 3937145945 | 2147 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | crew on site installing new conductors | -90.0906 | 29.9245 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 43 | 2020 | 1328337701 | Yes | ORLEANS | FAIR | 508 | 2020-04-19 | 21844 | LFUS | 33236 | 38237465803 | 2014 | ENOI | 1 | 43 | EARM | Equipment Failure - Crossarm | N | dead end crossarm broken, crew changed out arm | -90.1261 | 29.9423 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 4
2020 | 46 | 2020 | 1325089224 | Yes | ORLEANS | FAIR | 513 | 2020-03-05 | 23598 | DIS | 24025 | 3942345968 | 2147 | ENOI | 1 | 46 | SCHD | Scheduled Interruption | N | crew on site installing new conductors | -90.0889 | 29.9251 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 3
2020 | 111 | 2020 | 1330669967 | Yes | EAST ORLEANS | FAIR | 520 | 2020-05-15 | 57720 | LFUS | 17870 | 4036349293 | 506 | ENOI | 6 | 111 | EARM | Equipment Failure - Crossarm | N | crew replaced broke crossarm | -90.0582 | 30.0161 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 5
2020 | 9 | 2020 | 1323084922 | Yes | EAST ORLEANS | FAIR | 524 | 2020-01-21 | 4716 | TFUS | 1315139 | 43498509515 | 2217 | ENOI | 6 | 9 | EABS | Equipment Failure - Air Break / Disconnect Switch | N |  | -89.9583 | 30.0609 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 168 | 2020 | 1329252770 | Yes | ORLEANS | THDR | 536 | 2020-04-28 | 90048 | LFUS | 27894 | 3922646091 | 1924 | ENOI | 1 | 168 | EARM | Equipment Failure - Crossarm | N | Broken corner structure at Amelia & Dryades - Crew repaired - Portion of fdr 1922 dropped out for repairs | -90.0952 | 29.9286 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 6 | 2020 | 1333061327 | Yes | ORLEANS | FAIR | 536 | 2020-06-14 | 3216 | XFMR | 51114 | 38586484379 | 407 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | replaced broken primary arms and replaced bad transformer | -90.1145 | 29.9932 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 6
2020 | 3 | 2020 | 1328246188 | Yes | ORLEANS | THDR | 543 | 2020-04-18 | 1629 | TFUS | 1256945 | 39327471365 | 1512 | ENOI | 1 | 3 | EARM | Equipment Failure - Crossarm | N | changed out broken lateral arm | -90.0915 | 29.9573 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 4
2020 | 1 | 2020 | 1328249615 | Yes | EAST ORLEANS | THDR | 543 | 2020-04-18 | 543 | TFUS | 71197 | 43234492055 | 1612 | ENOI | 6 | 1 | EPOL | Equipment Failure - Pole | N | Crew on site replacing pole | -89.9674 | 30.0129 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 31 | 2020 | 1323930361 | Yes | EAST ORLEANS | FAIR | 550 | 2020-02-13 | 17050 | LFUS | 25289 | 4290350439 | 2216 | ENOI | 6 | 31 | ETRD | Equipment Failure - Transformer | N | crew to replace underground pot | -89.9774 | 30.0469 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 45 | 2020 | 1323657975 | Yes | EAST ORLEANS | WIND | 558 | 2020-02-07 | 25110 | DIS | D01653 | 4116547515 | 2347 | ENOI | 6 | 45 | EARM | Equipment Failure - Crossarm | N | crew to replace insulator and crossarm | -90.0333 | 29.9672 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 92 | 2020 | 1328280796 | Yes | ORLEANS | RAIN | 561 | 2020-04-18 | 51612 | LFUS | 38032 | 3893546975 | 2015 | ENOI | 1 | 92 | EARM | Equipment Failure - Crossarm | N | crossarm broken changed out | -90.1038 | 29.953 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 852 | 2020 | 1325409607 | Yes | ALGIERS ELEC ONLY | FAIR | 571 | 2020-03-15 | 152002 | DIS | 5135 | 4249246144 | W1725 | ENOI | 81 | 852 | VHCL | Vehicle | N | vehicle hi pole | -89.9919 | 29.929 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | C | Council District C | Kristin Palmer | 70131 | 3
2020 | 51 | 2020 | 1323083919 | Yes | EAST ORLEANS | FAIR | 576 | 2020-01-21 | 29376 | LFUS | 24971 | 4214250165 | 2212 | ENOI | 6 | 51 | ETRD | Equipment Failure - Transformer | N | Failed padmount transformer | -90.0015 | 30.0396 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 66 | 2020 | 1323642921 | Yes | EAST ORLEANS | WIND | 578 | 2020-02-06 | 38148 | LFUS | 36787 | 4369551079 | 2217 | ENOI | 6 | 66 | ETRD | Equipment Failure - Transformer | N | Crew on site replacing transformer | -89.9522 | 30.0643 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 42 | 2020 | 1323384290 | Yes | EAST ORLEANS | FAIR | 579 | 2020-02-01 | 24318 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 42 | ETRD | Equipment Failure - Transformer | N | crew replaced | -89.9562 | 30.0596 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 134 | 2020 | 1326718187 | Yes | ORLEANS | THDR | 600 | 2020-04-10 | 80400 | LFUS | 21813 | 3928146648 | 2021 | ENOI | 1 | 134 | EPOL | Equipment Failure - Pole | N | broken pole AT S. MIRO AND 3RD ST | -90.0932 | 29.9438 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 4
2020 | 1 | 2020 | 1326047719 | Yes | EAST ORLEANS | FAIR | 617 | 2020-03-30 | 617 | TFUS | 30067 | 43767504790 | 2214 | ENOI | 6 | 1 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | replaced tie bar in underground transformer | -89.9501 | 30.0479 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 6 | 2020 | 1328296360 | Yes | ORLEANS | FAIR | 619 | 2020-04-18 | 3714 | XFMR | 1537127 | 39979478467 | 615 | ENOI | 1 | 6 | ETRD | Equipment Failure - Transformer | N | CHANGED TRANSFORMER | -90.0707 | 29.9766 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 4
2020 | 12 | 2020 | 1324391305 | Yes | EAST ORLEANS | FAIR | 639 | 2020-02-23 | 7668 | XFMR | 1373043 | 44468499346 | 1601 | ENOI | 6 | 12 | ETRD | Equipment Failure - Transformer | N |  | -89.9282 | 30.0326 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 9 | 2020 | 1323082060 | Yes | EAST ORLEANS | FAIR | 640 | 2020-01-21 | 5760 | XFMR | 1495749 | 40463475459 | 623 | ENOI | 6 | 9 | ETRD | Equipment Failure - Transformer | N | crew changedtransformer | -90.0556 | 29.9681 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 2 | 2020 | 1325378067 | Yes | ORLEANS | FAIR | 666 | 2020-03-14 | 1332 | TFUS | 73662 | 40283491759 | 1701 | ENOI | 1 | 2 | VHCL | Vehicle | N | KC | -90.0605 | 30.013 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70122 | 3
2020 | 24 | 2020 | 1323267264 | Yes | ORLEANS | FAIR | 692 | 2020-01-28 | 16608 | TFUS | 603506 | 38759464546 | 1554 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1097 | 29.9386 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 1 | 2020 | 1325216450 | Yes | EAST ORLEANS | FAIR | 698 | 2020-03-09 | 698 | DIS | 27384 | 4359850869 | 2217 | ENOI | 6 | 1 | VHCL | Vehicle | N | pole hit at gannon and morrison by vehicle RELATED TO TKT# 1325215886 (AKS) | -89.955 | 30.0581 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 3
2020 | 52 | 2020 | 1329234929 | Yes | ORLEANS | THDR | 699 | 2020-04-28 | 36348 | LFUS | 21504 | 3917546299 | 1925 | ENOI | 1 | 52 | LGHT | Lightning | N | refused lateral, out due to overnight storm, no other problems found | -90.0967 | 29.9343 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 23 | 2020 | 1330678899 | Yes | ORLEANS | THDR | 765 | 2020-05-15 | 17595 | LFUS | 27621 | 3858046356 | 1926 | ENOI | 1 | 23 | EARM | Equipment Failure - Crossarm | N | broken arm in backyard, crew in route | -90.1154 | 29.9361 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 5
2020 | 9 | 2020 | 1328276628 | Yes | ORLEANS | RAIN | 776 | 2020-04-18 | 6984 | XFMR | 57979 | 39099461768 | 1922 | ENOI | 1 | 9 | ETRD | Equipment Failure - Transformer | N | 50 kva tranformer top blew off turn in to crew case gave to 306 | -90.099 | 29.9309 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 4
2020 | 4 | 2020 | 1328286507 | Yes | ORLEANS | FAIR | 847 | 2020-04-18 | 3388 | TFUS | 23082 | 38455485577 | 410 | ENOI | 1 | 4 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.1186 | 29.9966 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 4
2020 | 58 | 2020 | 1326693036 | Yes | EAST ORLEANS | THDR | 853 | 2020-04-09 | 49474 | LFUS | 27992 | 4264649381 | 1604 | ENOI | 6 | 58 | EPOL | Equipment Failure - Pole | N | Two rotted off SCBT poles need to transfer poles already set | -89.9857 | 30.0179 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 4
2020 | 14 | 2020 | 1321631146 | Yes | ORLEANS | FAIR | 904 | 2020-01-01 | 12656 | OPEN | 3917946550 | 3917946550 | 1915 | ENOI | 1 | 14 | VHCL | Vehicle | N | car hit pole; 5 broke poles and wire down, PID chg to NO, related to #1321627546 (DGault) | -90.0964 | 29.9411 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Open | Public Damage | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 5 | 2020 | 1326732805 | Yes | EAST ORLEANS | THDR | 927 | 2020-04-09 | 4635 | OPEN | 5036554805 | 5036554805 | 1204 | ENOI | 6 | 5 | EPOL | Equipment Failure - Pole | N | 2 poles and primary down, repaired and replaced | -89.7396 | 30.1643 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Open | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 4
2020 | 1 | 2020 | 1323526696 | Yes | ORLEANS | FAIR | 1055 | 2020-02-05 | 1055 | DIS | 23962 | 3843647209 | 2024 | ENOI | 1 | 1 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1197 | 29.9594 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 1 | 2020 | 1330358845 | Yes | ORLEANS | FAIR | 1118 | 2020-05-12 | 1118 | SBKR | 1515 | 3951946983 | 1515 | ENOI | 1 | 1 | EPRI | Equipment Failure - Primary Conductor | N | Failed cable in manhole #3-1550 | -90.0855 | 29.953 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 5
2020 | 11 | 2020 | 1323525368 | Yes | ORLEANS | FAIR | 1140 | 2020-02-05 | 12540 | DIS | 23886 | 3851346971 | 2016 | ENOI | 1 | 11 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1172 | 29.9529 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 17 | 2020 | 1324472835 | Yes | ORLEANS | FAIR | 1511 | 2020-02-25 | 25687 | XFMR | 75060 | 40339473868 | 614 | ENOI | 1 | 17 | ETRD | Equipment Failure - Transformer | N | crew to replace transformer | -90.0595 | 29.9638 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70116 | 2
2020 | 12 | 2020 | 1323232466 | Yes | EAST ORLEANS | FAIR | 1673 | 2020-01-27 | 20076 | TFUS | 1313464 | 41862495089 | 1610 | ENOI | 6 | 12 | ETRD | Equipment Failure - Transformer | N | bad submersible;will be out until tomorrow morning | -90.0107 | 30.0217 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 11 | 2020 | 1324654003 | Yes | EAST ORLEANS | FAIR | 1757 | 2020-02-28 | 19327 | SWIT | 27120 | 4230549755 | 1610 | ENOI | 6 | 11 | EPRI | Equipment Failure - Primary Conductor | N | Isolated bad cable bet sw, # 25680 & 86561 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 2 | 2020 | 1332581406 | Yes | EAST ORLEANS | RAIN | 2560 | 2020-06-07 | 5120 | TFUS | 1026789 | 5038654837 | 1204 | ENOI | 6 | 2 | EPRI | Equipment Failure - Primary Conductor | N | repaired | -89.7393 | 30.1647 | NP | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 6