## NO Outage Cause Chart
Outages By Cause
ANIMAL | ANIMAL | 17 | 6.489%
CONDUCTOR | CONDUCTOR | 23 | 8.779%
EQUIPMENT | EQUIPMENT | 70 | 26.72%
HUMAN FACTORS | HUMAN FACTORS | 17 | 6.489%
LIGHTNING | LIGHTNING | 7 | 2.672%
OTHER | OTHER | 29 | 11.07%
OVERLOAD | OVERLOAD | 0 | 0%
SCHEDULED INTERRUPTIONS | Scheduled Interruption | 61 | 23.28%
STORM | STORM | 0 | 0%
SUMMARY MISSING | Summary Missing | 21 | 8.015%
VEGETATION | VEGETATION | 17 | 6.489%
TOTAL OUTAGES |  | 262

## Outage Cause Category Details
SUMMARY_CAUSE | Cause Detail
ANIMAL | Animal - Squirrel | 7
| Animal - Other (Describe in Remarks Field) | 10
ANIMAL Total |  | 17
CONDUCTOR | Secondary/Service Conductor | 9
| Slack Conductor / Inadequate Phase Spacing | 1
| Equipment - Primary Conductor | 11
| Equipment - Shield Conductor | 1
| Cable in duct | 1
CONDUCTOR Total |  | 23
EQUIPMENT | Equipment - Fuse Link | 4
| Equipment - Transformer | 19
| Equipment - Arrestor | 4
| Equipment - Pole | 6
| Equipment - Fuse Switch | 5
| Equipment - Crossarm | 18
| Equipment - Connector Sleeve | 6
| Equipment - Elbow | 1
| Equipment - Other (Describe in Remarks Field) | 4
| Equipment - Insulator | 2
| Substation Breaker - Oil | 1
EQUIPMENT Total |  | 70
HUMAN FACTORS | Human Error - Non-Entergy Workers (Describe in Remarks) | 1
| Vehicle | 14
| Contractor - Distribution Line (Describe in remarks) | 1
| Malicious Damage | 1
HUMAN FACTORS Total |  | 17
LIGHTNING | Lightning | 7
LIGHTNING Total |  | 7
OTHER | Scheduled Interruption | 61
| Inspected Unknown | 10
| Foreign Objects - Other | 4
| Emergency Switching | 8
| Unknown - Under Investigation | 4
| Mandated Outage per Public Authority (Describe in remarks) | 3
OTHER Total |  | 90
Summary Missing | Equipment - Connector / Sleeve | 21
Summary Missing Total |  | 21
VEGETATION | Overhanging Limb | 4
| Tree/Limb Growing Inside R.O.W. | 2
| Tree On Line Outside R.O.W. | 3
| Vine Growing into Line | 8
VEGETATION Total |  | 17
Grand Total |  | 262

## Outages by District & Weather
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
NAME | Weather Condition | SUMMARY_CAUSE | Cause Detail | Outage Date | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES1 | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 42
Council District B | [9 empty] | 52
Council District C | [9 empty] | 39
Council District D | [9 empty] | 69
Council District E | [9 empty] | 60
Grand Total | [9 empty] | 262

## Outages by District & Zip Code
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
NAME | ZIP | SUMMARY_CAUSE | Cause Detail | Outage Date | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES1 | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 42
Council District B | [9 empty] | 52 | NOTE: Outages that occurred outside the physical boundaries of Algiers into Gretna are grouped into zip code 70056 – Council District C, as they are serviced by feeders from Algiers.
Council District C | [9 empty] | 39
Council District D | [9 empty] | 69
Council District E | [9 empty] | 60
Grand Total | [9 empty] | 262

## Data
CASE_ID | In NOCC Reporting | NETWORK_NAME | WEATHER_CONDITION | FIRST_CALL_DATE_TIME | LAST_CALL_DATE_TIME | TROUBLE_CLEAR_TIME | FEEDER_ID | Feeder Owner | DEVICE_TYPE | DEVICE_ID | DISTRIBUTION_LOCATION_NBR | System_ | LOCAL_OFFICE_NBR | TOTAL_CUSTOMERS_AFFECTED | ACTUAL_CUSTOMER_MINUTES | TOTAL_DURATION_MINUTES1 | SUMMARY_CAUSE | CAUSE | CAUSE_DESC | MAJOR_EVENT | REMARKS | LONGITUDE | LATITUDE | ZIP | DISTRICTID | NAME | REPNAME
1304152092 | Yes | ORLEANS | RAIN | 2019-03-16 07:05 | 2019-03-16 07:05 | 2019-03-16 09:11 | 1708 | ENOI | TFUS | 669675 | 40184485263 | DLIN | 1 | 1 | 126 | 126 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | rat in cust switch gear, refused ok, advised cust jmarten | -90.0639 | 29.9953 | 70122 | D | Council District D | Joseph Giarrusso
1304058401 | Yes | ALGIERS | FAIR | 2019-03-13 20:36 | 2019-03-13 20:40 | 2019-03-13 22:51 | W1714 | ENOI | TFUS | 1235574 | 4220045164 | DLIN | 81 | 7 | 945 | 135 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | Trans. was out from small varmint that came out from under it when opened. | -90.0015 | 29.9021 | 70131 | C | Council District C | Kristin Palmer
1303068189 | Yes | ALGIERS | FAIR | 2019-02-10 02:30 | 2019-02-10 07:13 | 2019-02-10 07:46 | W1713 | ENOI | TFUS | 1281095 | 4244246034 | DLIN | 81 | 10 | 3160 | 316 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | found rat dead at base of pole,refused transformer. had to cut link out of cust chain on side gate to access yard, replaced link with entergy customer lock, left door hanger and keys to cust lock at front door truffi | -89.9936 | 29.926 | 70131 | C | Council District C | Jay Banks
1304166993 | Yes | ALGIERS | FAIR | 2019-03-17 06:31 | 2019-03-17 08:46 | 2019-03-17 09:00 | W1714 | ENOI | TFUS | 1413394 | 4252045558 | DLIN | 81 | 14 | 2086 | 149 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | found fresh dead rat at base of pole in rear. refused 100by transformer and restored power truffi1 | -89.9912 | 29.9128 | 70131 | C | Council District C | Jay Banks
1303927285 | Yes | ORLEANS | FAIR | 2019-03-10 15:34 | 2019-03-10 16:44 | 2019-03-10 19:08 | 2147 | ENOI | LFUS | 28018 | 3964845832 | DLIN | 1 | 15 | 3210 | 214 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | Crew picked up wire and are placing bad transformer. Pigeons got across transformer and fault took out lateral & feeder | -90.0819 | 29.9212 | 70115 | B | Council District B | Cyndi Nguyen
1304468223 | Yes | EAST ORLEANS | FAIR | 2019-03-30 19:22 | 2019-03-30 21:24 | 2019-03-30 22:54 | 505 | ENOI | OPEN | UNK | UNK | DLIN | 6 | 18 | 3816 | 212 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | Squirrell got into primary in cubile causing fuse to blow |  |  | 70122 | D | Council District D | Kristin Palmer
1303800046 | Yes | ORLEANS | FAIR | 2019-03-08 06:26 | 2019-03-08 07:12 | 2019-03-08 07:40 | 1712 | ENOI | TFUS | 31262 | 40262474760 | DLIN | 1 | 24 | 1752 | 73 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | taking by piegon installed animal guard refused ok jbologn | -90.0618 | 29.9662 | 70116 | C | Council District C | Jay Banks
1304479088 | Yes | EAST ORLEANS | FAIR | 2019-03-31 02:06 | 2019-03-31 02:32 | 2019-03-31 03:57 | 2214 | ENOI | LFUS | 27220 | 4339950679 | DLIN | 6 | 53 | 5883 | 111 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | Changed **LFUS 27220 197 to LFUS 27220 34** --- patrol area refuse a&b phases went back in rat took out lateral cschexn | -97.0758 | 27.9066 | 70128 | E | Council District E | Cyndi Nguyen
1304463288 | Yes | EAST ORLEANS | FAIR | 2019-03-30 15:45 | 2019-03-30 18:33 | 2019-03-30 19:03 | 505 | ENOI | LFUS | 14680 | 4040249589 | DLIN | 6 | 97 | 19109 | 197 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | refused a phase 14680 / tbrock: See Open Point case: Serviceman found a squirril got into switch vault; | -97.0758 | 27.9066 | 70122 | D | Council District D | Joseph Giarrusso
1303597123 | Yes | EAST ORLEANS | FAIR | 2019-02-28 07:45 | 2019-02-28 08:26 | 2019-02-28 08:27 | 1613 | ENOI | SBKR | 1613 | 4350949759 | DLIN | 6 | 430 | 18060 | 42 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | Crews found rat had contacted live front swicth & grounded cub tank in cub. # 229 on PLaza Dr. | -89.9585 | 30.028 | 70127 | E | Council District E | Jay Banks
1304500306 | Yes | EAST ORLEANS | FAIR | 2019-03-31 14:35 | 2019-03-31 14:45 | 2019-03-31 16:38 | 501 | ENOI | TFUS | 19011 | 41081491527 | DLIN | 6 | 3 | 369 | 123 | ANIMAL | ASQL | Animal - Squirrel | N | squerrl / refused trans.. tbrock | -90.0355 | 30.0121 | 70126 | D | Council District D | Jared Brossett
1304260681 | Yes | ALGIERS | FAIR | 2019-03-22 08:44 | 2019-03-22 08:44 | 2019-03-22 11:30 | W1726 | ENOI | TFUS | BY69644 | 4224046018 | DLIN | 81 | 4 | 664 | 166 | ANIMAL | ASQL | Animal - Squirrel | N | cleared and refused ok. back energized mtaruc | -89.9999 | 29.9256 | 70131 | C | Council District C | Jared Brossett
1302937524 | Yes | ORLEANS | FOGG | 2019-02-05 10:19 | 2019-02-05 10:23 | 2019-02-05 11:06 | 503 | ENOI | TFUS | 53102 | 40130493888 | DLIN | 1 | 6 | 282 | 47 | ANIMAL | ASQL | Animal - Squirrel | N | transformer taken out by squirrel, installed animal guard, refused ok, good volt at loc 121/121/242 jmarten | -90.0654 | 30.0189 | 70122 | D | Council District D | Cyndi Nguyen
1303069271 | Yes | ORLEANS | FAIR | 2019-02-10 08:06 | 2019-02-10 09:21 | 2019-02-10 09:44 | 406 | ENOI | TFUS | 17075 | 38928491918 | DLIN | 1 | 7 | 686 | 98 | ANIMAL | ASQL | Animal - Squirrel | N | refused 5o kva taken out by squrriel installed animal guard jbologn | -90.1034 | 30.0138 | 70124 | A | Council District A | Kristin Palmer
1303503609 | Yes | ALGIERS | FOGG | 2019-02-25 09:02 | 2019-02-25 11:11 | 2019-02-25 12:12 | W1726 | ENOI | TFUS | BY9-6655 | 4271245772 | DLIN | 81 | 9 | 1710 | 190 | ANIMAL | ASQL | Animal - Squirrel | N | back n now brizzut | -89.9851 | 29.9187 | 70131 | C | Council District C | Joseph Giarrusso
1304244850 | Yes | ALGIERS | FAIR | 2019-03-21 12:17 | 2019-03-21 13:19 | 2019-03-21 13:45 | W1713 | ENOI | TFUS | BY75265 | 4232346016 | DLIN | 81 | 16 | 1408 | 88 | ANIMAL | ASQL | Animal - Squirrel | N | found dead squirell at base of pole, refused truffi1 | -89.9973 | 29.9255 | 70131 | C | Council District C | Kristin Palmer
1304238806 | Yes | ALGIERS | FAIR | 2019-03-21 07:48 | 2019-03-21 08:28 | 2019-03-21 09:51 | W0722 | ENOI | LFUS | F06486 | 4186146001 | DLIN | 81 | 74 | 9102 | 123 | ANIMAL | ASQL | Animal - Squirrel | N | Changed **RCLR 4016 149 to LFUS 4016 39** --- squirell got across top side transformer #BY75901 blowing that fuse and lateral new lateral fuse #F06486 dloc#4187546129 installed between saint nick st and prancer st on fiesta dr, there | -90.0119 | 29.9253 | 70131 | C | Council District C | Jay Banks
1303768461 | Yes | ALGIERS | FAIR | 2019-03-07 08:06 | 2019-03-07 08:25 | 2019-03-07 09:20 | W1714 | ENOI | TFUS | BY49130 | 4249645530 | DLIN | 81 | 1 | 74 | 74 | OTHER | FOBJ | Foreign Objects - Other | N | Changed **LFUS 5602 48 to SECO BY49130 8** --- removed ballons from open wire secondary behind 6112 which cause transformer fuse to blow, not a line fuse. removed metalic ballons and refused transformer. good to go truffi1 | -89.9919 | 29.9121 | 70131 | C | Council District C | Kristin Palmer
1304307643 | NO | EAST ORLEANS | FAIR | 2019-03-24 17:45 | 2019-03-24 17:45 | 2019-03-24 17:45 | 508 | ENOI | SBKR | 508 | 4075449223 | DLIN | 6 | 479 | 0 | 0 | OTHER | FOBJ | Foreign Objects - Other | N | RSM found mettalic balloons contacted line in frt. 3020 New York St. causing fdr. to operate | -90.0457 | 30.0142 | 70126 | D | Council District D | Jared Brossett
1303445859 | NO | EAST ORLEANS | FAIR | 2019-02-23 09:35 | 2019-02-23 09:35 | 2019-02-23 09:35 | 2345 | ENOI | SBKR | 2345 | 4214847806 | DLIN | 6 | 590 | 0 | 0 | OTHER | FOBJ | Foreign Objects - Other | N | Circuit was patrolled, no problem found mylar balloons contacted priamry conductor and apparent flashover cause 2347 to trip also | -90.0022 | 29.9748 | 70117 | E | Council District E | Joseph Giarrusso
1303445944 | NO | EAST ORLEANS | FAIR | 2019-02-23 09:35 | 2019-02-23 09:35 | 2019-02-23 09:35 | 2346 | ENOI | SBKR | 2346 | 4215047805 | DLIN | 6 | 2166 | 0 | 0 | OTHER | FOBJ | Foreign Objects - Other | N | Circuit patrolled, no problem found for mylar balloons contacted primary conductor & apparent flashover caused fdr. 2345 to trip also | -90.0021 | 29.9747 | 70117 | E | Council District E | Jay Banks
1304225696 | Yes | EAST ORLEANS | FAIR | 2019-03-20 13:20 | 2019-03-20 13:37 | 2019-03-20 14:13 | 617 | ENOI | LFUS | 21818 | 4100348960 | DLIN | 6 | 59 | 3127 | 53 | HUMAN FACTORS | HNWK | Human Error - Non-Entergy Workers (Describe in Remarks) | N | A.T.&T. contractor setting new pole put pole into primary causing fuses to blow: PID was created | -90.038 | 30.0068 | 70126 | D | Council District D | Cyndi Nguyen
1303598801 | Yes | ALGIERS | FAIR | 2019-02-28 09:16 | 2019-02-28 09:16 | 2019-02-28 12:12 | W0725 | ENOI | TFUS | 607363 | 4130046427 | DLIN | 81 | 1 | 176 | 176 | LIGHTNING | LGHT | Lightning | N | weasther caused outage gcharl1 | -90.0294 | 29.9371 | 70114 | C | Council District C | Jared Brossett
1303671279 | Yes | EAST ORLEANS | THDR | 2019-03-03 14:58 | 2019-03-03 14:58 | 2019-03-03 16:59 | 616 | ENOI | TFUS | 73957 | 41821479083 | DLIN | 6 | 11 | 1331 | 121 | LIGHTNING | LGHT | Lightning | N | weather | -90.0125 | 29.9777 | 70117 | E | Council District E | Jay Banks
1303670701 | Yes | EAST ORLEANS | THDR | 2019-03-03 14:50 | 2019-03-03 16:32 | 2019-03-03 16:59 | 611 | ENOI | TFUS | 67324 | 40975475507 | DLIN | 6 | 16 | 2064 | 129 | LIGHTNING | LGHT | Lightning | N | Refused transformer taken out by bad weather jvickna | -90.0392 | 29.9681 | 70117 | C | Council District C | Joseph Giarrusso
1303670671 | Yes | EAST ORLEANS | THDR | 2019-03-03 14:46 | 2019-03-03 15:42 | 2019-03-03 16:58 | 616 | ENOI | LFUS | 62285 | 4180447921 | DLIN | 6 | 16 | 2112 | 132 | LIGHTNING | LGHT | Lightning | N | weather | -90.0131 | 29.9781 | 70117 | E | Council District E | Jay Banks
1303606513 | Yes | ORLEANS | THDR | 2019-02-28 15:53 | 2019-02-28 17:13 | 2019-02-28 17:42 | 1703 | ENOI | LFUS | 21643 | 39698485179 | DLIN | 1 | 18 | 1944 | 108 | LIGHTNING | LGHT | Lightning | N | Changed **[type] [id] 39 to LFUS 21643 18** --- taken out by weather refused ok transformer 1576904 also out due to lighning hitting phase rdeano |  |  | 70122 | D | Council District D | Jared Brossett
1303606916 | Yes | ORLEANS | THDR | 2019-02-28 16:06 | 2019-02-28 18:06 | 2019-02-28 18:26 | 1917 | ENOI | LFUS | 21083 | 3852946097 | DLIN | 1 | 18 | 2520 | 140 | LIGHTNING | LGHT | Lightning | N | taken out by lightning refused ok rdeano | -90.117 | 29.9288 | 70115 | A | Council District A | Jared Brossett
1303565243 | Yes | ORLEANS | THDR | 2019-02-27 00:05 | 2019-02-27 00:50 | 2019-02-27 02:34 | 903 | ENOI | LFUS | 21525 | 3902447856 | DLIN | 1 | 70 | 10430 | 149 | LIGHTNING | LGHT | Lightning | N | inspected ...took out by lightning refused ok rdeano | -90.1009 | 29.9772 | 70119 | A | Council District A | Joseph Giarrusso
1303936439 | Yes | EAST ORLEANS | FAIR | 2019-03-11 08:42 | 2019-03-11 08:42 | 2019-03-11 10:42 | 1607 | ENOI | TFUS | 1373124 | 42322493665 | DLIN | 6 | 1 | 120 | 120 | HUMAN FACTORS | MALD | Malicious Damage | N | stolen mtr do mtr change vemery | -89.996 | 30.0176 | 70126 | E | Council District E | Jay Banks
1304234557 | NO | ORLEANS | FAIR | 2019-03-20 22:57 | 2019-03-20 22:57 | 2019-03-20 23:01 | 2025 | ENOI | TFUS | 62283 | 39049469456 | DLIN | 1 | 19 | 76 | 4 | OTHER | MNDT | Mandated Outage per Public Authority (Describe in remarks) | N | transformer opened due to fire to make scene safe | -90.1004 | 29.952 | 70125 | B | Council District B | Jared Brossett
1303354081 | NO | ORLEANS | WIND | 2019-02-20 10:17 | 2019-02-20 11:58 | 2019-02-20 12:38 | 2132 | ENOI | DIS | 14558 | 3950246214 | DLIN | 1 | 263 | 37083 | 141 | OTHER | MNDT | Mandated Outage per Public Authority (Describe in remarks) | N | Due to a large structure fire a section of line had to be deenergized for safety. | -90.0863 | 29.9319 | 70130 | B | Council District B | Jared Brossett
1303352939 | NO | ORLEANS | WIND | 2019-02-20 09:58 | 2019-02-20 10:02 | 2019-02-20 10:01 | 2132 | ENOI | SBKR | 2132 | 4013446133 | DLIN | 1 | 3218 | 9654 | 3 | OTHER | MNDT | Mandated Outage per Public Authority (Describe in remarks) | N | had to drop this breaker due to large structure fire at this location | -90.0664 | 29.9294 | 70130 | B | Council District B | Kristin Palmer
1303387560 | Yes | ORLEANS | FAIR | 2019-02-21 15:48 | 2019-02-21 15:48 | 2019-02-21 19:44 | 1914 | ENOI | TFUS | 77769 | 38807460357 | DLIN | 1 | 12 | 2832 | 236 | VEGETATION | VOHL | Overhanging Limb | N | tree fell across lines crew to rerun service line across st charles street | -90.1083 | 29.927 | 70115 | B | Council District B | Kristin Palmer
1303930445 | Yes | ORLEANS | FAIR | 2019-03-10 21:42 | 2019-03-10 22:48 | 2019-03-10 23:05 | B0526 | ENOI | TFUS | 516909 | 38080461926 | DLIN | 1 | 16 | 1328 | 83 | VEGETATION | VOHL | Overhanging Limb | N | Changed **TFUS 516909 16 to TELE 516909 16** --- dead limb across transformer removed limb refused ok abengst | -90.1313 | 29.9317 | 70118 | A | Council District A | Joseph Giarrusso
1302939784 | Yes | ORLEANS | FOGG | 2019-02-05 12:37 | 2019-02-05 13:23 | 2019-02-05 13:49 | 2016 | ENOI | LFUS | 27826 | 3841046787 | DLIN | 1 | 22 | 1584 | 72 | VEGETATION | VOHL | Overhanging Limb | N | found b phase blown, walked out lat, found limb that fell between phase and shield, refused ok jmarten | -90.1206 | 29.9479 | 70118 | A | Council District A | Jared Brossett
1303619377 | Yes | ORLEANS | FAIR | 2019-03-01 10:29 | 2019-03-01 11:55 | 2019-03-01 11:59 | 1554 | ENOI | LFUS | 21407 | 3857446521 | DLIN | 1 | 83 | 7387 | 89 | VEGETATION | VOHL | Overhanging Limb | N | tree fell taking down primary | -90.1156 | 29.9405 | 70118 | A | Council District A | Jay Banks
1303767597 | Yes | ORLEANS | FAIR | 2019-03-07 03:17 | 2019-03-07 03:23 | 2019-03-07 05:26 | 904 | ENOI | TFUS | 72344 | 38820483956 | DLIN | 1 | 6 | 774 | 129 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | tree branch fell across top side of transformer refused ok | -90.1071 | 29.9921 | 70124 | A | Council District A | Jared Brossett
1303382331 | Yes | ORLEANS | WIND | 2019-02-21 11:25 | 2019-02-21 11:26 | 2019-02-21 12:13 | B0527 | ENOI | LFUS | 21181 | 3808446743 | DLIN | 1 | 47 | 2256 | 48 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | removed limb off B and C phase in mid span refused ok jbologn | -90.1315 | 29.9473 | 70118 | A | Council District A | Jay Banks
1303495549 | Yes | ORLEANS | WIND | 2019-02-24 15:54 | 2019-02-24 16:53 | 2019-02-24 16:51 | 1705 | ENOI | SBKR | 1705 | 4023648723 | DLIN | 1 | 2036 | 118088 | 58 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | Primary and shield wire down from tree on line at Paauger & Humanity Sts. | -90.0623 | 30.0006 | 70122 | D | Council District D | Jay Banks
1303081540 | Yes | ORLEANS | FAIR | 2019-02-11 05:33 | 2019-02-11 10:03 | 2019-02-11 10:41 | 2146 | ENOI | LFUS | 17535 | 3963546115 | DLIN | 1 | 184 | 56672 | 308 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | PICKED UP WIRE | -90.0822 | 29.929 | 70130 | B | Council District B | Jared Brossett
1303890232 | Yes | ORLEANS | WIND | 2019-03-09 16:25 | 2019-03-09 17:23 | 2019-03-09 17:22 | 903 | ENOI | LFUS | 27681 | 3889447598 | DLIN | 1 | 212 | 12084 | 57 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | load side switch (c phase) wire burnt up because wind and tree growing in ROW. repairs made apalomb | -90.1051 | 29.9701 | 70119 | A | Council District A | Jay Banks
1303932377 | Yes | ORLEANS | FAIR | 2019-03-11 04:14 | 2019-03-11 04:14 | 2019-03-11 14:28 | 1915 | ENOI | TFUS | 1206730 | 3920746564 | DLIN | 1 | 2 | 1228 | 614 | HUMAN FACTORS | VHCL | Vehicle | N | Crew to repair piping and replace 3 pot bank. Environmental called to clean up spill.- DUP TICKET# 1303932372 (AKS) | -90.0956 | 29.9416 | 70115 | B | Council District B | Cyndi Nguyen
1304327968 | Yes | ORLEANS | FAIR | 2019-03-25 07:20 | 2019-03-25 07:20 | 2019-03-25 08:50 | 1917 | ENOI | LFUS | 37032 | 3851546030 | DLIN | 1 | 4 | 360 | 90 | HUMAN FACTORS | VHCL | Vehicle | N | garbage truck hit pole, wires down **Sent to minimal claims KC** | -90.1174 | 29.9269 | 70115 | A | Council District A | Cyndi Nguyen
1302872219 | Yes | ORLEANS | FAIR | 2019-02-01 15:04 | 2019-02-01 21:02 | 2019-02-01 21:27 | 1554 | ENOI | DIS | 25325 | 3950046722 | DLIN | 1 | 12 | 4596 | 383 | HUMAN FACTORS | VHCL | Vehicle | N | pole hit and broke at Felicity and Clara *FORWARDED PID TO CLAIMS 02/05/2019* | -90.0863 | 29.9458 | 70113 | B | Council District B | Kristin Palmer
1304377704 | Yes | EAST ORLEANS | FAIR | 2019-03-27 02:36 | 2019-03-27 02:47 | 2019-03-27 03:56 | 2325 | ENOI | LFUS | 31617 | 41720475157 | DLIN | 6 | 19 | 1520 | 80 | HUMAN FACTORS | VHCL | Vehicle | N | refused transformer and lateral 31617 | -90.0159 | 29.9669 | 70117 | E | Council District E | Jay Banks
1302875062 | Yes | ORLEANS | FAIR | 2019-02-01 16:34 | 2019-02-01 20:32 | 2019-02-01 22:00 | 2021 | ENOI | LFUS | 28052 | 3949846689 | DLIN | 1 | 22 | 7172 | 326 | HUMAN FACTORS | VHCL | Vehicle | N | hit and run *FORWARDED PID TO CLAIMS 02/05/19* | -90.0863 | 29.9449 | 70113 | B | Council District B | Jared Brossett
1303622797 | Yes | EAST ORLEANS | FAIR | 2019-03-01 14:23 | 2019-03-01 15:24 | 2019-03-01 15:58 | 1604 | ENOI | LFUS | 27992 | 4264649381 | DLIN | 6 | 48 | 4560 | 95 | HUMAN FACTORS | VHCL | Vehicle | N | crew to replace pole due to vehicle accident | -89.9858 | 30.0179 | 70127 | E | Council District E | Jay Banks
1303561852 | Yes | EAST ORLEANS | FAIR | 2019-02-26 22:01 | 2019-02-26 23:05 | 2019-02-26 23:18 | 2223 | ENOI | LFUS | 23476 | 4333250949 | DLIN | 6 | 51 | 3927 | 77 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole | -89.9637 | 30.0609 | 70128 | E | Council District E | Jay Banks
1303632340 | Yes | EAST ORLEANS | FOGG | 2019-03-02 05:36 | 2019-03-02 10:01 | 2019-03-02 10:31 | 1002 | ENOI | DIS | 14536 | 4191149122 | DLIN | 6 | 79 | 23305 | 295 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole at location taking down 2 poles | -90.0062 | 30.0114 | 70126 | E | Council District E | Cyndi Nguyen
1302871839 | Yes | ORLEANS | FAIR | 2019-02-01 14:45 | 2019-02-01 19:32 | 2019-02-01 21:42 | 2135 | ENOI | DIS | 23341 | 3951946599 | DLIN | 1 | 93 | 38781 | 417 | HUMAN FACTORS | VHCL | Vehicle | N | pole hit at Felicity and Clara *FORWARDED PID TO CLAIMS ON 2/5/19 CW* | -90.0855 | 29.9424 | 70113 | B | Council District B | Cyndi Nguyen
1304384350 | Yes | EAST ORLEANS | FAIR | 2019-03-27 09:52 | 2019-03-27 09:54 | 2019-03-27 10:06 | 611 | ENOI | LFUS | 32647 | 4123847544 | DLIN | 6 | 120 | 1680 | 14 | HUMAN FACTORS | VHCL | Vehicle | N | DUP TICKET# 1304382188, 1304381644, 1304384734 (AKS) | -90.031 | 29.9678 | 70117 | D | Council District D | Jared Brossett
1303561713 | Yes | EAST ORLEANS | FAIR | 2019-02-26 21:50 | 2019-02-26 23:17 | 2019-02-26 23:19 | 2217 | ENOI | LFUS | 22155 | 4360450861 | DLIN | 6 | 141 | 12549 | 89 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole | -89.9558 | 30.0577 | 70128 | E | Council District E | Joseph Giarrusso
1303632480 | Yes | EAST ORLEANS | FOGG | 2019-03-02 06:21 | 2019-03-02 07:40 | 2019-03-02 07:57 | 1002 | ENOI | SBKR | 1002 | 4141549320 | DLIN | 6 | 255 | 24225 | 95 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole burning wire down | -90.0126 | 30.0089 | 70126 | E | Council District E | Kristin Palmer
1304177684 | NO | EAST ORLEANS | FAIR | 2019-03-17 19:21 | 2019-03-17 19:21 | 2019-03-17 19:21 | 509 | ENOI | SBKR | 509 | 4075349223 | DLIN | 6 | 552 | 0 | 0 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole | -90.0458 | 30.0142 | 70126 | D | Council District D | Cyndi Nguyen
1304177853 | NO | EAST ORLEANS | FAIR | 2019-03-17 19:21 | 2019-03-17 19:21 | 2019-03-17 19:21 | 512 | ENOI | SBKR | 512 | 4074849223 | DLIN | 6 | 1085 | 0 | 0 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole | -90.0459 | 30.0142 | 70126 | D | Council District D | Joseph Giarrusso
1303333397 | Yes | ORLEANS | RAIN | 2019-02-20 07:51 | 2019-02-20 07:51 | 2019-02-20 12:00 | 904 | ENOI | TFUS | 1417781 | 3898948457 | DLIN | 1 | 3 | 747 | 249 | VEGETATION | VINE | Vine Growing into Line | N | cleared vines off xfmr refused tsmit29 | -90.1017 | 29.9936 | 70124 | A | Council District A | Joseph Giarrusso
1304054258 | Yes | ORLEANS | FAIR | 2019-03-13 21:03 | 2019-03-13 21:03 | 2019-03-13 21:31 | 1922 | ENOI | TFUS | 1125609 | 39060467387 | DLIN | 1 | 4 | 112 | 28 | VEGETATION | VINE | Vine Growing into Line | N | cleared vines on pole jtatma1 | -90.1 | 29.9464 | 70125 | B | Council District B | Cyndi Nguyen
1303479739 | Yes | ORLEANS | THDR | 2019-02-24 00:04 | 2019-02-24 00:04 | 2019-02-24 01:14 | 2024 | ENOI | TFUS | C40822 | 38335464661 | DLIN | 1 | 4 | 280 | 70 | VEGETATION | VINE | Vine Growing into Line | N | vinies took out trans. cleared and refused ok rbiles | -90.123 | 29.9391 | 70118 | A | Council District A | Jay Banks
1304152004 | Yes | ORLEANS | RAIN | 2019-03-16 06:36 | 2019-03-16 08:51 | 2019-03-16 10:21 | 1711 | ENOI | TFUS | 55454 | 39489480518 | DLIN | 1 | 10 | 2240 | 224 | VEGETATION | VINE | Vine Growing into Line | N | refused trans ok, vines on pole and trans, need vegetation ticket jmarten **CREATED TRIM TICKET FOR FOLLOW UP ** KC | -90.086 | 29.9823 | 70119 | A | Council District A | Jared Brossett
1303241652 | Yes | ORLEANS | RAIN | 2019-02-18 09:32 | 2019-02-18 09:36 | 2019-02-18 10:04 | 911 | ENOI | TFUS | 76405 | 39138475774 | DLIN | 1 | 12 | 384 | 32 | VEGETATION | VINE | Vine Growing into Line | N | cleared vines off pole refused ok advised jbologn | -90.0973 | 29.9695 | 70119 | B | Council District B | Cyndi Nguyen
1304483292 | Yes | EAST ORLEANS | FAIR | 2019-03-31 06:07 | 2019-03-31 08:03 | 2019-03-31 08:10 | 2345 | ENOI | LFUS | 32593 | 4191747484 | DLIN | 6 | 27 | 3321 | 123 | VEGETATION | VINE | Vine Growing into Line | N | refused lat 32593/ cleared vine pole.. tbrock | -90.0095 | 29.966 | 70117 | E | Council District E | Jared Brossett
1303071597 | Yes | EAST ORLEANS | FAIR | 2019-02-10 13:20 | 2019-02-10 14:33 | 2019-02-10 14:45 | 1710 | ENOI | LFUS | 27755 | 4044648582 | DLIN | 6 | 126 | 10710 | 85 | VEGETATION | VINE | Vine Growing into Line | N | vines growing into lines in rear, removed and refused: Main lat. was restored up to sw. # 27755 | -90.0557 | 29.9965 | 70122 | D | Council District D | Jared Brossett
1303071040 | Yes | EAST ORLEANS | FAIR | 2019-02-10 11:47 | 2019-02-10 12:30 | 2019-02-10 13:20 | 1710 | ENOI | LFUS | 32033 | 4050548616 | DLIN | 6 | 191 | 17763 | 93 | VEGETATION | VINE | Vine Growing into Line | N | GVine growing into line, crew dispatched to clear pole. Laterial is back in down to Sw. 27755 | -90.0537 | 29.9975 | 70122 | D | Council District D | Cyndi Nguyen
1303958237 | Yes | ORLEANS | FAIR | 2019-03-12 06:45 | 2019-03-12 15:39 | 2019-03-12 17:12 | 406 | ENOI | TFUS | 27833 | 39256494180 | DLIN | 1 | 25 | 15675 | 627 | CONDUCTOR | CFID | Cable in duct | N | repaired elbow on submersible trans former, good volt ok jmarten | -90.0929 | 30.0201 | 70124 | D | Council District D | Cyndi Nguyen
1304242939 | Yes | ORLEANS | FAIR | 2019-03-21 11:10 | 2019-03-21 11:44 | 2019-03-21 11:40 | 903 | ENOI | SBKR | 903 | 3896847414 | DLIN | 1 | 2048 | 61440 | 30 | HUMAN FACTORS | HCDC | Contractor - Distribution Line (Describe in remarks) | N | Contractor Left Jumper on Laying on Bottom Feeder ( Feeder Lock Out While Switching to Restore to Normal Configuration ) | -90.1028 | 29.965 | 70119 | B | Council District B | Joseph Giarrusso
1303457576 | Yes | EAST ORLEANS | FAIR | 2019-02-23 12:45 | 2019-02-23 14:08 | 2019-02-23 16:02 | 622 | ENOI | DIS | 26147 | 4077948049 | DLIN | 6 | 25 | 4925 | 197 | OTHER | EMER | Emergency Switching | N | Emergency switchng to change pole. | -90.0452 | 29.9819 | 70117 | D | Council District D | Jared Brossett
1303496934 | Yes | ORLEANS | WIND | 2019-02-24 15:54 | 2019-02-24 19:29 | 2019-02-24 19:33 | 1705 | ENOI | DIS | 25281 | 4026548405 | DLIN | 1 | 45 | 10080 | 219 | OTHER | EMER | Emergency Switching | N | Equipment - Shield Conductor | -90.0613 | 29.9917 | 70122 | D | Council District D | Jared Brossett
1303457546 | Yes | EAST ORLEANS | FAIR | 2019-02-23 12:45 | 2019-02-23 16:07 | 2019-02-23 16:02 | 622 | ENOI | DIS | 25926 | 4078148133 | DLIN | 6 | 54 | 10638 | 197 | OTHER | EMER | Emergency Switching | N | Emergency switchng to replace pole damaged from car hitting it. | -90.0452 | 29.9843 | 70117 | D | Council District D | Jared Brossett
1304454076 | Yes | EAST ORLEANS | FAIR | 2019-03-29 22:15 | 2019-03-29 22:23 | 2019-03-29 22:31 | 1010 | ENOI | LFUS | 13192-F | 4145049884 | DLIN | 6 | 66 | 1056 | 16 | OTHER | EMER | Emergency Switching | N | crew took lateral out for safety to make repairs in a submersible | -90.0234 | 30.032 | 70126 | E | Council District E | Joseph Giarrusso
1303307994 | NO | EAST ORLEANS | FAIR | 2019-02-19 21:51 | 2019-02-19 23:33 | 2019-02-19 21:51 | 1603 | ENOI | SWIT | 27031 | 4264749966 | DLIN | 6 | 99 | 0 | 0 | OTHER | EMER | Emergency Switching | N | Followup crew found cub 205 all flashed up | -97.0758 | 27.9066 | 70127 | E | Council District E | Jay Banks
1303308503 | Yes | EAST ORLEANS | FAIR | 2019-02-19 21:51 | 2019-02-19 21:51 | 2019-02-19 23:50 | 1603 | ENOI | SWIT | 27024 | 4264749966 | DLIN | 6 | 99 | 11781 | 119 | OTHER | EMER | Emergency Switching | N | Inspected Unknown did not find anything | -97.0758 | 27.9066 | 70127 | E | Council District E | Kristin Palmer
1302878377 | Yes | ORLEANS | FAIR | 2019-02-01 21:06 | 2019-02-01 22:08 | 2019-02-01 22:10 | 2025 | ENOI | DIS | 23116 | 3913547330 | DLIN | 1 | 167 | 10688 | 64 | OTHER | EMER | Emergency Switching | N | Emergency Switching | -90.0974 | 29.9625 | 70119 | B | Council District B | Jay Banks
1303498072 | Yes | ORLEANS | WIND | 2019-02-24 17:58 | 2019-02-24 18:59 | 2019-02-24 19:08 | 1708 | ENOI | LFUS | 27677 | 4025648435 | DLIN | 1 | 176 | 12320 | 70 | OTHER | EMER | Emergency Switching | N | drop out line to pick up sheld : See Fdr. 1705 outage case | -90.0618 | 29.9927 | 70122 | D | Council District D | Jay Banks
1303922196 | Yes | EAST ORLEANS | FAIR | 2019-03-10 12:07 | 2019-03-10 12:45 | 2019-03-10 13:08 | 2212 | ENOI | LFUS | 25183 | 4224550149 | DLIN | 6 | 32 | 1952 | 61 | EQUIPMENT | EARR | Equipment - Arrestor | N | fnd c phase blown bc of failed arrestor on load side of sw-25183-cleared arrestor and re-fused ok-custs back on swalsh1 3-10-19 swalsh1 | -89.9982 | 30.0392 | 70127 | E | Council District E | Jared Brossett
1303315155 | Yes | EAST ORLEANS | FOGG | 2019-02-20 01:05 | 2019-02-20 01:45 | 2019-02-20 02:01 | 1607 | ENOI | LFUS | 34358 | 4208549276 | DLIN | 6 | 41 | 2296 | 56 | EQUIPMENT | EARR | Equipment - Arrestor | N | found blown arrestor at location. cleared and refused A phase. dwillin | -90.0037 | 30.0153 | 70126 | E | Council District E | Joseph Giarrusso
1303368747 | Yes | EAST ORLEANS | FAIR | 2019-02-20 18:29 | 2019-02-20 19:02 | 2019-02-20 19:50 | 2346 | ENOI | LFUS | 34975 | 4151047208 | DLIN | 6 | 41 | 3321 | 81 | EQUIPMENT | EARR | Equipment - Arrestor | N | Changed **LFUS 34975 64 to LFUS 34975 40** --- cleared arestor/ refused b phase.. tbrock | -90.0226 | 29.9585 | 70117 | E | Council District E | Jay Banks
1303300921 | Yes | EAST ORLEANS | FAIR | 2019-02-19 20:56 | 2019-02-20 01:07 | 2019-02-20 01:10 | 611 | ENOI | LFUS | 28077 | 4115047686 | DLIN | 6 | 113 | 28702 | 254 | EQUIPMENT | EARR | Equipment - Arrestor | N | B phase only | -90.0337 | 29.9718 | 70117 | D | Council District D | Jay Banks
1302924663 | Yes | ORLEANS | FAIR | 2019-02-04 17:10 | 2019-02-04 17:10 | 2019-02-04 17:55 | 1513 | ENOI | SECO | SECONDARY | 39446475774 | DLIN | 1 | 1 | 45 | 45 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 69592 * 5 to SECO 69592 * [count]** --- bad connection changed out connection at pole treed3 | -90.0876 | 29.9694 | 70119 | B | Council District B | Cyndi Nguyen
1303193220 | Yes | ORLEANS | FAIR | 2019-02-15 10:54 | 2019-02-15 10:54 | 2019-02-15 11:42 | 1709 | ENOI | SERV | SERVICE | 40273479205 | DLIN | 1 | 1 | 48 | 48 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | connector burnt at pole replaced. apalomb | -90.0613 | 29.9785 | 70119 | D | Council District D | Joseph Giarrusso
1303809762 | Yes | ORLEANS | FAIR | 2019-03-08 17:03 | 2019-03-08 17:09 | 2019-03-08 18:07 | 912_2 | ENOI | SERV | SERVICE | 39473478021 | DLIN | 1 | 1 | 64 | 64 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 70660 13 to SERV 70660 13** --- bad connection at pole abengst | -90.0866 | 29.9755 | 70119 | A | Council District A | Joseph Giarrusso
1303742151 | Yes | ORLEANS | COLD | 2019-03-05 19:20 | 2019-03-05 19:22 | 2019-03-05 20:29 | 2026 | ENOI | SERV | SERVICE | 38777478355 | DLIN | 1 | 1 | 69 | 69 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1585793 17 to SERV 1585793 17** --- bad connection at pole abengst | -90.1087 | 29.9767 | 70119 | A | Council District A | Jay Banks
1302968284 | Yes | EAST ORLEANS | FAIR | 2019-02-06 18:26 | 2019-02-06 18:26 | 2019-02-06 19:43 | 503 | ENOI | SERV | SERVICE | 40317495183 | DLIN | 6 | 1 | 77 | 77 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1190144 11 to SERV 1190144 3** --- Replaced hot leg connection feeding open wire secondary jvickna | -90.0594 | 30.0224 | 70122 | D | Council District D | Jared Brossett
1303764285 | Yes | EAST ORLEANS | FAIR | 2019-03-06 17:55 | 2019-03-06 18:29 | 2019-03-06 19:23 | 611 | ENOI | SERV | SERVICE | 4095947693 | DLIN | 6 | 1 | 87 | 87 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | hanged hot leg conect on pole tbrock | -90.0398 | 29.972 | 70117 | D | Council District D | Cyndi Nguyen
1303020622 | Yes | EAST ORLEANS | FAIR | 2019-02-07 15:57 | 2019-02-07 15:57 | 2019-02-07 17:32 | 622 | ENOI | SERV | SERVICE | 40727478728 | DLIN | 6 | 1 | 95 | 95 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 57215 8 to SERV 57215 8** --- Replaced hot leg connector at wilson rack jvickna | -90.0471 | 29.977 | 70117 | D | Council District D | Cyndi Nguyen
1302949266 | Yes | EAST ORLEANS | FAIR | 2019-02-05 23:47 | 2019-02-05 23:47 | 2019-02-06 01:26 | 506 | ENOI | SERV | SERVICE | 40543494852 | DLIN | 6 | 1 | 99 | 99 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1374954 * 14 to TFUS 1374954 * 1** --- Replaced hot leg connector at pole jvickna | -90.0523 | 30.0215 | 70122 | D | Council District D | Cyndi Nguyen
1303764385 | Yes | EAST ORLEANS | FAIR | 2019-03-06 18:02 | 2019-03-06 19:28 | 2019-03-06 19:45 | 613 | ENOI | LFUS | 96847 | 4054447943 | DLIN | 6 | 1 | 103 | 103 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | refused b phase lat / wood from x arm fell off.. tbrock | -90.0529 | 29.979 | 70117 | D | Council District D | Cyndi Nguyen
1303476538 | Yes | EAST ORLEANS | RAIN | 2019-02-23 20:43 | 2019-02-23 20:43 | 2019-02-23 23:00 | 1710 | ENOI | SERV | SERVICE | 4055748547 | DLIN | 6 | 1 | 137 | 137 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1027414 9 to SERV 1027414 9** --- service burned up in tree spliced out good voltage dfahr | -90.0523 | 29.9956 | 70122 | D | Council District D | Joseph Giarrusso
1303762709 | Yes | ORLEANS | COLD | 2019-03-06 16:03 | 2019-03-06 16:03 | 2019-03-06 18:25 | 1915 | ENOI | SERV | SERVICE | 39382466830 | DLIN | 1 | 1 | 142 | 142 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1231431 2 to SECO 1231431 2** --- bad connection at pole abengst | -90.09 | 29.9448 | 70113 | B | Council District B | Jay Banks
1303741488 | Yes | EAST ORLEANS | FAIR | 2019-03-05 18:32 | 2019-03-05 18:41 | 2019-03-05 21:03 | 1204 | ENOI | SECO | SERVICE | 48018512868 | DLIN | 6 | 1 | 151 | 151 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | changed sec upc block in handhole.. tbrock | -89.8154 | 30.0685 | 70129 | E | Council District E | Jay Banks
1303756083 | Yes | EAST ORLEANS | FAIR | 2019-03-06 10:46 | 2019-03-06 10:46 | 2019-03-06 13:43 | 1601 | ENOI | SERV | SERVICE | 43776496253 | DLIN | 6 | 1 | 177 | 177 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1601971 7 to SERV 1601971 1** --- bad hot leg connection in handhole-changed connection-voltage ok- cust back on swalsh1 3-6-19 swalsh1 | -89.95 | 30.0243 | 70128 | E | Council District E | Jay Banks
1304246669 | Yes | ORLEANS | FAIR | 2019-03-21 13:52 | 2019-03-21 13:52 | 2019-03-21 16:50 | 2135 | ENOI | SERV | SERVICE | 39936462104 | DLIN | 1 | 1 | 178 | 178 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1006925 * 10 to SERV 1006925 * [count]** --- changed burnt connection at pole no lights out tsmit29 | -90.0726 | 29.9316 | 70130 | B | Council District B | Cyndi Nguyen
1303148666 | Yes | EAST ORLEANS | FAIR | 2019-02-13 13:58 | 2019-02-13 13:58 | 2019-02-13 16:58 | 2217 | ENOI | SERV | SERVICE | 44005512350 | DLIN | 6 | 1 | 180 | 180 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 527083 4 to SERV 527083 1** --- hot leg connection bad in transformer vault-changed connection-voltage ok-cust back on swalsh1 2-13-19 swalsh1 | -89.9424 | 30.0686 | 70128 | E | Council District E | Cyndi Nguyen
1304198778 | Yes | EAST ORLEANS | FAIR | 2019-03-19 05:50 | 2019-03-19 08:25 | 2019-03-19 10:41 | 2211 | ENOI | SERV | SERVICE | 42125497849 | DLIN | 6 | 1 | 291 | 291 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1373122 5 to TFUS 1373122 1** --- Had to repair hot leg in vault, customer back in lights mjack11 | -90.0021 | 30.0292 | 70126 | E | Council District E | Cyndi Nguyen
1303969329 | Yes | ORLEANS | FAIR | 2019-03-12 11:41 | 2019-03-12 11:41 | 2019-03-12 17:15 | 1512 | ENOI | SERV | SERVICE | 3992647384 | DLIN | 1 | 1 | 334 | 334 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | hot leg burned up at weatherhead. repaired hot leg, good voltage now jtatma1 | -90.0725 | 29.9639 | 70116 | C | Council District C | Joseph Giarrusso
1303155804 | Yes | ORLEANS | FAIR | 2019-02-14 04:26 | 2019-02-14 07:38 | 2019-02-14 12:37 | 1704 | ENOI | SERV | SERVICE | 40081489539 | DLIN | 1 | 1 | 491 | 491 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | service line burnt down replaced service line with 1awg apalomb | -90.067 | 30.007 | 70122 | D | Council District D | Jay Banks
1303158970 | Yes | ORLEANS | FAIR | 2019-02-14 07:59 | 2019-02-14 15:33 | 2019-02-14 16:48 | 2013 | ENOI | SERV | SERVICE | 38069463282 | DLIN | 1 | 1 | 529 | 529 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | burnt connection at weatherhead replaced apalomb | -90.1315 | 29.9354 | 70118 | A | Council District A | Joseph Giarrusso
1302947893 | Yes | EAST ORLEANS | FAIR | 2019-02-05 19:20 | 2019-02-05 19:20 | 2019-02-05 20:27 | 1610 | ENOI | TFUS | 1048691 | 42270496982 | DLIN | 6 | 3 | 201 | 67 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Replaced upc on hot leg in transformer vault jvickna | -89.9977 | 30.0267 | 70126 | E | Council District E | Jay Banks
1304396266 | Yes | ORLEANS | FAIR | 2019-03-27 17:00 | 2019-03-27 17:36 | 2019-03-27 17:27 | 627 | ENOI | LFUS | 27727 | 4029748047 | DLIN | 1 | 142 | 3834 | 27 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **LFUS 27727 139 to LFUS 27727 20** --- riser came out the bottom of one latteral switch made repair everyone back in lights gkathma | -90.0605 | 29.982 | 70119 | D | Council District D | Jared Brossett
1304202045 | Yes | ORLEANS | FAIR | 2019-03-19 09:54 | 2019-03-19 09:54 | 2019-03-19 11:25 | 2026 | ENOI | SERV | SERVICE | 38949477586 | DLIN | 1 | 1 | 91 | 91 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | repaired bad connection at pole, good volt 121/121/242, need vegetation ticket to cut tree growing into pole and blocking access to wilson rack *MADETRIMTICKET* | -90.1033 | 29.9745 | 70119 | A | Council District A | Cyndi Nguyen
1304097599 | Yes | ORLEANS | FAIR | 2019-03-14 11:28 | 2019-03-14 11:28 | 2019-03-14 13:23 | 512 | ENOI | SERV | SERVICE | 40221490597 | DLIN | 1 | 1 | 115 | 115 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | connector burnt at pole replaced apalomb | -90.0625 | 30.0098 | 70122 | D | Council District D | Cyndi Nguyen
1304234913 | Yes | EAST ORLEANS | FAIR | 2019-03-20 23:46 | 2019-03-20 23:46 | 2019-03-21 01:45 | 1702 | ENOI | SERV | SERVICE | 40331490381 | DLIN | 6 | 1 | 119 | 119 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | bad hot leg repaired on pole | -90.0592 | 30.0092 | 70122 | D | Council District D | Joseph Giarrusso
1304155659 | Yes | EAST ORLEANS | FAIR | 2019-03-16 10:51 | 2019-03-16 10:59 | 2019-03-16 12:48 | 1612 | ENOI | TFUS | 1340890 | 43501496924 | DLIN | 6 | 7 | 819 | 117 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | riser burned off switch waited for backup to repair/good voltage dfahr | -89.9588 | 30.0262 | 70127 | E | Council District E | Jared Brossett
1304479098 | Yes | EAST ORLEANS | THDR | 2019-03-31 02:06 | 2019-03-31 04:34 | 2019-03-31 05:21 | 2212 | ENOI | LFUS | 24972 | 4199150097 | DLIN | 6 | 55 | 22815 | 195 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | top riser broken on lateral switch call crew oh protion b phase opened switch cschexn | -90.0064 | 30.0378 | 70126 | E | Council District E | Jared Brossett
1303214158 | Yes | ORLEANS | FAIR | 2019-02-16 11:56 | 2019-02-16 12:22 | 2019-02-16 13:00 | B0527 | ENOI | LFUS | 21179 | 3800746955 | DLIN | 1 | 83 | 5312 | 64 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | Phase burned down by connections at Monroe & Willow Sts. | -90.1333 | 29.9528 | 70118 | A | Council District A | Jared Brossett
1304498789 | Yes | ORLEANS | FAIR | 2019-03-31 12:48 | 2019-03-31 12:48 | 2019-03-31 20:00 | 2027 | ENOI | TFUS | 1051894 | 38603471406 | DLIN | 1 | 1 | 432 | 432 | EQUIPMENT | EARM | Equipment - Crossarm | N | secondary arm | -90.1144 | 29.9576 | 70125 | B | Council District B | Joseph Giarrusso
1304375588 | Yes | ORLEANS | FAIR | 2019-03-26 20:03 | 2019-03-26 20:03 | 2019-03-26 22:35 | 512 | ENOI | TFUS | 53843 | 39674491682 | DLIN | 1 | 3 | 456 | 152 | EQUIPMENT | EARM | Equipment - Crossarm | N | making repairs to broken cross arm | -90.0799 | 30.0131 | 70122 | D | Council District D | Cyndi Nguyen
1303275720 | Yes | ORLEANS | FAIR | 2019-02-19 12:19 | 2019-02-19 12:19 | 2019-02-19 14:01 | 1513 | ENOI | TFUS | 62331 | 39476476499 | DLIN | 1 | 8 | 816 | 102 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.0866 | 29.9713 | 70119 | A | Council District A | Cyndi Nguyen
1303235879 | Yes | ORLEANS | FAIR | 2019-02-18 01:26 | 2019-02-18 02:05 | 2019-02-18 03:10 | 1923 | ENOI | TFUS | 58684 | 39221459548 | DLIN | 1 | 11 | 1144 | 104 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.0953 | 29.9248 | 70115 | B | Council District B | Jared Brossett
1304282670 | Yes | ORLEANS | FAIR | 2019-03-23 13:48 | 2019-03-23 14:12 | 2019-03-23 16:30 | 1917 | ENOI | TFUS | 77721 | 38759458502 | DLIN | 1 | 14 | 2268 | 162 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to replace switch arm | -90.11 | 29.9221 | 70115 | B | Council District B | Jared Brossett
1304309582 | Yes | ORLEANS | FAIR | 2019-03-24 09:40 | 2019-03-24 09:40 | 2019-03-24 23:16 | 1711 | ENOI | TFUS | 1497802 | 39587479855 | DLIN | 1 | 15 | 12240 | 816 | EQUIPMENT | EARM | Equipment - Crossarm | N | bad wilson rack | -90.083 | 29.9804 | 70119 | A | Council District A | Kristin Palmer
1303234966 | Yes | ORLEANS | FAIR | 2019-02-17 21:38 | 2019-02-17 21:53 | 2019-02-18 03:09 | 1923 | ENOI | TFUS | 1394002 | 39235459460 | DLIN | 1 | 16 | 5296 | 331 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to repair broken crossarms | -90.0949 | 29.9245 | 70115 | B | Council District B | Jared Brossett
1303193595 | Yes | ORLEANS | FAIR | 2019-02-15 11:16 | 2019-02-15 11:21 | 2019-02-15 11:48 | 907 | ENOI | TFUS | 56948 | 39675476356 | DLIN | 1 | 21 | 672 | 32 | EQUIPMENT | EARM | Equipment - Crossarm | N | broken wilson rack in trees | -90.0804 | 29.9709 | 70119 | D | Council District D | Jared Brossett
1303217896 | Yes | ORLEANS | FAIR | 2019-02-16 15:43 | 2019-02-16 15:54 | 2019-02-16 16:57 | 2146 | ENOI | TFUS | 729628 | 39681459752 | DLIN | 1 | 21 | 1554 | 74 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew changed out wilson rack | -90.0807 | 29.9253 | 70130 | B | Council District B | Jared Brossett
1303912658 | Yes | ORLEANS | FAIR | 2019-03-10 01:00 | 2019-03-10 04:48 | 2019-03-10 05:25 | 510 | ENOI | LFUS | 17892 | 3986149301 | DLIN | 1 | 32 | 8480 | 265 | EQUIPMENT | EARM | Equipment - Crossarm | N | Crew case for broke primary arm | -90.074 | 30.0165 | 70122 | D | Council District D | Joseph Giarrusso
1303191307 | Yes | EAST ORLEANS | FAIR | 2019-02-15 09:18 | 2019-02-15 09:35 | 2019-02-15 10:01 | 2346 | ENOI | LFUS | 31781 | 4156147172 | DLIN | 6 | 34 | 1462 | 43 | EQUIPMENT | EARM | Equipment - Crossarm | N | broken cross arm crew making repairs | -90.021 | 29.9576 | 70117 | E | Council District E | Joseph Giarrusso
1303602464 | Yes | EAST ORLEANS | FAIR | 2019-02-28 12:50 | 2019-02-28 13:22 | 2019-02-28 14:00 | 506 | ENOI | LFUS | 17858 | 4047049301 | DLIN | 6 | 41 | 2870 | 70 | EQUIPMENT | EARM | Equipment - Crossarm | N | Crew to replace crossarm | -90.0547 | 30.0164 | 70122 | D | Council District D | Cyndi Nguyen
1303212704 | Yes | EAST ORLEANS | FOGG | 2019-02-16 09:19 | 2019-02-16 09:32 | 2019-02-16 09:54 | 613 | ENOI | LFUS | 21024 | 4046347924 | DLIN | 6 | 57 | 1995 | 35 | EQUIPMENT | EARM | Equipment - Crossarm | N | call crew Dudley Grady switch arm needs to be replaced broken arm cschexn | -90.0553 | 29.9786 | 70117 | D | Council District D | Kristin Palmer
1303568078 | Yes | ORLEANS | THDR | 2019-02-27 02:09 | 2019-02-27 02:09 | 2019-02-27 05:57 | 1712 | ENOI | DIS | 23629 | 4039547670 | DLIN | 1 | 64 | 14592 | 228 | EQUIPMENT | EARM | Equipment - Crossarm | N | WEATHER CREW TO REPLACE CROSSARM | -90.0574 | 29.9715 | 70116 | C | Council District C | Cyndi Nguyen
1303625846 | Yes | ORLEANS | FAIR | 2019-03-01 15:46 | 2019-03-01 16:09 | 2019-03-01 16:38 | 1513 | ENOI | LFUS | 21320 | 3953747706 | DLIN | 1 | 93 | 4836 | 52 | EQUIPMENT | EARM | Equipment - Crossarm | N | crossarm braces broke put new braces on and straighterned arm refused A phase rdeano | -90.0845 | 29.9728 | 70119 | A | Council District A | Jay Banks
1303274517 | Yes | ORLEANS | FAIR | 2019-02-19 12:19 | 2019-02-19 12:38 | 2019-02-19 13:18 | 1513 | ENOI | LFUS | 21243 | 3949247646 | DLIN | 1 | 127 | 7493 | 59 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.0861 | 29.9711 | 70119 | A | Council District A | Jay Banks
1303495017 | Yes | EAST ORLEANS | FAIR | 2019-02-24 15:04 | 2019-02-24 15:24 | 2019-02-24 17:51 | 623 | ENOI | LFUS | 27777 | 4085447421 | DLIN | 6 | 145 | 24215 | 167 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew repaired arm | -90.0433 | 29.9647 | 70117 | C | Council District C | Jared Brossett
1303565293 | Yes | ORLEANS | THDR | 2019-02-27 00:10 | 2019-02-27 05:16 | 2019-02-27 05:57 | 614 | ENOI | RCLR | 24010 | 4040047678 | DLIN | 1 | 2308 | 308046 | 347 | EQUIPMENT | EARM | Equipment - Crossarm | N | CROSS ARM BROKEN DUE TO WEATHER IN AREA | -90.0573 | 29.9718 | 70116 | C | Council District C | Cyndi Nguyen
1303965577 | Yes | ORLEANS | FAIR | 2019-03-12 10:31 | 2019-03-12 11:42 | 2019-03-12 13:50 | 407 | ENOI | LFUS | 14872 | 3841548350 | DLIN | 1 | 13 | 2587 | 199 | EQUIPMENT | EELB | Equipment - Elbow | N | changed primary elbow | -90.1199 | 29.9909 | 70124 | A | Council District A | Cyndi Nguyen
1304341567 | Yes | ORLEANS | FAIR | 2019-03-25 13:22 | 2019-03-25 14:08 | 2019-03-25 15:04 | 1917 | ENOI | LFUS | F05722 | 3850745998 | DLIN | 1 | 8 | 816 | 102 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused B phase on main lat. 25666 old fuse link broke jbologn | -90.1177 | 29.9261 | 70115 | A | Council District A | Joseph Giarrusso
1303111842 | Yes | EAST ORLEANS | THDR | 2019-02-12 08:37 | 2019-02-12 09:02 | 2019-02-12 09:20 | 1601 | ENOI | LFUS | 27281 | 4377749595 | DLIN | 6 | 23 | 989 | 43 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused ok B phase cbowden | -89.95 | 30.0234 | 70128 | E | Council District E | Kristin Palmer
1304437793 | Yes | ALGIERS | FAIR | 2019-03-29 08:18 | 2019-03-29 08:47 | 2019-03-29 11:02 | W1715 | ENOI | LFUS | 93149 | 4451845424 | DLIN | 81 | 33 | 5412 | 164 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **LFUS 93149 33 to LFUS 93149 17** --- 50 amp fuse link gcharl1 | -89.9283 | 29.9086 | 70131 | C | Council District C | Jay Banks
1303571215 | Yes | ORLEANS | FAIR | 2019-02-27 07:29 | 2019-02-27 07:34 | 2019-02-27 08:58 | 907 | ENOI | LFUS | 38003 | 3986247643 | DLIN | 1 | 223 | 19624 | 88 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | blown lattural fuse refused ok apalomb | -90.0743 | 29.971 | 70116 | D | Council District D | Kristin Palmer
1304499242 | Yes | ORLEANS | FAIR | 2019-03-31 13:22 | 2019-03-31 16:01 | 2019-03-31 17:46 | 1512 | ENOI | TFUS | 1391870 | 39791472220 | DLIN | 1 | 3 | 792 | 264 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | crew needs to replace switch | -90.0768 | 29.9596 | 70112 | B | Council District B | Jared Brossett
1303213508 | Yes | EAST ORLEANS | FAIR | 2019-02-16 10:42 | 2019-02-16 11:51 | 2019-02-16 12:19 | 613 | ENOI | LFUS | 42889 | 4046247935 | DLIN | 6 | 12 | 1164 | 97 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | crew replaced fuse switch | -90.0553 | 29.9788 | 70117 | D | Council District D | Jared Brossett
1303286444 | Yes | ORLEANS | FAIR | 2019-02-19 16:29 | 2019-02-19 18:06 | 2019-02-19 19:16 | 2132 | ENOI | TFUS | 1078947 | 39998461534 | DLIN | 1 | 16 | 2672 | 167 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | bad switch | -90.0707 | 29.93 | 70130 | B | Council District B | Kristin Palmer
1303213133 | Yes | EAST ORLEANS | FAIR | 2019-02-16 10:00 | 2019-02-16 11:03 | 2019-02-16 12:19 | 613 | ENOI | LFUS | 21024 | 4046347924 | DLIN | 6 | 29 | 4031 | 139 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | crew is on way to replace switch | -90.0553 | 29.9786 | 70117 | D | Council District D | Jared Brossett
1304306667 | NO | ALGIERS | FAIR | 2019-03-24 17:04 | 2019-03-24 17:04 | 2019-03-24 17:05 | W0713 | ENOI | SBKR | W0713 | 4173945845 | DLIN | 81 | 2638 | 0 | 0 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | Disconnect flashed over when serviceman was closing pole dip. Breaker is in and everything is okay. | -90.0158 | 29.921 | 70114 | C | Council District C | Jay Banks
1303934571 | Yes | EAST ORLEANS | FOGG | 2019-03-11 07:05 | 2019-03-11 07:47 | 2019-03-11 08:16 | 626 | ENOI | LFUS | 27140-F | 4089848388 | DLIN | 6 | 39 | 2730 | 70 | EQUIPMENT | EINS | Equipment - Insulator | N | found b phase blown on sw-21213-one span to river of sw-21213 b phase insulator tracking/arm burned-refused lateral ok-custs back on-turning in ticket for crew to change arm swalsh1 3-11-19 swalsh1 | -90.0414 | 29.9912 | 70126 | D | Council District D | Jay Banks
1302878053 | Yes | ORLEANS | FAIR | 2019-02-01 20:26 | 2019-02-01 21:04 | 2019-02-01 21:07 | 2025 | ENOI | SBKR | 2025 | 3847947391 | DLIN | 1 | 446 | 17840 | 40 | EQUIPMENT | EINS | Equipment - Insulator | N | Washington ve. & Genois St. Crews found a damaged insulator: Network will make repairs on Monday ***PER J. DOMANGUE REPAIRS COMPLETED ON 2/28/19 KC*** | -90.1182 | 29.9645 | 70118 | A | Council District A | Cyndi Nguyen
1302886365 | Yes | EAST ORLEANS | FAIR | 2019-02-02 08:52 | 2019-02-02 08:52 | 2019-02-02 08:58 | 617 | ENOI | TFUS | 61176 | 41002490412 | DLIN | 6 | 11 | 66 | 6 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | repaired lead on transformer | -90.0379 | 30.0092 | 70126 | D | Council District D | Kristin Palmer
1303240529 | Yes | ORLEANS | RAIN | 2019-02-18 09:18 | 2019-02-18 09:19 | 2019-02-18 10:36 | 2147 | ENOI | TFUS | 1000462 | 39789459299 | DLIN | 1 | 11 | 858 | 78 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | animal guard bad tracking replaced refused ok advised jbologn | -90.0774 | 29.9238 | 70130 | B | Council District B | Jared Brossett
1303303894 | Yes | EAST ORLEANS | FAIR | 2019-02-19 21:52 | 2019-02-19 23:07 | 2019-02-19 23:07 | 1603 | ENOI | SBKR | 1603 | 4351349756 | DLIN | 6 | 158 | 11850 | 75 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | RSM found sw. cubicle #205 bay 4 all flashed up | -89.9583 | 30.0279 | 70127 | E | Council District E | Jared Brossett
1303382237 | Yes | EAST ORLEANS | FAIR | 2019-02-21 11:24 | 2019-02-21 12:03 | 2019-02-21 12:09 | 1602 | ENOI | VFI | 38268 | 4264649768 | DLIN | 6 | 375 | 16875 | 45 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | closed VFI : RSM found insulator tracking over & flashed in cub #3 | -97.0758 | 27.9066 | 70127 | E | Council District E | Joseph Giarrusso
1303135095 | Yes | ORLEANS | FAIR | 2019-02-13 01:14 | 2019-02-13 01:14 | 2019-02-13 06:31 | 1553 | ENOI | XFMR | 3937446988 | 3937446988 | DLIN | 1 | 1 | 317 | 317 | EQUIPMENT | EPOL | Equipment - Pole | N | Equipment - Pole | -90.0901 | 29.9531 | 70125 | B | Council District B | Cyndi Nguyen
1303798618 | Yes | ORLEANS | FAIR | 2019-03-08 03:00 | 2019-03-08 03:00 | 2019-03-08 04:43 | 1704 | ENOI | TFUS | 1256337 | 3962748823 | DLIN | 1 | 4 | 412 | 103 | EQUIPMENT | EPOL | Equipment - Pole | N |  | -90.0815 | 30.0034 | 70122 | D | Council District D | Joseph Giarrusso
1303481316 | Yes | EAST ORLEANS | FAIR | 2019-02-24 01:37 | 2019-02-24 02:09 | 2019-02-24 02:16 | 2217 | ENOI | LFUS | 26048 | 4353050960 | DLIN | 6 | 19 | 741 | 39 | EQUIPMENT | EPOL | Equipment - Pole | N | CREW STRIGHTING POLE | -89.9574 | 30.061 | 70128 | E | Council District E | Cyndi Nguyen
1303674126 | Yes | EAST ORLEANS | FAIR | 2019-03-03 17:25 | 2019-03-03 17:36 | 2019-03-03 18:05 | 2325 | ENOI | LFUS | 38218 | 4178847684 | DLIN | 6 | 21 | 840 | 40 | EQUIPMENT | EPOL | Equipment - Pole | N | crew on site to stubb rotten pole and local office will replace at later date (pwd) | -90.0135 | 29.9716 | 70117 | E | Council District E | Joseph Giarrusso
1303481643 | Yes | EAST ORLEANS | FAIR | 2019-02-24 01:55 | 2019-02-24 02:05 | 2019-02-24 02:16 | 2223 | ENOI | LFUS | 24738 | 4346351051 | DLIN | 6 | 57 | 1197 | 21 | EQUIPMENT | EPOL | Equipment - Pole | N | DROP OUT L/FUSE TO STRIGHTON POLE | -89.9595 | 30.0635 | 70128 | E | Council District E | Cyndi Nguyen
1303500243 | Yes | ORLEANS | FAIR | 2019-02-24 22:02 | 2019-02-24 22:28 | 2019-02-25 01:35 | 2014 | ENOI | LFUS | 28102 | 3828046542 | DLIN | 1 | 75 | 15975 | 213 | EQUIPMENT | EPOL | Equipment - Pole | N | Equipment - Pole drop out l28102 to replace pole | -90.1248 | 29.9413 | 70118 | A | Council District A | Cyndi Nguyen
1304412368 | Yes | ORLEANS | FAIR | 2019-03-28 10:06 | 2019-03-28 10:06 | 2019-03-28 12:39 | 1553 | ENOI | TFUS | 1095766 | 39228470646 | DLIN | 1 | 1 | 153 | 153 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | phases got wrapped together. apalomb | -90.0946 | 29.9553 | 70125 | B | Council District B | Joseph Giarrusso
1302863491 | Yes | ALGIERS | RAIN | 2019-02-01 07:46 | 2019-02-01 07:50 | 2019-02-01 08:23 | W0723 | ENOI | TFUS | 716993 | 4171845941 | DLIN | 81 | 3 | 111 | 37 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Changed **TFUS 716993 3 to TFUS 716993 1** --- riser broke on transformer/ replaced/ bk in nwashi1 | -90.0165 | 29.9236 | 70114 | C | Council District C | Jared Brossett
1303454551 | Yes | ORLEANS | FAIR | 2019-02-23 11:42 | 2019-02-23 11:42 | 2019-02-23 14:20 | 1916 | ENOI | TFUS | 1369589 | 3877346691 | DLIN | 1 | 6 | 948 | 158 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Primary conductor down, crew enroute | -90.1091 | 29.9452 | 70125 | A | Council District A | Jared Brossett
1304403213 | Yes | ORLEANS | FAIR | 2019-03-28 06:46 | 2019-03-28 07:15 | 2019-03-28 08:40 | 1713 | ENOI | LFUS | 17837 | 3998749548 | DLIN | 1 | 18 | 2052 | 114 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Single phase lateral drop. Crew enroute to make repairs. | -90.0699 | 30.0234 | 70122 | D | Council District D | Cyndi Nguyen
1303091709 | Yes | EAST ORLEANS | FAIR | 2019-02-11 16:21 | 2019-02-11 18:38 | 2019-02-11 20:25 | 1601 | ENOI | LFUS | 27281 | 4377749595 | DLIN | 6 | 23 | 5612 | 244 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Equipment - Primary Conductor | -89.95 | 30.0234 | 70128 | E | Council District E | Cyndi Nguyen
1302852262 | Yes | ORLEANS | RAIN | 2019-02-01 03:09 | 2019-02-01 08:10 | 2019-02-01 09:12 | 1926 | ENOI | LFUS | 27621 | 3858046356 | DLIN | 1 | 23 | 8349 | 363 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | primary down | -90.1153 | 29.936 | 70115 | A | Council District A | Kristin Palmer
1303713523 | Yes | EAST ORLEANS | FAIR | 2019-03-05 02:40 | 2019-03-05 05:15 | 2019-03-05 07:00 | 622 | ENOI | LFUS | 21137 | 4087847754 | DLIN | 6 | 45 | 11700 | 260 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | span of number six primary down...crew to repair | -90.0424 | 29.9738 | 70117 | D | Council District D | Cyndi Nguyen
1302953580 | Yes | ORLEANS | FAIR | 2019-02-06 08:15 | 2019-02-06 11:17 | 2019-02-06 11:31 | 2021 | ENOI | LFUS | 21813 | 3928146648 | DLIN | 1 | 49 | 9604 | 196 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Changed **LFUS 21813 127 to LFUS 21813 96** --- refused latural apalomb | -90.0932 | 29.9438 | 70125 | B | Council District B | Cyndi Nguyen
1303956569 | Yes | EAST ORLEANS | FAIR | 2019-03-12 04:17 | 2019-03-12 07:25 | 2019-03-12 07:30 | 2212 | ENOI | LFUS | 24865 | 4196050092 | DLIN | 6 | 53 | 10229 | 193 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | bad between v 13 and v 14 | -90.0072 | 30.0377 | 70126 | E | Council District E | Cyndi Nguyen
1303950653 | Yes | EAST ORLEANS | FAIR | 2019-03-11 16:02 | 2019-03-11 19:04 | 2019-03-11 19:25 | 2223 | ENOI | LFUS | 27641 | 4365151213 | DLIN | 6 | 83 | 16849 | 203 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | bad primary cable | -89.9534 | 30.068 | 70128 | E | Council District E | Jared Brossett
1303059678 | Yes | ALGIERS | COLD | 2019-02-09 10:20 | 2019-02-09 10:56 | 2019-02-09 11:30 | W1714 | ENOI | RCLR | 5129 | 4249645515 | DLIN | 81 | 148 | 10212 | 69 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Changed **RCLR 5129 346 to RCLR 5129 262** --- riser on load switch failed, changed snao tap gcharl1 | -89.992 | 29.9117 | 70131 | C | Council District C | Cyndi Nguyen
1303489324 | Yes | EAST ORLEANS | FAIR | 2019-02-24 08:00 | 2019-02-24 08:16 | 2019-02-24 08:40 | 1710 | ENOI | LFUS | 32292 | 4065548592 | DLIN | 6 | 61 | 2440 | 40 | CONDUCTOR | EOSC | Equipment - Shield Conductor | N | sheild picked back up, lateral back in | -90.0491 | 29.9969 | 70122 | D | Council District D | Joseph Giarrusso
1303236405 | Yes | ORLEANS | FAIR | 2019-02-18 05:00 | 2019-02-18 05:00 | 2019-02-18 17:30 | 1708 | ENOI | XFMR | 669675 | 40184485263 | DLIN | 1 | 1 | 750 | 750 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer | -90.0639 | 29.9953 | 70122 | D | Council District D | Kristin Palmer
1303809600 | NO | ALGIERS | FAIR | 2019-03-08 16:54 | 2019-03-08 16:54 | 2019-03-09 00:31 | W0524 | ELA | XFMR | 1358610 | 4162145630 | DLIN | 81 | 2 | 914 | 457 | EQUIPMENT | ETRD | Equipment - Transformer | N | broken bushing inside 1500 padmount | -90.0196 | 29.9151 | 70114 | C | Council District C | Cyndi Nguyen
1304455270 | Yes | EAST ORLEANS | FAIR | 2019-03-30 04:03 | 2019-03-30 04:03 | 2019-03-30 07:13 | 2345 | ENOI | XFMR | 74053 | 41934474135 | DLIN | 6 | 3 | 570 | 190 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer crew to change | -90.0092 | 29.964 | 70117 | E | Council District E | Jay Banks
1303071650 | Yes | ORLEANS | FAIR | 2019-02-10 13:02 | 2019-02-10 13:02 | 2019-02-10 17:01 | 1554 | ENOI | XFMR | 59946 | 39418468154 | DLIN | 1 | 3 | 717 | 239 | EQUIPMENT | ETRD | Equipment - Transformer | N | transformer need to be changed | -90.0887 | 29.9484 | 70125 | B | Council District B | Jared Brossett
1303534829 | Yes | EAST ORLEANS | FAIR | 2019-02-26 08:55 | 2019-02-26 09:26 | 2019-02-26 12:42 | 1607 | ENOI | XFMR | 67768 | 42117494486 | DLIN | 6 | 4 | 908 | 227 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change out bad transformer | -90.0025 | 30.0199 | 70126 | E | Council District E | Jared Brossett
1304112159 | Yes | EAST ORLEANS | FAIR | 2019-03-14 15:10 | 2019-03-14 15:10 | 2019-03-14 18:00 | 2212 | ENOI | XFMR | 80070 | 41994499040 | DLIN | 6 | 6 | 1020 | 170 | EQUIPMENT | ETRD | Equipment - Transformer | N | CREW CHANGING TRANSFORMER | -90.0062 | 30.0326 | 70126 | E | Council District E | Joseph Giarrusso
1304366654 | Yes | ORLEANS | FAIR | 2019-03-26 13:03 | 2019-03-26 14:23 | 2019-03-26 18:24 | 1705 | ENOI | XFMR | 62574 | 39533478773 | DLIN | 1 | 6 | 1926 | 321 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change xfmr | -90.0847 | 29.9775 | 70119 | A | Council District A | Jay Banks
1303569097 | Yes | EAST ORLEANS | THDR | 2019-02-27 03:33 | 2019-02-27 03:33 | 2019-02-27 06:46 | 622 | ENOI | XFMR | 60894 | 40895477832 | DLIN | 6 | 7 | 1351 | 193 | EQUIPMENT | ETRD | Equipment - Transformer | N | Transformer changed | -90.0418 | 29.9746 | 70117 | D | Council District D | Kristin Palmer
1303710272 | Yes | EAST ORLEANS | FAIR | 2019-03-04 20:44 | 2019-03-04 23:30 | 2019-03-05 01:30 | 2345 | ENOI | XFMR | 73322 | 41997476066 | DLIN | 6 | 7 | 2002 | 286 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace bad transformer...complete | -90.007 | 29.9693 | 70117 | E | Council District E | Kristin Palmer
1302943025 | Yes | ORLEANS | FAIR | 2019-02-05 15:07 | 2019-02-05 17:32 | 2019-02-05 20:11 | 1922 | ENOI | XFMR | 58748 | 39180457378 | DLIN | 1 | 7 | 2128 | 304 | EQUIPMENT | ETRD | Equipment - Transformer | N | Crew replaced bad 50 kva trans. | -90.0966 | 29.9188 | 70115 | B | Council District B | Kristin Palmer
1303158022 | Yes | EAST ORLEANS | FAIR | 2019-02-14 03:58 | 2019-02-14 06:17 | 2019-02-14 08:05 | 1601 | ENOI | XFMR | 1294700 | 43773496459 | DLIN | 6 | 8 | 1976 | 247 | EQUIPMENT | ETRD | Equipment - Transformer | N | Crew changed out failed transformer | -89.9501 | 30.0249 | 70128 | E | Council District E | Jared Brossett
1303750594 | Yes | ALGIERS | FAIR | 2019-03-06 08:09 | 2019-03-06 09:51 | 2019-03-06 10:19 | W0713 | ENOI | XFMR | 662959 | 4137745876 | DLIN | 81 | 9 | 1170 | 130 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer crew on the way to replace | -90.0272 | 29.922 | 70114 | C | Council District C | Kristin Palmer
1303931633 | Yes | ORLEANS | FAIR | 2019-03-11 01:06 | 2019-03-11 01:36 | 2019-03-11 04:00 | 1915 | ENOI | XFMR | 61338 | 39392465921 | DLIN | 1 | 9 | 1566 | 174 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad trans. crew to replace | -90.0897 | 29.9422 | 70113 | B | Council District B | Joseph Giarrusso
1304302449 | Yes | ALGIERS | FAIR | 2019-03-24 14:24 | 2019-03-24 17:53 | 2019-03-24 21:51 | W0713 | ENOI | LFUS | 11281 | 4149345934 | DLIN | 81 | 10 | 3100 | 447 | EQUIPMENT | ETRD | Equipment - Transformer | N | Bad transformer and cable between 1st and 2nd transformers. | -90.0235 | 29.9235 | 70114 | C | Council District C | Jay Banks
1303634249 | Yes | ORLEANS | FAIR | 2019-03-02 07:54 | 2019-03-02 09:42 | 2019-03-02 12:42 | 627 | ENOI | XFMR | 56897 | 40083480633 | DLIN | 1 | 11 | 3168 | 288 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew ot change | -90.0674 | 29.9825 | 70119 | D | Council District D | Cyndi Nguyen
1304167980 | Yes | ORLEANS | FAIR | 2019-03-17 08:51 | 2019-03-17 13:11 | 2019-03-17 18:41 | 1917 | ENOI | TFUS | 79324 | 38509460088 | DLIN | 1 | 11 | 6490 | 590 | EQUIPMENT | ETRD | Equipment - Transformer | N | CREW TO REPLACE TRANSFORMER | -90.1176 | 29.9264 | 70115 | A | Council District A | Kristin Palmer
1303116428 | Yes | ORLEANS | RAIN | 2019-02-12 11:05 | 2019-02-12 12:24 | 2019-02-12 15:06 | 1712 | ENOI | TFUS | 76084 | 40113475053 | DLIN | 1 | 23 | 5543 | 241 | EQUIPMENT | ETRD | Equipment - Transformer | N | 29 OTHER/MISCELLANEOUS SEND TO BUCKET..RECLOSE FUSE..1105 djohn26 | -90.0665 | 29.9671 | 70116 | C | Council District C | Kristin Palmer
1303570095 | Yes | EAST ORLEANS | THDR | 2019-02-27 05:26 | 2019-02-27 05:49 | 2019-02-27 05:53 | 622 | ENOI | LFUS | 21137 | 4087847754 | DLIN | 6 | 38 | 1026 | 27 | EQUIPMENT | ETRD | Equipment - Transformer | N | BAD TRANSFORMER TOOK OUT LATERAL | -90.0424 | 29.9738 | 70117 | D | Council District D | Joseph Giarrusso
1303219306 | Yes | ALGIERS | FAIR | 2019-02-16 17:39 | 2019-02-16 18:28 | 2019-02-16 21:11 | W0713 | ENOI | XFMR | 715599 | 4149245886 | DLIN | 81 | 59 | 12508 | 212 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace transformer | -90.0236 | 29.9222 | 70114 | C | Council District C | Joseph Giarrusso
1302931857 | Yes | ALGIERS | FAIR | 2019-02-05 00:33 | 2019-02-05 00:33 | 2019-02-05 02:14 | W1712 | ENOI | TFUS | BY153082 | 4251645278 | DLIN | 81 | 1 | 101 | 101 | OTHER | UNKN | Inspected Unknown | N | back n now found nothing brizzut | -89.9915 | 29.9051 | 70131 | C | Council District C | Jared Brossett
1302955077 | Yes | ORLEANS | FAIR | 2019-02-06 09:13 | 2019-02-06 09:14 | 2019-02-06 11:29 | 2021 | ENOI | LFUS | 75337 | 3929646618 | DLIN | 1 | 1 | 136 | 136 | OTHER | UNKN | Inspected Unknown | N | restored latural apalomb | -90.0927 | 29.943 | 70113 | B | Council District B | Jared Brossett
1302873612 | Yes | ORLEANS | FAIR | 2019-02-01 15:53 | 2019-02-01 15:53 | 2019-02-01 18:48 | 907 | ENOI | TFUS | 1281202 | 40098473696 | DLIN | 1 | 3 | 525 | 175 | OTHER | UNKN | Inspected Unknown | N | found A phase on terminal pole, refused ok wkamm | -90.0671 | 29.9634 | 70116 | C | Council District C | Cyndi Nguyen
1302903942 | Yes | ALGIERS | FAIR | 2019-02-03 16:45 | 2019-02-03 17:08 | 2019-02-03 17:33 | W1726 | ENOI | TFUS | 1417998 | 4213646159 | DLIN | 81 | 9 | 432 | 48 | OTHER | UNKN | Inspected Unknown | N | on arrival found xformer switch fuse blown ,refuse switch cust. back in lights jthom15 | -90.0031 | 29.9295 | 70131 | C | Council District C | Jay Banks
1303190009 | Yes | ORLEANS | FAIR | 2019-02-15 06:44 | 2019-02-15 07:54 | 2019-02-15 09:00 | 2147 | ENOI | TFUS | 76573 | 39560459216 | DLIN | 1 | 11 | 1496 | 136 | OTHER | UNKN | Inspected Unknown | N | refused ok apalomb | -90.0846 | 29.9238 | 70115 | B | Council District B | Jay Banks
1304050435 | Yes | ORLEANS | FAIR | 2019-03-13 19:49 | 2019-03-13 19:52 | 2019-03-13 20:29 | 1922 | ENOI | LFUS | 27635 | 3907846707 | DLIN | 1 | 14 | 560 | 40 | OTHER | UNKN | Inspected Unknown | N | refused c phase of sub lateral cause unknown jtatma1 | -90.0994 | 29.9454 | 70125 | B | Council District B | Joseph Giarrusso
1303634233 | Yes | EAST ORLEANS | FAIR | 2019-03-02 07:52 | 2019-03-02 08:53 | 2019-03-02 09:14 | 508 | ENOI | LFUS | 17586 | 4099049317 | DLIN | 6 | 25 | 2050 | 82 | OTHER | UNKN | Inspected Unknown | N | Refused B phase at sw# 17586 jvickna | -90.0383 | 30.0167 | 70126 | D | Council District D | Jay Banks
1303377255 | Yes | EAST ORLEANS | RAIN | 2019-02-21 08:18 | 2019-02-21 08:32 | 2019-02-21 09:25 | 2346 | ENOI | LFUS | 34975 | 4151047208 | DLIN | 6 | 41 | 2747 | 67 | OTHER | UNKN | Inspected Unknown | N | fnd b phase blown at sw-47381 and sw-34975-rode out lateral-possible insulator tracking-will have RSM carefully inspect-refused ok-cust back on swalsh1 2-21-19 swalsh1 | -90.0226 | 29.9585 | 70117 | E | Council District E | Jay Banks
1303542623 | Yes | ORLEANS | FAIR | 2019-02-26 13:14 | 2019-02-26 13:14 | 2019-02-26 16:04 | 1513 | ENOI | LFUS | 27852 | 39439473295 | DLIN | 1 | 71 | 12070 | 170 | OTHER | UNKN | Inspected Unknown | N | blown lattural fuse cause unknown apalomb **GAVE TO RELIABILITY TO FOLLOWUP CW 3/7/19*** | -90.0878 | 29.9625 | 70119 | B | Council District B | Jared Brossett
1303086907 | Yes | EAST ORLEANS | FAIR | 2019-02-11 13:28 | 2019-02-11 13:36 | 2019-02-11 13:36 | 509 | ENOI | SBKR | 509 | 4075349223 | DLIN | 6 | 553 | 4424 | 8 | OTHER | UNKN | Inspected Unknown | N | didn t fine anything | -90.0458 | 30.0142 | 70126 | D | Council District D | Cyndi Nguyen
1304269172 | NO | EAST ORLEANS | FAIR | 2019-03-22 13:49 | 2019-03-22 13:49 | 2019-03-22 13:50 | 2217 | ENOI | TFUS | SERVICE | 43448509750 | DLIN | 6 | 1 | 1 | 1 | OTHER | SCHD | Scheduled Interruption | N | Serviceman has out | -89.9599 | 30.0616 | 70128 | E | Council District E | Kristin Palmer
1304269725 | NO | EAST ORLEANS | FAIR | 2019-03-22 14:08 | 2019-03-22 14:08 | 2019-03-22 14:09 | 2217 | ENOI | LFUS | SERVICE | 43417509773 | DLIN | 6 | 1 | 1 | 1 | OTHER | SCHD | Scheduled Interruption | N | Crew dropped out to look in transformer. downstream. | -89.9608 | 30.0616 | 70128 | E | Council District E | Cyndi Nguyen
1303941080 | Yes | ORLEANS | FAIR | 2019-03-11 10:05 | 2019-03-11 10:05 | 2019-03-11 10:18 | 1712 | ENOI | TFUS | SERVICE | 40151476175 | DLIN | 1 | 1 | 13 | 13 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 66066 10 to SERV 66066 [count]** --- Crew is on location working. bsens | -90.0652 | 29.9701 | 70116 | C | Council District C | Cyndi Nguyen
1303947611 | Yes | EAST ORLEANS | FAIR | 2019-03-11 13:52 | 2019-03-11 13:52 | 2019-03-11 14:06 | 2213 | ENOI | TFUS | SERVICE | 44519508875 | DLIN | 6 | 1 | 98 | 14 | OTHER | SCHD | Scheduled Interruption | N |  | -89.926 | 30.0587 | 70129 | E | Council District E | Cyndi Nguyen
1303181364 | Yes | EAST ORLEANS | FAIR | 2019-02-14 14:51 | 2019-02-14 15:01 | 2019-02-14 15:06 | 1601 | ENOI | LFUS | SERVICE | 4377749595 | DLIN | 6 | 1 | 15 | 15 | OTHER | SCHD | Scheduled Interruption | N | Crew outage to replace possible bad arrestor. | -89.95 | 30.0234 | 70128 | E | Council District E | Jared Brossett
1302877266 | Yes | EAST ORLEANS | FAIR | 2019-02-01 18:22 | 2019-02-01 18:22 | 2019-02-01 18:41 | 1604 | ENOI | TFUS | SERVICE | 42757495117 | DLIN | 6 | 1 | 18 | 18 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9824 | 30.0215 | 70127 | E | Council District E | Kristin Palmer
1304341728 | Yes | EAST ORLEANS | FAIR | 2019-03-25 13:30 | 2019-03-25 14:00 | 2019-03-25 14:00 | 1710 | ENOI | LFUS | SERVICE | 4042448442 | DLIN | 6 | 1 | 30 | 30 | OTHER | SCHD | Scheduled Interruption | N | opened for safety of crew | -90.0563 | 29.9928 | 70122 | D | Council District D | Jay Banks
1303238435 | Yes | ORLEANS | FAIR | 2019-02-18 08:15 | 2019-02-18 08:15 | 2019-02-18 08:51 | 409 | ENOI | TFUS | SERVICE | 38371491817 | DLIN | 1 | 1 | 35 | 35 | OTHER | SCHD | Scheduled Interruption | N |  | -90.1209 | 30.0137 | 70124 | A | Council District A | Jared Brossett
1303489963 | Yes | EAST ORLEANS | FAIR | 2019-02-24 08:50 | 2019-02-24 09:16 | 2019-02-24 09:26 | 617 | ENOI | TFUS | SERVICE | 40957489571 | DLIN | 6 | 1 | 36 | 36 | OTHER | SCHD | Scheduled Interruption | N | back on | -90.0393 | 30.0068 | 70126 | D | Council District D | Joseph Giarrusso
1303992306 | Yes | ORLEANS | FAIR | 2019-03-13 09:30 | 2019-03-13 09:30 | 2019-03-13 10:11 | 1923 | ENOI | TFUS | SERVICE | 39212459856 | DLIN | 1 | 1 | 41 | 41 | OTHER | SCHD | Scheduled Interruption | N | contractors working in area apalomb | -90.0955 | 29.9256 | 70115 | B | Council District B | Kristin Palmer
1303180901 | Yes | ORLEANS | FAIR | 2019-02-14 14:26 | 2019-02-14 14:26 | 2019-02-14 15:15 | 407 | ENOI | TFUS | SERVICE | 38612487356 | DLIN | 1 | 1 | 49 | 49 | OTHER | SCHD | Scheduled Interruption | N | Crew outage to replace pole. | -90.1136 | 30.0014 | 70124 | A | Council District A | Jay Banks
1303174426 | Yes | ORLEANS | FAIR | 2019-02-14 13:12 | 2019-02-14 13:12 | 2019-02-14 14:05 | 407 | ENOI | TFUS | SERVICE | 38612487356 | DLIN | 1 | 1 | 583 | 53 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 32516 11 to XFMR 32516 1** --- CREW WORKING ON POLE. BCHATEL bchatel | -90.1136 | 30.0014 | 70124 | A | Council District A | Jay Banks
1303399779 | Yes | ORLEANS | FAIR | 2019-02-22 10:16 | 2019-02-22 10:21 | 2019-02-22 11:10 | 1913 | ENOI | TFUS | SERVICE | 38625457958 | DLIN | 1 | 1 | 54 | 54 | OTHER | SCHD | Scheduled Interruption | N | crew outage | -90.1141 | 29.9206 | 70115 | B | Council District B | Kristin Palmer
1303399786 | Yes | ORLEANS | FAIR | 2019-02-22 10:16 | 2019-02-22 10:16 | 2019-02-22 11:21 | 1705 | ENOI | TFUS | SERVICE | 39665479541 | DLIN | 1 | 1 | 65 | 65 | OTHER | SCHD | Scheduled Interruption | N | Crew outage | -90.0805 | 29.9797 | 70119 | A | Council District A | Jay Banks
1304383271 | Yes | ORLEANS | FAIR | 2019-03-27 08:43 | 2019-03-27 09:34 | 2019-03-27 09:50 | 2021 | ENOI | DIS | SERVICE | 3871847378 | DLIN | 1 | 1 | 67 | 67 | OTHER | SCHD | Scheduled Interruption | N | crew repairing | -90.1107 | 29.964 | 70125 | B | Council District B | Kristin Palmer
1303501954 | Yes | ORLEANS | FAIR | 2019-02-25 07:00 | 2019-02-25 07:39 | 2019-02-25 08:08 | 904 | ENOI | TFUS | SERVICE | 39212480070 | DLIN | 1 | 1 | 68 | 68 | OTHER | SCHD | Scheduled Interruption | N | Crew has a scheduled outage for three hours at this location to do a pole transfer | -90.0949 | 29.9812 | 70119 | A | Council District A | Jared Brossett
1303143854 | Yes | ORLEANS | FAIR | 2019-02-13 10:34 | 2019-02-13 11:15 | 2019-02-13 11:49 | 1924 | ENOI | TFUS | SERVICE | 39160461486 | DLIN | 1 | 1 | 75 | 75 | OTHER | SCHD | Scheduled Interruption | N | crew opened to preform work safley | -90.0972 | 29.9301 | 70115 | B | Council District B | Jared Brossett
1303537733 | Yes | ORLEANS | FAIR | 2019-02-26 10:16 | 2019-02-26 10:16 | 2019-02-26 11:37 | 1926 | ENOI | TFUS | SERVICE | 38777463425 | DLIN | 1 | 1 | 729 | 81 | OTHER | SCHD | Scheduled Interruption | N | crew working at location | -90.1092 | 29.9356 | 70115 | B | Council District B | Cyndi Nguyen
1303959634 | Yes | EAST ORLEANS | FAIR | 2019-03-12 07:10 | 2019-03-12 07:26 | 2019-03-12 08:40 | 2347 | ENOI | TFUS | SERVICE | 41121473211 | DLIN | 6 | 1 | 90 | 90 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0347 | 29.9617 | 70117 | C | Council District C | Joseph Giarrusso
1303120123 | Yes | ORLEANS | RAIN | 2019-02-12 13:26 | 2019-02-12 13:26 | 2019-02-12 14:58 | 2021 | ENOI | TFUS | SERVICE | 39166468017 | DLIN | 1 | 1 | 91 | 91 | OTHER | SCHD | Scheduled Interruption | N | contractors working in area. notified customers on it. abengst | -90.0967 | 29.948 | 70125 | B | Council District B | Jared Brossett
1303804187 | Yes | EAST ORLEANS | FAIR | 2019-03-08 11:37 | 2019-03-08 11:37 | 2019-03-08 13:09 | 2346 | ENOI | TFUS | SERVICE | 41566474057 | DLIN | 6 | 1 | 92 | 92 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 73883 4 to TFUS 73883 1** --- OVERHEAD CONTRACT CREW WORKING SCHEDULED OUTAGE, RB, 3/8/19 rbeaco | -90.0208 | 29.964 | 70117 | E | Council District E | Jared Brossett
1303120791 | Yes | ORLEANS | FAIR | 2019-02-12 13:53 | 2019-02-12 13:53 | 2019-02-12 15:30 | 1708 | ENOI | TFUS | SERVICE | 40298485353 | DLIN | 1 | 1 | 97 | 97 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0603 | 29.9954 | 70122 | D | Council District D | Jared Brossett
1303058108 | Yes | EAST ORLEANS | FAIR | 2019-02-09 08:07 | 2019-02-09 08:40 | 2019-02-09 09:45 | 508 | ENOI | LFUS | SERVICE | 4081949240 | DLIN | 6 | 1 | 98 | 98 | OTHER | SCHD | Scheduled Interruption | N | Crew outage | -90.0437 | 30.0146 | 70126 | D | Council District D | Cyndi Nguyen
1304082626 | Yes | ORLEANS | FAIR | 2019-03-14 07:55 | 2019-03-14 09:09 | 2019-03-14 09:54 | 614 | ENOI | TFUS | SERVICE | 40293476707 | DLIN | 1 | 1 | 118 | 118 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption Crew work | -90.0607 | 29.9716 | 70116 | C | Council District C | Kristin Palmer
1303212517 | Yes | ORLEANS | FAIR | 2019-02-16 09:00 | 2019-02-16 10:01 | 2019-02-16 11:16 | 1913 | ENOI | TFUS | SERVICE | 38568456938 | DLIN | 1 | 1 | 1496 | 136 | OTHER | SCHD | Scheduled Interruption | N |  | -90.1159 | 29.9178 | 70115 | A | Council District A | Joseph Giarrusso
1303809282 | Yes | ORLEANS | FAIR | 2019-03-08 16:35 | 2019-03-08 16:35 | 2019-03-08 19:00 | 622 | ENOI | TFUS | SERVICE | 40403476425 | DLIN | 1 | 1 | 145 | 145 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0573 | 29.9708 | 70116 | C | Council District C | Kristin Palmer
1303032264 | Yes | ORLEANS | FAIR | 2019-02-08 01:12 | 2019-02-08 01:12 | 2019-02-08 04:00 | 1913 | ENOI | TFUS | SERVICE | 38573458049 | DLIN | 1 | 1 | 168 | 168 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1158 | 29.9209 | 70115 | A | Council District A | Jared Brossett
1303779669 | Yes | ORLEANS | FAIR | 2019-03-07 12:35 | 2019-03-07 13:33 | 2019-03-07 15:35 | 1712 | ENOI | TFUS | SERVICE | 40151476175 | DLIN | 1 | 1 | 1800 | 180 | OTHER | SCHD | Scheduled Interruption | N | scheduled interuption | -90.0652 | 29.9701 | 70116 | C | Council District C | Jared Brossett
1303769155 | Yes | EAST ORLEANS | FAIR | 2019-03-07 08:55 | 2019-03-07 09:11 | 2019-03-07 12:06 | 2347 | ENOI | TFUS | SERVICE | 41106474061 | DLIN | 6 | 1 | 3629 | 191 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0351 | 29.9642 | 70117 | C | Council District C | Jared Brossett
1304329537 | Yes | ORLEANS | FAIR | 2019-03-25 08:22 | 2019-03-25 09:35 | 2019-03-25 13:03 | 1926 | ENOI | TFUS | SERVICE | 38549461695 | DLIN | 1 | 1 | 281 | 281 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.1163 | 29.9309 | 70115 | A | Council District A | Jared Brossett
1303574803 | Yes | ORLEANS | FAIR | 2019-02-27 10:09 | 2019-02-27 10:59 | 2019-02-27 14:59 | 1924 | ENOI | TFUS | SERVICE | 39442461748 | DLIN | 1 | 1 | 290 | 290 | OTHER | SCHD | Scheduled Interruption | N | Crew outage | -90.0883 | 29.9308 | 70115 | B | Council District B | Cyndi Nguyen
1302954985 | Yes | ORLEANS | FAIR | 2019-02-06 09:09 | 2019-02-06 11:37 | 2019-02-06 17:22 | 2026 | ENOI | DIS | SERVICE | 3851947426 | DLIN | 1 | 1 | 493 | 493 | OTHER | SCHD | Scheduled Interruption | N | Scheduled Interruption, crew replacing rotten xarms | -90.1174 | 29.965 | 70118 | A | Council District A | Joseph Giarrusso
1303047079 | Yes | EAST ORLEANS | FAIR | 2019-02-08 13:20 | 2019-02-08 13:33 | 2019-02-08 13:36 | 1710 | ENOI | LFUS | SERVICE | 4065748564 | DLIN | 6 | 2 | 32 | 16 | OTHER | SCHD | Scheduled Interruption | N | SCHEDULED INTERRUPTION | -90.0491 | 29.9961 | 70122 | D | Council District D | Jared Brossett
1304221355 | Yes | EAST ORLEANS | FAIR | 2019-03-20 10:15 | 2019-03-20 10:23 | 2019-03-20 10:36 | 626 | ENOI | LFUS | SERVICE | 4089848388 | DLIN | 6 | 2 | 42 | 21 | OTHER | SCHD | Scheduled Interruption | N | back on | -90.0414 | 29.9912 | 70126 | D | Council District D | Jared Brossett
1302913602 | Yes | ORLEANS | FAIR | 2019-02-04 11:00 | 2019-02-04 11:38 | 2019-02-04 11:45 | 903 | ENOI | TFUS | SERVICE | 38875476312 | DLIN | 1 | 2 | 90 | 45 | OTHER | SCHD | Scheduled Interruption | N |  | -90.1055 | 29.971 | 70119 | A | Council District A | Jay Banks
1303570558 | Yes | ORLEANS | RAIN | 2019-02-27 06:26 | 2019-02-27 07:04 | 2019-02-27 07:30 | 614 | ENOI | TFUS | SERVICE | 40259475063 | DLIN | 1 | 2 | 128 | 64 | OTHER | SCHD | Scheduled Interruption | N | crew scheduled outage | -90.0619 | 29.9672 | 70116 | C | Council District C | Jared Brossett
1304279653 | Yes | EAST ORLEANS | FAIR | 2019-03-23 09:20 | 2019-03-23 09:56 | 2019-03-23 10:41 | 502 | ENOI | TFUS | SERVICE | 40595491203 | DLIN | 6 | 2 | 160 | 80 | OTHER | SCHD | Scheduled Interruption | N | Crew outage | -90.0509 | 30.0114 | 70122 | D | Council District D | Kristin Palmer
1304343460 | Yes | EAST ORLEANS | FAIR | 2019-03-25 14:54 | 2019-03-25 14:56 | 2019-03-25 16:24 | 2212 | ENOI | TFUS | SERVICE | 42365502044 | DLIN | 6 | 2 | 180 | 90 | OTHER | SCHD | Scheduled Interruption | N | CONTRACT CREW ON SITE | -89.9944 | 30.0406 | 70127 | E | Council District E | Jay Banks
1303960985 | Yes | ORLEANS | FAIR | 2019-03-12 09:07 | 2019-03-12 09:08 | 2019-03-12 10:46 | 1704 | ENOI | TFUS | SERVICE | 39756487062 | DLIN | 1 | 2 | 588 | 98 | OTHER | SCHD | Scheduled Interruption | N | scheduled interuption | -90.0775 | 30.0003 | 70122 | D | Council District D | Kristin Palmer
1303091192 | Yes | ORLEANS | FAIR | 2019-02-11 15:56 | 2019-02-11 16:54 | 2019-02-11 17:47 | 2021 | ENOI | TFUS | SERVICE | 39519466759 | DLIN | 1 | 2 | 222 | 111 | OTHER | SCHD | Scheduled Interruption | N | pole transfer | -90.0856 | 29.9446 | 70113 | B | Council District B | Jay Banks
1304366117 | Yes | EAST ORLEANS | FAIR | 2019-03-26 12:31 | 2019-03-26 12:38 | 2019-03-26 14:51 | 623 | ENOI | TFUS | SERVICE | 40523476314 | DLIN | 6 | 2 | 280 | 140 | OTHER | SCHD | Scheduled Interruption | N | contract crew on site | -90.0535 | 29.9705 | 70117 | C | Council District C | Kristin Palmer
1303159795 | Yes | ALGIERS | FAIR | 2019-02-14 08:55 | 2019-02-14 11:38 | 2019-02-14 11:39 | W1714 | ENOI | TFUS | SERVICE | 4226444970 | DLIN | 81 | 2 | 328 | 164 | OTHER | SCHD | Scheduled Interruption | N | opened for safety of crew to open jumpers | -89.9996 | 29.8967 | 70131 | C | Council District C | Cyndi Nguyen
1303632908 | Yes | ORLEANS | FOGG | 2019-03-02 07:24 | 2019-03-02 09:56 | 2019-03-02 11:07 | 408 | ENOI | TFUS | SERVICE | 38680486876 | DLIN | 1 | 2 | 446 | 223 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.1115 | 30.0001 | 70124 | A | Council District A | Cyndi Nguyen
1303083484 | Yes | ORLEANS | FAIR | 2019-02-11 10:30 | 2019-02-11 15:40 | 2019-02-11 15:40 | 2021 | ENOI | TFUS | SERVICE | 39519466759 | DLIN | 1 | 2 | 620 | 310 | OTHER | SCHD | Scheduled Interruption | N | POLE TRANSFER | -90.0856 | 29.9446 | 70113 | B | Council District B | Jared Brossett
1303917171 | Yes | EAST ORLEANS | FAIR | 2019-03-10 09:35 | 2019-03-10 09:52 | 2019-03-10 10:07 | 501 | ENOI | LFUS | SERVICE | 4097349099 | DLIN | 6 | 3 | 96 | 32 | OTHER | SCHD | Scheduled Interruption | N | opened to preform work safley | -90.0389 | 30.0107 | 70126 | D | Council District D | Jay Banks
1303211386 | Yes | EAST ORLEANS | FAIR | 2019-02-16 08:23 | 2019-02-16 09:56 | 2019-02-16 10:01 | 1612 | ENOI | LFUS | SERVICE | 4179549351 | DLIN | 6 | 3 | 2037 | 97 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.0127 | 30.0173 | 70126 | E | Council District E | Kristin Palmer
1304185421 | Yes | EAST ORLEANS | FAIR | 2019-03-18 09:37 | 2019-03-18 11:40 | 2019-03-18 11:43 | 1702 | ENOI | LFUS | SERVICE | 4057148946 | DLIN | 6 | 3 | 378 | 126 | OTHER | SCHD | Scheduled Interruption | N | crew work | -90.0515 | 30.0066 | 70122 | D | Council District D | Joseph Giarrusso
1303544080 | Yes | EAST ORLEANS | FAIR | 2019-02-26 13:29 | 2019-02-26 13:47 | 2019-02-26 13:45 | 617 | ENOI | LFUS | SERVICE | 4096548942 | DLIN | 6 | 4 | 592 | 16 | OTHER | SCHD | Scheduled Interruption | N | crew working on lateral | -90.039 | 30.0064 | 70126 | D | Council District D | Kristin Palmer
1303211361 | Yes | EAST ORLEANS | FAIR | 2019-02-16 08:23 | 2019-02-16 09:23 | 2019-02-16 10:00 | 1612 | ENOI | LFUS | SERVICE | 4179749329 | DLIN | 6 | 4 | 3104 | 97 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.0126 | 30.0168 | 70126 | E | Council District E | Kristin Palmer
1303801234 | Yes | ORLEANS | FAIR | 2019-03-08 09:03 | 2019-03-08 13:06 | 2019-03-08 15:01 | B0527 | ENOI | TFUS | SERVICE | 38070466211 | DLIN | 1 | 4 | 1432 | 358 | OTHER | SCHD | Scheduled Interruption | N | Referred**29 OTHER/MISCELLANEOUS send to bucket zarom90 Referred**29 OTHER/MISCELLANEOUS crew case jbologn | -90.1314 | 29.9434 | 70118 | A | Council District A | Jared Brossett
1303961086 | Yes | ORLEANS | FAIR | 2019-03-12 09:05 | 2019-03-12 10:50 | 2019-03-12 12:00 | 1922 | ENOI | LFUS | SERVICE | 3936546383 | DLIN | 1 | 5 | 14175 | 175 | OTHER | SCHD | Scheduled Interruption | N | scheduled interuption | -90.0905 | 29.9365 | 70115 | B | Council District B | Joseph Giarrusso
1303359241 | Yes | ORLEANS | WIND | 2019-02-20 10:17 | 2019-02-20 15:11 | 2019-02-20 15:44 | 2132 | ENOI | LFUS | SERVICE | 3957346262 | DLIN | 1 | 5 | 1635 | 327 | OTHER | SCHD | Scheduled Interruption | N | Fire dept required this section of line remain out for safety reasons | -90.0842 | 29.9331 | 70130 | B | Council District B | Joseph Giarrusso
1304488243 | Yes | EAST ORLEANS | FAIR | 2019-03-31 09:05 | 2019-03-31 09:14 | 2019-03-31 09:16 | 2215 | ENOI | LFUS | SERVICE | 4307750618 | DLIN | 6 | 6 | 66 | 11 | OTHER | SCHD | Scheduled Interruption | N | replace secondary arm | -89.9719 | 30.0517 | 70128 | E | Council District E | Joseph Giarrusso
1302900657 | Yes | EAST ORLEANS | FAIR | 2019-02-03 09:15 | 2019-02-03 10:15 | 2019-02-03 10:20 | 2215 | ENOI | LFUS | SERVICE | 4286250619 | DLIN | 6 | 9 | 585 | 65 | OTHER | SCHD | Scheduled Interruption | N |  | -89.9787 | 30.0519 | 70127 | E | Council District E | Jared Brossett
1303243680 | Yes | EAST ORLEANS | FAIR | 2019-02-18 10:41 | 2019-02-18 11:27 | 2019-02-18 14:10 | 1601 | ENOI | LFUS | SERVICE | 4377749595 | DLIN | 6 | 9 | 1881 | 209 | OTHER | SCHD | Scheduled Interruption | N | switched out to change xfmer : Crews isolated the first 2 trans. from T.P.& restored remaining from back tie | -89.95 | 30.0234 | 70128 | E | Council District E | Cyndi Nguyen
1304295824 | Yes | EAST ORLEANS | FAIR | 2019-03-24 08:43 | 2019-03-24 08:43 | 2019-03-24 09:50 | 622 | ENOI | TFUS | 66461 | 40877476723 | DLIN | 6 | 15 | 1005 | 67 | OTHER | SCHD | Scheduled Interruption | N | crew outage | -90.0424 | 29.9714 | 70117 | C | Council District C | Kristin Palmer
1303191200 | Yes | ORLEANS | FAIR | 2019-02-15 09:09 | 2019-02-15 09:09 | 2019-02-15 10:24 | 615 | ENOI | TFUS | SERVICE | 40046479636 | DLIN | 1 | 20 | 1500 | 75 | OTHER | SCHD | Scheduled Interruption | N | crew making reparis here | -90.0686 | 29.9797 | 70119 | D | Council District D | Joseph Giarrusso
1302885535 | Yes | EAST ORLEANS | FAIR | 2019-02-02 07:41 | 2019-02-02 09:04 | 2019-02-02 09:26 | 1710 | ENOI | LFUS | SERVICE | 4057348499 | DLIN | 6 | 22 | 2310 | 105 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0515 | 29.9943 | 70122 | D | Council District D | Jared Brossett
1303802014 | Yes | ORLEANS | FAIR | 2019-03-08 09:48 | 2019-03-08 09:48 | 2019-03-08 11:04 | 1923 | ENOI | TFUS | 64347 | 39311459424 | DLIN | 1 | 24 | 1824 | 76 | OTHER | SCHD | Scheduled Interruption | N | crew opened to preform work safley | -90.0924 | 29.9245 | 70115 | B | Council District B | Cyndi Nguyen
1304152369 | Yes | EAST ORLEANS | FAIR | 2019-03-16 08:05 | 2019-03-16 10:06 | 2019-03-16 10:46 | 1702 | ENOI | LFUS | 21625 | 4057148946 | DLIN | 6 | 49 | 7889 | 161 | OTHER | SCHD | Scheduled Interruption | N | back on | -90.0515 | 30.0066 | 70122 | D | Council District D | Jay Banks
1304152388 | Yes | EAST ORLEANS | FAIR | 2019-03-16 08:05 | 2019-03-16 09:33 | 2019-03-16 10:45 | 1702 | ENOI | LFUS | 21610 | 4056948968 | DLIN | 6 | 52 | 8320 | 160 | OTHER | SCHD | Scheduled Interruption | N | back on | -90.0516 | 30.0072 | 70122 | D | Council District D | Jared Brossett
1304177199 | Yes | ALGIERS | FAIR | 2019-03-17 18:28 | 2019-03-17 18:28 | 2019-03-17 20:24 | W1725 | ENOI | SERV | 1571251 | 4105746581 | DLIN | 81 | 1 | 116 | 116 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 1571251 23 to SERV 1571251 1** --- changed out service line zwashin | -90.0371 | 29.9414 | 70114 | C | Council District C | Jared Brossett
1303767975 | Yes | ORLEANS | COLD | 2019-03-07 06:50 | 2019-03-07 07:38 | 2019-03-07 08:54 | 1922 | ENOI | SERV | SERVICE COND | 39125457091 | DLIN | 1 | 1 | 124 | 124 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | bad connections at pole, replaced connections, good volt 119/119/238, spoke w oc to have secondary reworked on pole jmarten | -90.0984 | 29.9181 | 70115 | B | Council District B | Jared Brossett
1304103549 | Yes | EAST ORLEANS | FAIR | 2019-03-14 12:42 | 2019-03-14 13:38 | 2019-03-14 15:02 | 505 | ENOI | SERV | SERVICE | 40415495716 | DLIN | 6 | 1 | 140 | 140 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Replaced 4/0 hot leg on transformer jvickna | -90.0564 | 30.0238 | 70122 | D | Council District D | Jay Banks
1303645166 | Yes | EAST ORLEANS | FAIR | 2019-03-02 17:15 | 2019-03-02 17:15 | 2019-03-02 20:10 | 2223 | ENOI | SERV | SERVICE | 43898513336 | DLIN | 6 | 1 | 175 | 175 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | crew installed dry cell (pwd) | -89.9457 | 30.0712 | 70128 | E | Council District E | Kristin Palmer
1303503120 | Yes | EAST ORLEANS | FAIR | 2019-02-25 08:39 | 2019-02-25 09:03 | 2019-02-25 13:35 | 1204 | ENOI | SERV | SERVICE | 48001511715 | DLIN | 6 | 1 | 296 | 296 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | crew to install dry cell...complete | -89.8162 | 30.0653 | 70129 | E | Council District E | Cyndi Nguyen
1304190229 | Yes | EAST ORLEANS | FAIR | 2019-03-18 12:27 | 2019-03-18 12:27 | 2019-03-18 17:26 | 1710 | ENOI | SERV | SERVICE | 40493485610 | DLIN | 6 | 1 | 299 | 299 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Referred**29 OTHER/MISCELLANEOUS voltage is 120 a phase to phase and 120 phase to ground voltage was tested at mtr panel customer cant use any appliances sgoins | -90.0542 | 29.996 | 70122 | D | Council District D | Cyndi Nguyen
1302923759 | Yes | ALGIERS | FAIR | 2019-02-04 16:27 | 2019-02-04 16:27 | 2019-02-04 23:43 | W1712 | ENOI | TFUS | BY166677 | 4254645285 | DLIN | 81 | 5 | 2180 | 436 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Primary cable | -89.9906 | 29.9054 | 70131 | C | Council District C | Jared Brossett
1303595230 | Yes | ORLEANS | FAIR | 2019-02-28 02:19 | 2019-02-28 06:05 | 2019-02-28 06:20 | 2135 | ENOI | TFUS | 693371 | 39695462102 | DLIN | 1 | 13 | 3133 | 241 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Secondary/Service Conductor | -90.0802 | 29.9317 | 70130 | B | Council District B | Jared Brossett
1302872208 | Yes | EAST ORLEANS | FAIR | 2019-02-01 15:05 | 2019-02-01 15:29 | 2019-02-01 15:50 | 1602 | ENOI | LFUS | 37957 | 4267449918 | DLIN | 6 | 53 | 2385 | 45 | CONDUCTOR | ESEC | Secondary/Service Conductor | N |  | -97.0758 | 27.9066 | 70127 | E | Council District E | Cyndi Nguyen
1303925828 | Yes | ORLEANS | FAIR | 2019-03-10 15:35 | 2019-03-10 16:35 | 2019-03-10 16:36 | 2147 | ENOI | SBKR | 2147 | 4012946119 | DLIN | 1 | 2804 | 171044 | 61 | CONDUCTOR | SLAK | Slack Conductor / Inadequate Phase Spacing | N | #6 copper burnt down hard tied to feeder caused by high fault current from lateral fuses blowing and phases whipped together | -90.0666 | 29.929 | 70130 | B | Council District B | Cyndi Nguyen
1303566404 | NO | ORLEANS | THDR | 2019-02-27 01:09 | 2019-02-27 04:02 | 2019-02-27 04:01 | 1912 | ENOI | SUBN | 1912 | 3909245668 | DSUB | 1 | 792 | 123896 | 171 | EQUIPMENT | BKRO | Substation Breaker - Oil | N | BREAKER 1912 SOMETHING GOING ON WITH BREAKER; SWMS WR#: 1380002249 Breaker | -90.0994 | 29.9169 | 70115 | B | Council District B | Cyndi Nguyen
1303037905 | Yes | ORLEANS | WIND | 2019-02-08 08:12 | 2019-02-08 09:26 | 2019-02-08 09:05 | 1543 | ENOI | SBKR | 1543 | 3950646993 | DLIN | 1 | 5 | 265 | 53 | OTHER | UNKI | Unknown - Under Investigation | N | CBD crew in investigate: All cust. with A.T.S. transferred auto: Manuel restored the remainder : Will patrol line for reliability oppourtunities | -90.0859 | 29.9532 | 70113 | B | Council District B | Cyndi Nguyen
1303612953 | NO | EAST ORLEANS | FAIR | 2019-02-28 22:57 | 2019-02-28 22:57 | 2019-02-28 22:57 | 1203 | ENOI | SBKR | 1203 | 4542350166 | DLIN | 6 | 54 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N | will patroo line on friday | -89.8978 | 30.0386 | 70129 | E | Council District E | Jay Banks
1303168458 | Yes | EAST ORLEANS | FAIR | 2019-02-14 12:07 | 2019-02-14 12:15 | 2019-02-14 14:05 | 1601 | ENOI | LFUS | 27281 | 4377749595 | DLIN | 6 | 65 | 7670 | 118 | OTHER | UNKI | Unknown - Under Investigation | N | Line fuse was blown again, refuse and holding. Will infrared to locate problem. | -89.95 | 30.0234 | 70128 | E | Council District E | Jay Banks
1303430641 | NO | EAST ORLEANS | FAIR | 2019-02-23 03:12 | 2019-02-23 03:12 | 2019-02-23 03:12 | 512 | ENOI | SBKR | 512 | 4074849223 | DLIN | 6 | 1081 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N | Unknown - Under Investigation: Patrolled with nothing found | -90.0459 | 30.0142 | 70126 | D | Council District D | Jared Brossett