## CI Cause Category Details
Row Labels | Sum of CI
Animal | 104
Animal - Other (Describe in Remarks Field) | 22
Animal - Squirrel | 82
Equipment Failure | 13699
Equipment Failure - Air Break / Disconnect Switch | 21 | 22567 | Distribution CI's, slide 1 of presentation
Equipment Failure - Arrestor | 316 | 7145 | Scheduled Interruption & Emergency Switching CI's, slide 4 of presentation
Equipment Failure - Connector / Sleeve | 43 | 0 | Transmission CI's, slide 9 of presentation
Equipment Failure - Connector Sleeve | 1397 | 29712 | Total CI's reported January - February 2020
Equipment Failure - Crossarm | 2767
Equipment Failure - Elbow | 460
Equipment Failure - Fuse Link | 582
Equipment Failure - Fuse Switch | 125
Equipment Failure - Insulator | 211
Equipment Failure - Metering | 1
Equipment Failure - Other (Describe in Remarks Fie | 116
Equipment Failure - Pole | 46
Equipment Failure - Primary Conductor | 4477
Equipment Failure - Transformer | 1223
Secondary/Service Conductor | 96
Switching Cabinet | 1818
Human Error | 16
Human Error - Company (Describe in Remarks Field) | 16
Lightning | 679
Lightning | 679
Other | 9917
Corrosion | 23
Emergency Switching | 5296
Fire - Other (Describe in Remarks Field) | 16
Foreign Objects (Describe in Remarks Field) | 2515
Inspected Unknown | 2063
Meter Exchange | 4
Public Damage | 3170
Vehicle | 3170
Scheduled Interruption | 1849
Scheduled Interruption | 1849
Vegetation | 278
Overhanging Limb | 65
Tree On Line Outside R.O.W | 76
Tree/Limb Growing Inside R.O.W. | 7
Vine Growing into Line | 130
Grand Total | 29712

## CI by District & Weather
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
Sum of CI
DISTRICT | WEATHER_CONDITION | Summary Cause Updated | CAUSE_DESC | MONTH | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 3279 | 11.04%
Council District B | [9 empty] | 7543 | 25.39%
Council District C | [9 empty] | 1623 | 5.462%
Council District D | [9 empty] | 7317 | 24.63%
Council District E | [9 empty] | 9950 | 33.49%
Grand Total | [9 empty] | 29712 | 100%

## CI by District & Zip Code
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
Sum of CI
DISTRICT | ZIP | Summary Cause Updated | CAUSE_DESC | MONTH | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 3279 | 11.04%
Council District B | [9 empty] | 7543 | 25.39%
Council District C | [9 empty] | 1623 | 5.462%
Council District D | [9 empty] | 7317 | 24.63%
Council District E | [9 empty] | 9950 | 33.49%
Grand Total | [9 empty] | 29712 | 100%

## data
'Date Table'[Year] | CI | 'Outages_NOCC-CAT'[Year] | CASE_ID | In_NOCC_Reporting | NETWORK_NAME | WEATHER_CONDITION | TOTAL_DURATION_MINUTES | FIRST_CALL_DATE_TIME | ACTUAL_CUSTOMER_MINUTES | DEVICE_TYPE | DEVICE_ID | DISTRIBUTION_LOCATION_NBR | FEEDER_ID | Fdr_Owner | LOCAL_OFFICE_NBR | TOTAL_CUSTOMERS_AFFECTED | CAUSE | CAUSE_DESC | MAJOR_EVENT | REMARKS | LONGITUDE | LATITUDE | AdvPeriod | V_Reliability_Custs_Legal_Entity.Cust_SRVD | Days to Include | SUMMARY_CAUSE | DEVICE_TYPE_DESC | Summary Cause Updated | System | DISTRICTID | DISTRICT | REPNAME | ZIP | MONTH
2020 | 1451 | 2020 | 1323244545 | Yes | ORLEANS | FAIR | 11 | 2020-01-27 | 15961 | SBKR | 1554 | 3950446990 | 1554 | ENOI | 1 | 1451 | UNKN | Inspected Unknown | N | serviceman did not find anything on line; closed bkr in and holding | -90.086 | 29.9532 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 6 | 2020 | 1322735719 | Yes | EAST ORLEANS | FAIR | 12 | 2020-01-14 | 72 | TFUS | 73176 | 41551474793 | 2347 | ENOI | 6 | 6 | ESEC | Secondary/Service Conductor | N | made repairs to trans | -90.0211 | 29.966 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 2365 | 2020 | 1323253767 | Yes | ORLEANS | FAIR | 17 | 2020-01-27 | 40205 | SBKR | 907 | 3897447410 | 907 | ENOI | 1 | 2365 | EMER | Emergency Switching | N | had to drop feeder for transformers on fire | -90.1026 | 29.9648 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70119 | 1
2020 | 841 | 2020 | 1321761982 | Yes | EAST ORLEANS | FAIR | 19 | 2020-01-06 | 15979 | SBKR | 1602 | 4351549756 | 1602 | ENOI | 6 | 841 | ESWC | Switching Cabinet | N | Fault in CUB 554 caused outage | -89.9583 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 313 | 2020 | 1323305072 | Yes | ORLEANS | FAIR | 21 | 2020-01-29 | 6573 | DIS | 25494 | 3882647318 | 2011 | ENOI | 1 | 313 | EMER | Emergency Switching | N | SHIELD WIRE DOWN | -90.1072 | 29.9624 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 1 | 2020 | 1321890202 | Yes | ORLEANS | FAIR | 22 | 2020-01-09 | 22 | SERV | METER | 38903461840 | 1914 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | Changed **TFUS 77590 * 11 to SERV 77590 * 1** --- meter was not all rthe way into meter socket. per 310 treed3 | -90.1052 | 29.9311 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 234 | 2020 | 1323084559 | Yes | EAST ORLEANS | FAIR | 27 | 2020-01-21 | 3510 | RCLR | 37793 | 4946452184 | 1204 | ENOI | 6 | 234 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.7693 | 30.0927 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 36 | 2020 | 1321744962 | Yes | EAST ORLEANS | FAIR | 34 | 2020-01-05 | 1224 | LFUS | 62597 | 4159649935 | 2212 | ENOI | 6 | 36 | ASQL | Animal - Squirrel | N | squirrel took out over head portion thata casuse outage for underground dwillin | -90.0189 | 30.0333 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 52 | 2020 | 1322857299 | Yes | EAST ORLEANS | FAIR | 34 | 2020-01-16 | 1768 | LFUS | 24311 | 4173149985 | 2212 | ENOI | 6 | 52 | VINE | Vine Growing into Line | N | vines grew into b phase cleaared as muc as i could but someone needs to coem clear vines road out lateral all lights came back on as i can tell | -90.0146 | 30.0348 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 88 | 2020 | 1322332691 | Yes | ORLEANS | THDR | 35 | 2020-01-11 | 3080 | LFUS | 37781 | 3988848138 | 1709 | ENOI | 1 | 88 | LGHT | Lightning | N | ispected unknown refused advise jcox7 | -90.0735 | 29.9846 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 1 | 2020 | 1321689819 | Yes | ORLEANS | RAIN | 36 | 2020-01-03 | 36 | SERV | SERVICE | 38483463662 | 2024 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | changed conector at pole voltage check good gkathma | -90.1185 | 29.9362 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 5 | 2020 | 1321924209 | Yes | ALGIERS ELEC ONLY | FAIR | 36 | 2020-01-10 | 180 | LFUS | 5534-F | 4462845638 | W1715 | ENOI | 81 | 5 | EARM | Equipment Failure - Crossarm | N | Crew to replace cross-arm downstream of this device, per Zach Washington...........PC | -89.9246 | 29.9144 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 2 | 2020 | 1322818414 | Yes | EAST ORLEANS | FAIR | 36 | 2020-01-15 | 72 | XFMR | 79392 | 49613525017 | 1204 | ENOI | 6 | 2 | ETRD | Equipment Failure - Transformer | N |  | -89.7641 | 30.1015 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 4 | 2020 | 1323272107 | Yes | ORLEANS | FAIR | 38 | 2020-01-28 | 152 | TFUS | 3004438 | 38731464304 | 1926 | ENOI | 1 | 4 | SCHD | Scheduled Interruption | N | Planned outage contractors working per#305 | -90.1105 | 29.938 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 1
2020 | 137 | 2020 | 1321931828 | Yes | EAST ORLEANS | FAIR | 39 | 2020-01-10 | 5343 | DIS | 38259 | 4126248306 | 626 | ENOI | 6 | 137 | SCHD | Scheduled Interruption | N | Scheduled Interruption; crew picking up low hanging primary | -90.0301 | 29.9887 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 1 | 2020 | 1321722737 | Yes | ORLEANS | FAIR | 40 | 2020-01-04 | 40 | SERV | SERVICE | 40316487839 | 1701 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Changed **TFUS 58867 5 to SERV 58867 5** --- hot leg burnt at pole dcain2 | -90.0596 | 30.0022 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 315 | 2020 | 1323252770 | Yes | EAST ORLEANS | FAIR | 40 | 2020-01-27 | 12600 | SBKR | 625 | 4081248423 | 625 | ENOI | 6 | 315 | VHCL | Vehicle | N | vehicle hit guy wire and flipped into feeder, removed and back on RELAED TO KT# 1323254789 (AKS) | -90.0442 | 29.9922 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Substation Breaker | Public Damage | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 1 | 2020 | 1322173499 | Yes | ORLEANS | WIND | 44 | 2020-01-11 | 44 | SECO | SECONDARY COND | 39729483055 | 627 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Changed **TFUS 9 to TFUS 1** --- loose connection at pole repaired and checked voltage jcox7 | -90.0785 | 29.9892 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Secondary Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 77 | 2020 | 1321760883 | Yes | ORLEANS | FAIR | 47 | 2020-01-06 | 3619 | LFUS | 33980 | 3956946513 | 2132 | ENOI | 1 | 77 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons let go by cust. removed balloons and refused lfus. dsmit36 | -89.9849 | 30.033 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 3 | 2020 | 1321852054 | Yes | EAST ORLEANS | FAIR | 48 | 2020-01-08 | 144 | XFMR | 665472 | 41954472941 | 2346 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N |  | -90.0084 | 29.9607 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 11 | 2020 | 1322240774 | Yes | ORLEANS | THDR | 49 | 2020-01-11 | 539 | LFUS | 33059 | 38974475070 | 903 | ENOI | 1 | 11 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | roof blew off building taking out a and b phase and taking down 1 span open wire secondary, picked up wire and refused lateral mrusse8 | -90.1025 | 29.9676 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70119 | 1
2020 | 5 | 2020 | 1322933942 | Yes | ALGIERS ELEC ONLY | FAIR | 53 | 2020-01-17 | 265 | TFUS | BY110681 | 4226045412 | W1714 | ENOI | 81 | 5 | SCHD | Scheduled Interruption | N | Nick Carroll will have xfmr out | -89.9995 | 29.9089 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 12 | 2020 | 1322234430 | Yes | ORLEANS | THDR | 54 | 2020-01-11 | 648 | TFUS | 518794 | 38168466520 | 2014 | ENOI | 1 | 12 | LGHT | Lightning | N | out by weather. refused ok dsmit36 | -90.1283 | 29.9443 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 3 | 2020 | 1323085293 | Yes | EAST ORLEANS | FAIR | 55 | 2020-01-21 | 165 | LFUS | F05622 | 4830351192 | 1204 | ENOI | 6 | 3 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.8064 | 30.0658 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 48 | 2020 | 1321847622 | Yes | EAST ORLEANS | FAIR | 58 | 2020-01-08 | 2784 | LFUS | 37416 | 40593476553 | 622 | ENOI | 6 | 48 | SCHD | Scheduled Interruption | N | crew on site | -90.0513 | 29.9711 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 61 | 2020 | 1322256616 | Yes | ORLEANS | THDR | 63 | 2020-01-11 | 3843 | LFUS | 28031 | 3833945903 | 1914 | ENOI | 1 | 61 | LGHT | Lightning | N | lightning tagged an insulator 1 span from the lateral. Crew changed ins. and refused lateral rbiles | -90.1231 | 29.9237 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 4 | 2020 | 1322854567 | Yes | EAST ORLEANS | FAIR | 66 | 2020-01-16 | 264 | TFUS | 1605537 | 42777504021 | 2215 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | crew onsite | -89.9813 | 30.046 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 83 | 2020 | 1323219985 | Yes | ORLEANS | FAIR | 66 | 2020-01-26 | 5478 | LFUS | 27976 | 4035147852 | 1709 | ENOI | 1 | 83 | EPRI | Equipment Failure - Primary Conductor | N |  | -90.0588 | 29.9766 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70116 | 1
2020 | 13 | 2020 | 1323133322 | Yes | ORLEANS | FAIR | 67 | 2020-01-23 | 871 | TFUS | 72349 | 38762481819 | 903 | ENOI | 1 | 13 | VHCL | Vehicle | N | truck pulled down service line and tore meters and stem pipe off of house. related to ticket 1323096279 yesterday already sent to minimalclaimskc | -90.1091 | 29.9862 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 33 | 2020 | 1322288849 | Yes | EAST ORLEANS | FAIR | 69 | 2020-01-11 | 2277 | LFUS | 34976 | 4152747182 | 2346 | ENOI | 6 | 33 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | ballon got into secondary took out stinger pot which blew lateral fuse refuse lateral and transformer and lights are back on and good voltage dwillin | -90.022 | 29.9578 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 1
2020 | 851 | 2020 | 1321740753 | Yes | EAST ORLEANS | FAIR | 70 | 2020-01-05 | 59570 | SBKR | 1602 | 4351549756 | 1602 | ENOI | 6 | 851 | ESWC | Switching Cabinet | N | opened in vfi 531 opened switch 38268 serviceman to ride remainng customer sout Cub, # 554 flashover Okay Temp | -89.9583 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 2 | 2020 | 1322340541 | Yes | EAST ORLEANS | THDR | 71 | 2020-01-11 | 142 | PRIM | 4341249109 | 4341249109 | 1612 | ENOI | 6 | 2 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | MOULDING | -89.9618 | 30.0102 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Primary Meter | Other | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 1 | 2020 | 1323164693 | Yes | ORLEANS | FAIR | 71 | 2020-01-24 | 71 | SERV | SERVICE COND | 38374484905 | 407 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | bad connection at weather head changed out ok #305 | -90.1212 | 29.9948 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 11 | 2020 | 1321820424 | Yes | ORLEANS | FAIR | 74 | 2020-01-07 | 814 | TFUS | 55653 | 38968480755 | 904 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1024 | 29.9832 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 7 | 2020 | 1323000141 | Yes | ALGIERS ELEC ONLY | FAIR | 74 | 2020-01-19 | 518 | TFUS | 1417734 | 4264345881 | W1713 | ENOI | 81 | 7 | VOHL | Overhanging Limb | N | ROBERT COURET W-00 | -89.9873 | 29.9217 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 716 | 2020 | 1323082860 | Yes | EAST ORLEANS | FAIR | 75 | 2020-01-21 | 53700 | SBKR | 1204 | 4544050173 | 1204 | ENOI | 6 | 716 | EPRI | Equipment Failure - Primary Conductor | N | poen midpoint breaker in | -89.8973 | 30.0387 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 56 | 2020 | 1323138236 | Yes | ORLEANS | FAIR | 77 | 2020-01-23 | 4312 | LFUS | 27806 | 3884646637 | 1916 | ENOI | 1 | 56 | EARM | Equipment Failure - Crossarm | N | cross arm broke street side phase was cut down temp ok gor now #305 | -90.1068 | 29.9437 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 1 | 2020 | 1321900766 | Yes | EAST ORLEANS | FAIR | 78 | 2020-01-10 | 78 | SERV | SERVICE | 42073500359 | 2212 | ENOI | 6 | 1 | EMET | Equipment Failure - Metering | N | ami meter burned up customer lug pulled meter meter #am10993i155 installed new meter 8154918 sn 92095254 cbowden | -90.0037 | 30.0361 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 5 | 2020 | 1322510653 | Yes | ORLEANS | FAIR | 78 | 2020-01-12 | 390 | TFUS | 1183487 | 39789466302 | 2137 | ENOI | 1 | 5 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0772 | 29.9432 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 26 | 2020 | 1322629818 | Yes | ORLEANS | FAIR | 78 | 2020-01-13 | 2028 | DIS | 23138 | 3852247482 | 2012 | ENOI | 1 | 26 | SCHD | Scheduled Interruption | N | Line de-energized to safely replace xarms | -90.1168 | 29.9669 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 2 | 2020 | 1322605291 | Yes | EAST ORLEANS | FOGG | 78 | 2020-01-13 | 156 | TFUS | 1106471 | 41320493904 | 1009 | ENOI | 6 | 2 | EFLK | Equipment Failure - Fuse Link | N | refused b phase check customer ok cschexn | -90.0277 | 30.0186 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 19 | 2020 | 1323227281 | Yes | ALGIERS ELEC ONLY | FAIR | 78 | 2020-01-26 | 1482 | LFUS | 5699 | 4261545915 | W1713 | ENOI | 81 | 19 | UNKN | Inspected Unknown | N | blown lat fuse refused and held also transformer 3004469 was blown not sure if this is what caused the lat fuse to blow. both lat fuse and transformer had proper size fuses in them also | -89.9882 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 5 | 2020 | 1322147313 | Yes | ORLEANS | WIND | 79 | 2020-01-11 | 395 | TFUS | 1385289 | 39706489324 | 1704 | ENOI | 1 | 5 | VOHL | Overhanging Limb | N | found tree branch on top of transformer resfued ok jcox7 | -90.079 | 30.0065 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 2 | 2020 | 1321608611 | Yes | ORLEANS CBD | FAIR | 80 | 2020-01-01 | 160 | SBKR | 1822 | 4015446698 | 1822 | ENOI | 4 | 2 | EPRI | Equipment Failure - Primary Conductor | N | failure in manhole 6-1460; bad splice on b phase: The 2 cust. were restored manuelly at 6;35 AM Fder was restored 1/2/20 4:08 AM: The 3rd cust was a mis-match | -90.0656 | 29.9449 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 1 | 2020 | 1321637104 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-02 | 80 | TFUS | 1223486 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | vines grew into terminal pole toook out a phase cleared vines refused barrrel and got lights cback on and tested voltage lights cam eback on dwillin | -90.0377 | 30.0062 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 1 | 2020 | 1321713956 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-03 | 80 | SERV | SERVICE | 42029493934 | 1607 | ENOI | 6 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed **TFUS 1315127 8 to SERV 1315127 8** --- sec conect..repaired tbrock | -90.0053 | 30.0185 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 9 | 2020 | 1323314478 | Yes | EAST ORLEANS | FAIR | 80 | 2020-01-29 | 720 | TFUS | 64100 | 43284495685 | 1611 | ENOI | 6 | 9 | SCHD | Scheduled Interruption | N |  | -89.9656 | 30.0229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 13 | 2020 | 1321665957 | Yes | EAST ORLEANS | RAIN | 81 | 2020-01-02 | 1053 | TFUS | 1205818 | 40891475703 | 622 | ENOI | 6 | 13 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.042 | 29.9687 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 167 | 2020 | 1323138006 | Yes | ALGIERS ELEC ONLY | THDR | 85 | 2020-01-23 | 14195 | RCLR | 5123 | 4150446191 | W0725 | ENOI | 81 | 167 | EMER | Emergency Switching | N | phase down on arm | -90.0231 | 29.9306 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Recloser | Emergency Switching | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 23 | 2020 | 1321643125 | Yes | ORLEANS | THDR | 89 | 2020-01-02 | 2047 | LFUS | 27621 | 3858046356 | 1926 | ENOI | 1 | 23 | VOHL | Overhanging Limb | N | Crew on site picking up down primary | -90.1153 | 29.936 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 1
2020 | 1 | 2020 | 1323096832 | Yes | ORLEANS | FAIR | 90 | 2020-01-22 | 90 | SERV | SERVICE | 39963459713 | 2147 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | bad connection at pole | -90.0718 | 29.9251 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 2 | 2020 | 1323182720 | Yes | ORLEANS | FAIR | 92 | 2020-01-24 | 184 | LFUS | 37944 | 38356458630 | 1914 | ENOI | 1 | 2 | EFLK | Equipment Failure - Fuse Link | N | Found phase switch blown on lateral to closed delta bank. Inspected primary and found flash mark where wire touched other potential. Refused lateral phase and threw it in. Back in lights. | -90.1226 | 29.9225 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 10 | 2020 | 1322249652 | Yes | EAST ORLEANS | THDR | 93 | 2020-01-11 | 930 | LFUS | 38536 | 43220496192 | 1611 | ENOI | 6 | 10 | LGHT | Lightning | N | Changed **TFUS 1361822 8 to LFUS 1361822 8** --- refused B and C phase on lateral 38536 due to weather jvickna | -89.9677 | 30.0243 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 1 | 2020 | 1322322442 | Yes | EAST ORLEANS | THDR | 96 | 2020-01-11 | 96 | LFUS | 83983 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | vines took out b phase on terminal pole-cleared vines and refused b phase ok-voltage ok-cust back on swalsh1 1-11-20 swalsh1 | -90.0377 | 30.0062 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 6 | 2020 | 1321686189 | Yes | EAST ORLEANS | FAIR | 97 | 2020-01-03 | 582 | XFMR | 1373368 | 43960512098 | 2217 | ENOI | 6 | 6 | ETRD | Equipment Failure - Transformer | N | bad transformer | -89.9437 | 30.0677 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 11 | 2020 | 1323273155 | Yes | ORLEANS | FAIR | 98 | 2020-01-28 | 1078 | TFUS | 61598 | 39294467195 | 2021 | ENOI | 1 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0927 | 29.9459 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 347 | 2020 | 1321742427 | Yes | EAST ORLEANS | FAIR | 99 | 2020-01-05 | 34353 | VFI | 38268 | 4264649768 | 1602 | ENOI | 6 | 347 | EFLK | Equipment Failure - Fuse Link | N | fault behind lateral 73441 | -89.9934 | 30.0265 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Vacuum Fault Interrupter | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 1 | 2020 | 1323068509 | Yes | ALGIERS ELEC ONLY | FAIR | 101 | 2020-01-21 | 101 | SERV | SERVICE | 4252245651 | W1714 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N |  | -89.9912 | 29.9154 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 16 | 2020 | 1321759209 | Yes | EAST ORLEANS | FAIR | 105 | 2020-01-06 | 1680 | TFUS | 569328 | 40728487726 | 1702 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N | Crew On Site Working | -90.0467 | 30.0019 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 30 | 2020 | 1322330888 | Yes | ORLEANS | THDR | 109 | 2020-01-11 | 3270 | LFUS | 27906 | 38475463265 | 1926 | ENOI | 1 | 30 | LGHT | Lightning | N | lightning took out c phase of lateral 27906 refused ok rbiles | -90.1186 | 29.9353 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 26 | 2020 | 1321808505 | Yes | ORLEANS | FAIR | 110 | 2020-01-07 | 2860 | LFUS | 37703 | 3947445909 | 2147 | ENOI | 1 | 26 | ASQL | Animal - Squirrel | N | got across lateral and blew 2 phases | -90.0873 | 29.9236 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Line Fuse | Animal | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 9 | 2020 | 1323304403 | Yes | ORLEANS | FAIR | 110 | 2020-01-29 | 990 | TFUS | 1361517 | 38447493598 | 409 | ENOI | 1 | 9 | EFSW | Equipment Failure - Fuse Switch | N | no comments | -90.1185 | 30.0186 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 6 | 2020 | 1323312030 | Yes | ORLEANS | FAIR | 110 | 2020-01-29 | 660 | TFUS | 1417271 | 39826488565 | 1704 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | fuse link corroded and broke. replaced and reenergized ok. | -90.0752 | 30.0044 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 6 | 2020 | 1323291673 | Yes | ORLEANS | FAIR | 112 | 2020-01-29 | 672 | TFUS | 16216 | 3989349266 | 510 | ENOI | 1 | 6 | EFLK | Equipment Failure - Fuse Link | N | refused transformer ( Dloc. # 39896492416 ) taken out by weather, lateral was still in | -90.073 | 30.0155 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 42 | 2020 | 1322269743 | Yes | ALGIERS ELEC ONLY | RAIN | 113 | 2020-01-11 | 4746 | LFUS | 5002 | 4141446606 | W1725 | ENOI | 81 | 42 | ETRD | Equipment Failure - Transformer | N | back n now bad pot brizzut | -90.0259 | 29.942 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 9 | 2020 | 1323073215 | Yes | EAST ORLEANS | FAIR | 121 | 2020-01-21 | 1089 | TFUS | 64100 | 43284495685 | 1611 | ENOI | 6 | 9 | SCHD | Scheduled Interruption | N | crew opened for safety to transfer pole | -89.9656 | 30.0229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 5 | 2020 | 1323263389 | Yes | EAST ORLEANS | FAIR | 124 | 2020-01-28 | 620 | TFUS | 1087299 | 42802502570 | 2216 | ENOI | 6 | 5 | VHCL | Vehicle | N | someoned bumped cubicle and knocked out c phase | -89.9807 | 30.042 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Transformer Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 12 | 2020 | 1323289932 | Yes | ALGIERS ELEC ONLY | FAIR | 124 | 2020-01-29 | 1488 | XFMR | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | ETRD | Equipment Failure - Transformer | N | bad 100by in rear of 6315 brighton pl, rc 1-29-20 | -89.9867 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 8 | 2020 | 1321649001 | Yes | EAST ORLEANS | THDR | 125 | 2020-01-02 | 1000 | TFUS | 1137669 | 41102491707 | 501 | ENOI | 6 | 8 | EPRI | Equipment Failure - Primary Conductor | N | Crew on the way to repair burned up riser | -90.0348 | 30.0126 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 25 | 2020 | 1323220694 | Yes | ORLEANS | FAIR | 125 | 2020-01-26 | 3125 | LFUS | 27940 | 3927945767 | 1922 | ENOI | 1 | 25 | VINE | Vine Growing into Line | N | Vines. Refused ok Veg ticket created Jmulle2 | -90.0935 | 29.9194 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 25 | 2020 | 1321769814 | Yes | EAST ORLEANS | FAIR | 128 | 2020-01-06 | 3200 | LFUS | 25370 | 4385351220 | 2217 | ENOI | 6 | 25 | EPRI | Equipment Failure - Primary Conductor | N | Switched out bad cable between V-24 to TP 25370 | -89.9472 | 30.0681 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 12 | 2020 | 1323222467 | Yes | ORLEANS | RAIN | 131 | 2020-01-26 | 1572 | TFUS | 18346 | 38366491158 | 409 | ENOI | 1 | 12 | AOTH | Animal - Other (Describe in Remarks Field) | N | bird droppings on top tformer cleaned off the droppings tformer refused good everyone back in lights | -90.1211 | 30.0119 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 3 | 2020 | 1322474174 | Yes | ALGIERS ELEC ONLY | RAIN | 133 | 2020-01-12 | 399 | TFUS | BY174123 | 4405545113 | W1715 | ENOI | 81 | 3 | EFSW | Equipment Failure - Fuse Switch | N | top riser on switch burnt in clear made repairs cust back in lights jthom15 | -89.943 | 29.9001 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 7 | 2020 | 1323001850 | Yes | ALGIERS ELEC ONLY | FAIR | 134 | 2020-01-19 | 938 | XFMR | 1417734 | 4264345881 | W1713 | ENOI | 81 | 7 | ETRD | Equipment Failure - Transformer | N | Nick Carroll crew (Ollie Hull, Benjamin Clayborn, Brad Barrios) | -89.9873 | 29.9217 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 17 | 2020 | 1321917083 | Yes | EAST ORLEANS | FAIR | 136 | 2020-01-10 | 2312 | LFUS | 23780 | 42465497468 | 1602 | ENOI | 6 | 17 | UNKN | Inspected Unknown | N | Changed **TFUS 1298164 * 17 to LFUS 1298164 * 17** --- Refused B phase in cub 167 sw 23780--Inspected unknown jvickna | -89.9915 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 65 | 2020 | 1322523814 | Yes | EAST ORLEANS | FAIR | 139 | 2020-01-12 | 9035 | LFUS | 25724 | 4319150521 | 2214 | ENOI | 6 | 65 | EPRI | Equipment Failure - Primary Conductor | N | bad cable between cub 60 and vault 100 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 1 | 2020 | 1323003961 | Yes | ORLEANS | FAIR | 140 | 2020-01-19 | 140 | SECO | SECONDARY | 38600465860 | 1554 | ENOI | 1 | 1 | ESEC | Secondary/Service Conductor | N | bad jumper on secondary wire | -90.1147 | 29.9424 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Secondary Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 1 | 2020 | 1323217578 | Yes | ORLEANS | FAIR | 140 | 2020-01-26 | 140 | SERV | SERVICE | 39316462677 | 1924 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | Repaired neutral at weatherhead | -90.0921 | 29.9333 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 1 | 2020 | 1321749621 | Yes | ORLEANS | COLD | 142 | 2020-01-05 | 142 | SERV | SERVICE | 38103461220 | 2013 | ENOI | 1 | 1 | ECON | Equipment Failure - Connector / Sleeve | N | Changed **TFUS 549754 * 10 to SERV 549754 * 10** --- bad connection at weather head abengst | -90.1306 | 29.9298 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 19 | 2020 | 1323119085 | Yes | EAST ORLEANS | FAIR | 145 | 2020-01-22 | 2755 | LFUS | 25651 | 4338850670 | 2214 | ENOI | 6 | 19 | EELB | Equipment Failure - Elbow | N | bad ebow crew chad.. | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 76 | 2020 | 1322200807 | Yes | ORLEANS | THDR | 147 | 2020-01-11 | 11172 | LFUS | 27822 | 3801346713 | B0527 | ENOI | 1 | 76 | VLFL | Tree On Line Outside R.O.W | N | crew repaired shield wire damaged by tree | -90.1331 | 29.946 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 1 | 2020 | 1323248173 | Yes | ORLEANS | FAIR | 147 | 2020-01-27 | 147 | SERV | SERVICE | 39402478092 | 912 | ENOI | 1 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | spliced service and made new connections at weatherhead | -90.0889 | 29.9758 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 47 | 2020 | 1323159950 | Yes | ORLEANS | FAIR | 153 | 2020-01-23 | 7191 | LFUS | 28009 | 3863545809 | 1913 | ENOI | 1 | 47 | SCHD | Scheduled Interruption | N | crew was out there on a schduled outage | -90.1137 | 29.9209 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 51 | 2020 | 1323295246 | Yes | EAST ORLEANS | RAIN | 159 | 2020-01-29 | 8262 | DIS | 23316 | 4124747804 | 621 | ENOI | 6 | 51 | EARM | Equipment Failure - Crossarm | N | broke arm at disc. 25291 | -90.0308 | 29.975 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 126 | 2020 | 1321765323 | Yes | EAST ORLEANS | FAIR | 161 | 2020-01-06 | 14154 | SWIT | 25111 | 4246449716 | 1602 | ENOI | 6 | 126 | ESWC | Switching Cabinet | N | Crew replacing bad switching cabinet | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 162 | 2020 | 1323291398 | Yes | EAST ORLEANS | RAIN | 162 | 2020-01-29 | 26244 | RCLR | 23282 | 4122747950 | 621 | ENOI | 6 | 162 | EARM | Equipment Failure - Crossarm | N | broke crossarm at disc. 25291 | -90.0313 | 29.979 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 15 | 2020 | 1323070035 | Yes | ALGIERS ELEC ONLY | FAIR | 165 | 2020-01-21 | 2475 | TFUS | 1203436 | 4255145618 | W1714 | ENOI | 81 | 15 | UNKN | Inspected Unknown | N |  | -89.9903 | 29.9145 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 2 | 2020 | 1323217943 | Yes | EAST ORLEANS | FAIR | 173 | 2020-01-26 | 346 | TFUS | 32086 | 44464496384 | 1601 | ENOI | 6 | 2 | ASQL | Animal - Squirrel | N | squirrel took out transformer feeding building refused transfomre got great voltage now no one is here its a commercial customer closed today | -89.9283 | 30.0244 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 1 | 2020 | 1323087626 | Yes | EAST ORLEANS | FAIR | 175 | 2020-01-21 | 175 | TFUS | 65841 | 46077507365 | 1204 | ENOI | 6 | 1 | EPRI | Equipment Failure - Primary Conductor | N |  | -89.8769 | 30.054 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 24 | 2020 | 1323314806 | Yes | ORLEANS | FAIR | 182 | 2020-01-29 | 4368 | TFUS | 1533023 | 39840459058 | 2147 | ENOI | 1 | 24 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | no comments | -90.0758 | 29.9232 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70130 | 1
2020 | 3 | 2020 | 1323025386 | Yes | ORLEANS | FAIR | 189 | 2020-01-20 | 567 | TFUS | 32466 | 39602493949 | 509 | ENOI | 1 | 3 | ESEC | Secondary/Service Conductor | N | transformer back in and secondary picked back up | -90.0821 | 30.0192 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 12 | 2020 | 1323298113 | Yes | ALGIERS ELEC ONLY | FAIR | 199 | 2020-01-29 | 2388 | TFUS | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | SCHD | Scheduled Interruption | N | CREW OUTAGE | -89.9867 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 15 | 2020 | 1323063051 | Yes | ORLEANS | FAIR | 201 | 2020-01-21 | 3015 | SWIT | V10-17 | 38818496158 | 401 | ENOI | 1 | 15 | SCHD | Scheduled Interruption | N | recable job | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Switch | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70124 | 1
2020 | 3 | 2020 | 1323198606 | Yes | EAST ORLEANS | FAIR | 203 | 2020-01-25 | 609 | TFUS | 1460718 | 40760480182 | 622 | ENOI | 6 | 3 | EARM | Equipment Failure - Crossarm | N | replaced crossarm arm on dead end pole | -90.046 | 29.9811 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 16 | 2020 | 1323046635 | Yes | ORLEANS | FAIR | 208 | 2020-01-20 | 3328 | TFUS | 729472 | 38920475976 | 903 | ENOI | 1 | 16 | ECON | Equipment Failure - Connector / Sleeve | N | changed out connections at weather head. | -90.1041 | 29.9701 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 1
2020 | 75 | 2020 | 1321820126 | Yes | EAST ORLEANS | FAIR | 211 | 2020-01-07 | 15825 | LFUS | 27348 | 4264949768 | 1602 | ENOI | 6 | 75 | EPRI | Equipment Failure - Primary Conductor | N | bad cable from cubicle 6 to vault 1 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 16 | 2020 | 1321829805 | Yes | ORLEANS | FAIR | 211 | 2020-01-08 | 3376 | TFUS | 53182 | 38684487237 | 408 | ENOI | 1 | 16 | FOTH | Fire - Other (Describe in Remarks Field) | N | fire at location burnt wire down, transformer back in | -90.1114 | 30.0011 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 7 | 2020 | 1323232948 | Yes | ORLEANS | FAIR | 211 | 2020-01-27 | 1477 | TFUS | 59936 | 38748467302 | 1916 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1099 | 29.9463 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 1
2020 | 460 | 2020 | 1323115884 | Yes | ALGIERS ELEC ONLY | FAIR | 213 | 2020-01-22 | 97980 | LFUS | 1105 | 4195645775 | W0712 | ENOI | 81 | 460 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | L1105 was blown as well as subL34242, cause balloons on switch, rc 1-22-20 | -90.009 | 29.919 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 1 | 2020 | 1322951627 | Yes | ALGIERS ELEC ONLY | FAIR | 215 | 2020-01-18 | 215 | SERV | METER | 4164146240 | W0725 | ENOI | 81 | 1 | MTEX | Meter Exchange | N | stolen meter, mtr change ticket to be made, rc | -90.0187 | 29.9319 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 2 | 2020 | 1322467215 | Yes | ALGIERS ELEC ONLY | RAIN | 216 | 2020-01-12 | 432 | TFUS | BY174099 | 4417845173 | W1715 | ENOI | 81 | 2 | EFSW | Equipment Failure - Fuse Switch | N | top riser on switch burnt in the clear made repairs cust back in light jthom15 | -89.9391 | 29.9017 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 211 | 2020 | 1323138909 | Yes | ALGIERS ELEC ONLY | THDR | 219 | 2020-01-23 | 46209 | RCLR | 33772 | 4313545406 | W1715 | ENOI | 81 | 211 | EINS | Equipment Failure - Insulator | N | BCLEME1 | -89.9719 | 29.9085 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 11 | 2020 | 1323304450 | Yes | ORLEANS | FAIR | 220 | 2020-01-29 | 2420 | DIS | 25476 | 3861947481 | 2011 | ENOI | 1 | 11 | EMER | Emergency Switching | N | SHIELD WIRE DOWN | -90.1137 | 29.9669 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 11 | 2020 | 1323088737 | Yes | EAST ORLEANS | FAIR | 226 | 2020-01-21 | 2486 | TFUS | 23813 | 40482495074 | 506 | ENOI | 6 | 11 | ECON | Equipment Failure - Connector / Sleeve | N | burnt trans lead ..replaced | -90.0541 | 30.0221 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 125 | 2020 | 1323111678 | Yes | ORLEANS | FAIR | 227 | 2020-01-22 | 28375 | LFUS | 21686 | 3971247620 | 907 | ENOI | 1 | 125 | VHCL | Vehicle | N | dump truck hit pole PID IN PROGRESS (Unable to to find info on dump truck that hit the pole) | -90.0791 | 29.9705 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | D | Council District D | Jared Brossett | 70119 | 1
2020 | 12 | 2020 | 1323088224 | Yes | EAST ORLEANS | FAIR | 228 | 2020-01-21 | 2736 | TFUS | 1048655 | 43916511664 | 2217 | ENOI | 6 | 12 | EABS | Equipment Failure - Air Break / Disconnect Switch | N | outage is due to crew picking up wire on curran. avon park is inside isolated portion of feeder thats under clearance | -89.945 | 30.0667 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 23 | 2020 | 1322735698 | Yes | EAST ORLEANS | FAIR | 240 | 2020-01-14 | 5520 | TFUS | 67500 | 40484476639 | 623 | ENOI | 6 | 23 | SCHD | Scheduled Interruption | N | ppole transfer | -90.0547 | 29.9714 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 28 | 2020 | 1323337190 | Yes | ORLEANS | FAIR | 241 | 2020-01-30 | 6748 | SWIT | 7 | 38833494311 | 401 | ENOI | 1 | 28 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Switch | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70124 | 1
2020 | 17 | 2020 | 1322615999 | Yes | ORLEANS | FAIR | 242 | 2020-01-13 | 4114 | DIS | 27125 | 38503474755 | 2011 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | outage required to safely replace rotten xarms located at the intersection of Olive and Leonidas | -90.1174 | 29.9667 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 276 | 2020 | 1321835001 | Yes | EAST ORLEANS | FAIR | 247 | 2020-01-08 | 68172 | LFUS | 26252 | 4360850642 | 2214 | ENOI | 6 | 276 | ETRD | Equipment Failure - Transformer | N | crew to replace | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 3 | 2020 | 1323037426 | Yes | EAST ORLEANS | FAIR | 249 | 2020-01-20 | 747 | XFMR | 1193965 | 42845504050 | 2216 | ENOI | 6 | 3 | ETRD | Equipment Failure - Transformer | N | bad transformer, crew in route | -89.9791 | 30.0459 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 4 | 2020 | 1321831987 | Yes | EAST ORLEANS | FAIR | 260 | 2020-01-08 | 1040 | TFUS | 79575 | 42517501966 | 2212 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N |  | -89.9896 | 30.0404 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 172 | 2020 | 1323119101 | Yes | EAST ORLEANS | FAIR | 278 | 2020-01-22 | 47816 | LFUS | 25610 | 4335750498 | 2214 | ENOI | 6 | 172 | EELB | Equipment Failure - Elbow | N | bad elbow | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 1 | 2020 | 1323284518 | Yes | EAST ORLEANS | FAIR | 303 | 2020-01-28 | 303 | SERV | SERVICE | 42166494030 | 1607 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | picked up wire, good voltage | -90.001 | 30.0187 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 90 | 2020 | 1323344448 | Yes | EAST ORLEANS | FAIR | 303 | 2020-01-30 | 27270 | LFUS | 27340-F | 4482350242 | 1205 | ENOI | 6 | 90 | ETRD | Equipment Failure - Transformer | N |  | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 44 | 2020 | 1321707115 | Yes | EAST ORLEANS | FAIR | 310 | 2020-01-03 | 13640 | LFUS | 27215 | 4204249890 | 2211 | ENOI | 6 | 44 | EPRI | Equipment Failure - Primary Conductor | N | crew to repair | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 1 | 2020 | 1322667082 | Yes | ALGIERS ELEC ONLY | FOGG | 311 | 2020-01-13 | 311 | SERV | SERVICE | 4136546563 | W0725 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N | Changed **TFUS BY88464 37 to SERV BY88464 1** --- old service line went bad. changed out line and good voltage checked mtaruc | -90.0274 | 29.9409 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 12 | 2020 | 1323251479 | Yes | ALGIERS ELEC ONLY | FAIR | 317 | 2020-01-27 | 3804 | TFUS | BY124694 | 4266245914 | W1713 | ENOI | 81 | 12 | EFLK | Equipment Failure - Fuse Link | N | refused blown fuse | -89.9867 | 29.9226 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 1
2020 | 262 | 2020 | 1323085775 | Yes | EAST ORLEANS | FAIR | 320 | 2020-01-21 | 83840 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 262 | EPRI | Equipment Failure - Primary Conductor | N | wire down in marsh | -89.8028 | 30.0694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 144 | 2020 | 1323293386 | Yes | EAST ORLEANS | RAIN | 321 | 2020-01-29 | 46224 | DIS | 23061 | 4122747782 | 621 | ENOI | 6 | 144 | EARM | Equipment Failure - Crossarm | N | broke crossarm at disc. 25291 | -90.0313 | 29.9745 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 1
2020 | 1 | 2020 | 1322323741 | Yes | ALGIERS ELEC ONLY | THDR | 330 | 2020-01-11 | 330 | TFUS | 1543046 | 4141646669 | W1725 | ENOI | 81 | 1 | EMER | Emergency Switching | N | Opened in order for crew to make repairs. per B. rissuto............PC | -90.0258 | 29.9437 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Emergency Switching | DLIN | C | Council District C | Kristin Palmer | 70114 | 1
2020 | 16 | 2020 | 1323357585 | Yes | ORLEANS | FAIR | 343 | 2020-01-30 | 5488 | LFUS | 17679 | 38333485489 | 400 | ENOI | 1 | 16 | VHCL | Vehicle | N | SENT TO CLAIMS AS MINIMAL CLAIM. NO CAR AT SCENE | -90.1224 | 29.9964 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 1
2020 | 5 | 2020 | 1323046317 | Yes | EAST ORLEANS | FAIR | 352 | 2020-01-20 | 1760 | TFUS | 1193973 | 40899482518 | 611 | ENOI | 6 | 5 | ESEC | Secondary/Service Conductor | N | repairs at transformer | -90.0415 | 29.9874 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 1
2020 | 224 | 2020 | 1321627546 | Yes | ORLEANS | FAIR | 355 | 2020-01-01 | 79520 | LFUS | 28059 | 3928646516 | 1915 | ENOI | 1 | 224 | VHCL | Vehicle | N | car hit pole; 5 broke poles and wire down | -90.0929 | 29.9402 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 8 | 2020 | 1323262374 | Yes | ORLEANS | FAIR | 357 | 2020-01-28 | 2856 | TFUS | 62321 | 39300467704 | 2021 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0925 | 29.9471 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 86 | 2020 | 1322194593 | Yes | ORLEANS | THDR | 361 | 2020-01-11 | 31046 | LFUS | 27790 | 39932484636 | 1703 | ENOI | 1 | 86 | EARM | Equipment Failure - Crossarm | N | crew replaced crossarm and repaired pole | -90.072 | 29.9935 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 1
2020 | 234 | 2020 | 1323299416 | Yes | ORLEANS | FAIR | 384 | 2020-01-29 | 89856 | LFUS | 37908 | 3865747472 | 2017 | ENOI | 1 | 234 | ECNS | Equipment Failure - Connector Sleeve | N | SHIELD WIRE DOWN | -90.1124 | 29.9666 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 1
2020 | 7 | 2020 | 1323295995 | Yes | ORLEANS | RAIN | 393 | 2020-01-29 | 2751 | TFUS | 1590194 | 39330467050 | 2021 | ENOI | 1 | 7 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0917 | 29.9454 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70125 | 1
2020 | 17 | 2020 | 1323248150 | Yes | ORLEANS | FAIR | 399 | 2020-01-27 | 6783 | XFMR | 62309 | 39410465886 | 1915 | ENOI | 1 | 17 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.089 | 29.9421 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 253 | 2020 | 1323053914 | Yes | EAST ORLEANS | FAIR | 401 | 2020-01-21 | 101453 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 253 | ETRD | Equipment Failure - Transformer | N | replaced transformer and lateral back in | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 614 | 2020 | 1323087728 | Yes | EAST ORLEANS | FAIR | 409 | 2020-01-21 | 251126 | RCLR | 85388 | 4373351112 | 2217 | ENOI | 6 | 614 | EPRI | Equipment Failure - Primary Conductor | N | wiredown | -89.951 | 30.0652 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 41 | 2020 | 1322465744 | Yes | ORLEANS | FAIR | 434 | 2020-01-12 | 17794 | DIS | 14349 | 3982346566 | 2137 | ENOI | 1 | 41 | EMER | Emergency Switching | N | broke pole, crew on site | -90.0761 | 29.9413 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70113 | 1
2020 | 263 | 2020 | 1323053986 | Yes | EAST ORLEANS | FAIR | 463 | 2020-01-21 | 121769 | RCLR | 22184 | 48411513283 | 1204 | ENOI | 6 | 263 | EPRI | Equipment Failure - Primary Conductor | N | primary wire down | -89.8028 | 30.0694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 1
2020 | 110 | 2020 | 1323217422 | Yes | EAST ORLEANS | FAIR | 464 | 2020-01-26 | 51040 | LFUS | 27177 | 4351250071 | 1609 | ENOI | 6 | 110 | ETRD | Equipment Failure - Transformer | N | crew changed out bad transformer | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 52 | 2020 | 1323254359 | Yes | ORLEANS | FAIR | 481 | 2020-01-27 | 25012 | XFMR | 1413671 | 3986247585 | 907 | ENOI | 1 | 52 | ETRD | Equipment Failure - Transformer | N | bad transformer changed out, good voltager now | -90.0745 | 29.9694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70116 | 1
2020 | 99 | 2020 | 1323233258 | Yes | EAST ORLEANS | FAIR | 507 | 2020-01-27 | 50193 | LFUS | 27653 | 4289350637 | 2215 | ENOI | 6 | 99 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9777 | 30.0523 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 1
2020 | 9 | 2020 | 1323084922 | Yes | EAST ORLEANS | FAIR | 524 | 2020-01-21 | 4716 | TFUS | 1315139 | 43498509515 | 2217 | ENOI | 6 | 9 | EABS | Equipment Failure - Air Break / Disconnect Switch | N |  | -89.9583 | 30.0609 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 1
2020 | 51 | 2020 | 1323083919 | Yes | EAST ORLEANS | FAIR | 576 | 2020-01-21 | 29376 | LFUS | 24971 | 4214250165 | 2212 | ENOI | 6 | 51 | ETRD | Equipment Failure - Transformer | N | Failed padmount transformer | -90.0015 | 30.0396 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 9 | 2020 | 1323082060 | Yes | EAST ORLEANS | FAIR | 640 | 2020-01-21 | 5760 | XFMR | 1495749 | 40463475459 | 623 | ENOI | 6 | 9 | ETRD | Equipment Failure - Transformer | N | crew changedtransformer | -90.0556 | 29.9681 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 1
2020 | 24 | 2020 | 1323267264 | Yes | ORLEANS | FAIR | 692 | 2020-01-28 | 16608 | TFUS | 603506 | 38759464546 | 1554 | ENOI | 1 | 24 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1097 | 29.9386 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 14 | 2020 | 1321631146 | Yes | ORLEANS | FAIR | 904 | 2020-01-01 | 12656 | OPEN | 3917946550 | 3917946550 | 1915 | ENOI | 1 | 14 | VHCL | Vehicle | N | car hit pole; 5 broke poles and wire down, PID chg to NO, related to #1321627546 (DGault) | -90.0964 | 29.9411 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Open | Public Damage | DLIN | B | Council District B | Jay Banks | 70115 | 1
2020 | 12 | 2020 | 1323232466 | Yes | EAST ORLEANS | FAIR | 1673 | 2020-01-27 | 20076 | TFUS | 1313464 | 41862495089 | 1610 | ENOI | 6 | 12 | ETRD | Equipment Failure - Transformer | N | bad submersible;will be out until tomorrow morning | -90.0107 | 30.0217 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 1
2020 | 3 | 2020 | 1324170082 | Yes | EAST ORLEANS | FAIR | 15 | 2020-02-19 | 45 | TFUS | 62400 | 42950505451 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | crew is onsite | -89.976 | 30.0498 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 6 | 2020 | 1324396947 | Yes | EAST ORLEANS | FAIR | 15 | 2020-02-23 | 90 | TFUS | 73309 | 41856476262 | 2325 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0114 | 29.97 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 14 | 2020 | 1324463884 | Yes | ORLEANS | FAIR | 17 | 2020-02-24 | 238 | LFUS | 21578 | 3886948465 | 904 | ENOI | 1 | 14 | EARM | Equipment Failure - Crossarm | N |  | -90.1055 | 29.9938 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 17 | 2020 | 1323822707 | Yes | ORLEANS | FAIR | 19 | 2020-02-11 | 323 | TFUS | 642509 | 39383459492 | 2147 | ENOI | 1 | 17 | SCHD | Scheduled Interruption | N | scheduled outage | -90.0902 | 29.9247 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 222 | 2020 | 1323655478 | Yes | EAST ORLEANS | WIND | 21 | 2020-02-07 | 4662 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 222 | EARM | Equipment Failure - Crossarm | N |  | -90.0021 | 29.9747 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 68 | 2020 | 1324566317 | Yes | ORLEANS | FAIR | 21 | 2020-02-26 | 1428 | LFUS | 33137 | 3866247573 | 2026 | ENOI | 1 | 68 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1125 | 29.9694 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 4 | 2020 | 1324676386 | Yes | EAST ORLEANS | FAIR | 21 | 2020-02-28 | 84 | TFUS | 60105 | 42939493496 | 1604 | ENOI | 6 | 4 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -89.9765 | 30.0171 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1 | 2020 | 1324005232 | Yes | ORLEANS | FAIR | 23 | 2020-02-15 | 23 | SECO | METER | 39473478021 | 912 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | 3128 dumaine AMI mtr had open indication AMOC doesnt work weekends and DOC doesnt have control to close mtrs changed to mtr#8180311 sn-57104979 r-00000 | -90.0866 | 29.9755 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Secondary Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 2
2020 | 119 | 2020 | 1323549856 | Yes | EAST ORLEANS | THDR | 25 | 2020-02-05 | 2975 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 119 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Crews found balloons on feeder on Florida & Egania | -90.0441 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1917 | 2020 | 1323805621 | Yes | ORLEANS | FAIR | 26 | 2020-02-11 | 49842 | SBKR | 2146 | 4012946121 | 2146 | ENOI | 1 | 1917 | EMER | Emergency Switching | N | dropped out for the crew , whencrew was in the process of closing in a laterial the switch came off of the arm and was being supported by the switch stick. | -90.0665 | 29.9291 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 118 | 2020 | 1324456985 | Yes | EAST ORLEANS | FAIR | 28 | 2020-02-24 | 3304 | SBKR | 612 | 4081648420 | 612 | ENOI | 6 | 118 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Serviceman patrolled feeder the next morning & found balloons on line at Florida & Gorden Sts. Removed okay | -90.0441 | 29.9921 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1462 | 2020 | 1324238968 | Yes | ORLEANS | RAIN | 32 | 2020-02-20 | 46784 | SBKR | 1702 | 4024148726 | 1702 | ENOI | 1 | 1462 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | Serviceman found a piece of molding fell onto primary, cleared object & feeder restored okay | -90.0621 | 30.0007 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Substation Breaker | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1288 | 2020 | 1323526756 | Yes | ORLEANS | FAIR | 36 | 2020-02-05 | 46368 | DIS | 21967 | 3862946737 | 2024 | ENOI | 1 | 1288 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1138 | 29.9464 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 2
2020 | 16 | 2020 | 1324336355 | Yes | EAST ORLEANS | FAIR | 37 | 2020-02-21 | 592 | TFUS | 54971 | 40370486325 | 1708 | ENOI | 6 | 16 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0581 | 29.9981 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 123 | 2020 | 1324415315 | Yes | ORLEANS | FAIR | 38 | 2020-02-24 | 4674 | LFUS | 27615 | 3972747795 | 615 | ENOI | 1 | 123 | SCHD | Scheduled Interruption | N | crew changing out pole | -90.0786 | 29.9753 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70119 | 2
2020 | 21 | 2020 | 1324132510 | Yes | ALGIERS ELEC ONLY | FAIR | 41 | 2020-02-18 | 861 | TFUS | BY149697 | 4115346444 | W1725 | ENOI | 81 | 21 | SCHD | Scheduled Interruption | N | opened transforemr to replace cut out (pwd) | -90.0342 | 29.9376 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 3 | 2020 | 1323551129 | Yes | ORLEANS | WIND | 44 | 2020-02-05 | 132 | TFUS | 76190 | 38463461461 | 1917 | ENOI | 1 | 3 | LGHT | Lightning | N | weather | -90.1191 | 29.9303 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 7 | 2020 | 1323551125 | Yes | ORLEANS | WIND | 45 | 2020-02-05 | 315 | TFUS | 1099405 | 39552488027 | 1703 | ENOI | 1 | 7 | LGHT | Lightning | N | weather | -90.0838 | 30.0031 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 241 | 2020 | 1323644227 | Yes | EAST ORLEANS | WIND | 47 | 2020-02-06 | 11327 | RCLR | 10123 | 4137849331 | 1001 | ENOI | 6 | 241 | UNKN | Inspected Unknown | N | high winds moved through area at time of lockout | -90.026 | 30.0169 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Recloser | Other | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 10 | 2020 | 1324063576 | Yes | EAST ORLEANS | FAIR | 50 | 2020-02-17 | 500 | TFUS | 61817 | 40999477699 | 611 | ENOI | 6 | 10 | SCHD | Scheduled Interruption | N | contractor are transfering pole they have pot out | -90.0384 | 29.9742 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 102 | 2020 | 1324519542 | Yes | ALGIERS ELEC ONLY | FAIR | 50 | 2020-02-26 | 5100 | RCLR | 5070 | 4119546688 | W1725 | ENOI | 81 | 102 | LGHT | Lightning | N | closed back in per I. Caruthers..........PC | -90.0326 | 29.9444 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Recloser | Lightning | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 115 | 2020 | 1323805002 | Yes | ORLEANS | FAIR | 52 | 2020-02-11 | 5980 | LFUS | F05219 | 3960746184 | 2146 | ENOI | 1 | 115 | SCHD | Scheduled Interruption | N | crew onsite transferring pole | -90.083 | 29.9309 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 14 | 2020 | 1323616190 | Yes | ORLEANS | RAIN | 53 | 2020-02-06 | 742 | TFUS | 641930 | 40302484935 | 1708 | ENOI | 1 | 14 | VOHL | Overhanging Limb | N | limb fell across bushing and riser on transformer. per 310 | -90.0602 | 29.9942 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 12 | 2020 | 1324081149 | Yes | EAST ORLEANS | FAIR | 53 | 2020-02-18 | 636 | XFMR | 633552 | 40981476969 | 611 | ENOI | 6 | 12 | SCHD | Scheduled Interruption | N | crew onsite removing old transformer | -90.0389 | 29.9722 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 23 | 2020 | 1323924228 | Yes | EAST ORLEANS | FAIR | 55 | 2020-02-13 | 1265 | LFUS | 21736 | 4186649358 | 1612 | ENOI | 6 | 23 | SCHD | Scheduled Interruption | N | crew got lateral back in | -90.0105 | 30.0175 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 735 | 2020 | 1323525567 | Yes | ORLEANS | FAIR | 56 | 2020-02-05 | 47040 | DIS | 23899 | 3851646958 | 2016 | ENOI | 1 | 735 | VHCL | Vehicle | N | car broke pole; shield wire down PID IN PROGRESS- WAITING ON CONTRACTORS | -90.1171 | 29.9525 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 8 | 2020 | 1324616546 | Yes | ORLEANS | FAIR | 56 | 2020-02-27 | 448 | TFUS | 60601 | 39064458650 | 1923 | ENOI | 1 | 8 | SCHD | Scheduled Interruption | N | scheduled outage | -90.1004 | 29.9224 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 44 | 2020 | 1323525769 | Yes | ORLEANS | FAIR | 68 | 2020-02-05 | 3212 | DIS | 23892 | 3854246996 | 2016 | ENOI | 1 | 44 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1163 | 29.9536 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70125 | 2
2020 | 4 | 2020 | 1323577065 | Yes | EAST ORLEANS | THDR | 70 | 2020-02-05 | 280 | TFUS | 73153 | 41749477220 | 2325 | ENOI | 6 | 4 | LGHT | Lightning | N | refused B and C phase taken out by bad weather | -90.0149 | 29.9726 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 7 | 2020 | 1324294885 | Yes | EAST ORLEANS | WIND | 72 | 2020-02-20 | 504 | TFUS | 57875 | 40375486483 | 1708 | ENOI | 6 | 7 | EFSW | Equipment Failure - Fuse Switch | N | c phase fuse burnt in half..refused | -90.058 | 29.9985 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1166 | 2020 | 1323550211 | Yes | EAST ORLEANS | THDR | 73 | 2020-02-05 | 85118 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 1166 | EPRI | Equipment Failure - Primary Conductor | N | crew onsiyte picking up lateral | -90.0021 | 29.9747 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 10 | 2020 | 1323664900 | Yes | ORLEANS | FAIR | 73 | 2020-02-07 | 730 | TFUS | 1585375 | 39461462505 | 1924 | ENOI | 1 | 10 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | no comments | -90.0875 | 29.9329 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 279 | 2020 | 1323663056 | Yes | EAST ORLEANS | THDR | 78 | 2020-02-07 | 21762 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 279 | EARR | Equipment Failure - Arrestor | N | blown arrestor | -90.0337 | 29.9718 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 28 | 2020 | 1324398683 | Yes | ORLEANS | FAIR | 78 | 2020-02-23 | 2184 | LFUS | 21435 | 3883945809 | 1921 | ENOI | 1 | 28 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | removed balloons off of line; a phase blown KC | -90.1073 | 29.9209 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 11 | 2020 | 1324416799 | Yes | EAST ORLEANS | FAIR | 78 | 2020-02-24 | 858 | TFUS | 71154 | 40600474196 | 623 | ENOI | 6 | 11 | ASQL | Animal - Squirrel | N | animal took out transformer re fused transformer and lights back on squirrel got into secondary | -90.0511 | 29.9648 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 1 | 2020 | 1323764163 | Yes | EAST ORLEANS | WIND | 79 | 2020-02-10 | 79 | LFUS | 27269 | 41375485531 | 616 | ENOI | 6 | 1 | EFLK | Equipment Failure - Fuse Link | N | B and C Phase fuse were blown at the lateral switch. Inspected line and determined that #6 copper phases blew together with wind. Made cust contact. Back in lights. | -90.0263 | 29.9955 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1 | 2020 | 1323491980 | Yes | ORLEANS | FAIR | 80 | 2020-02-04 | 80 | SERV | METER | 38614466197 | 1554 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | ami meter open internally | -90.1143 | 29.9433 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Service Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 64 | 2020 | 1323649733 | Yes | ORLEANS | WIND | 80 | 2020-02-06 | 5120 | LFUS | 28068 | 3960648669 | 1703 | ENOI | 1 | 64 | EPRI | Equipment Failure - Primary Conductor | N | high wind refused okay | -90.0821 | 29.9993 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 7 | 2020 | 1323543759 | Yes | ORLEANS | FAIR | 84 | 2020-02-05 | 588 | TFUS | 79233 | 38298464075 | 2013 | ENOI | 1 | 7 | VLGL | Tree/Limb Growing Inside R.O.W. | N | palm tree branches hitting power lines in rear, trimmed what could get need vegetation to clear lines vege ticket created jmulle2 | -90.1242 | 29.9374 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 42 | 2020 | 1323799758 | Yes | EAST ORLEANS | FAIR | 86 | 2020-02-10 | 3612 | LFUS | 17586 | 4099049317 | 508 | ENOI | 6 | 42 | EMER | Emergency Switching | N | crew straighting a pole | -90.0383 | 30.0167 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Emergency Switching | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 1 | 2020 | 1324109171 | Yes | ALGIERS ELEC ONLY | FAIR | 86 | 2020-02-18 | 86 | SERV | SERVICE COND | 4212046002 | W1726 | ENOI | 81 | 1 | ESEC | Secondary/Service Conductor | N | Replaced connection on service line............PC | -90.0036 | 29.9252 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 2
2020 | 6 | 2020 | 1323534021 | Yes | EAST ORLEANS | RAIN | 87 | 2020-02-05 | 522 | TFUS | 66110 | 43572495525 | 1601 | ENOI | 6 | 6 | LGHT | Lightning | N | weather | -89.9566 | 30.0223 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 8 | 2020 | 1323613484 | Yes | ORLEANS | RAIN | 89 | 2020-02-06 | 712 | TFUS | 60606 | 39493474594 | 907 | ENOI | 1 | 8 | ESEC | Secondary/Service Conductor | N | service wire failure caused transformer to fault. | -90.0861 | 29.9661 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 2
2020 | 127 | 2020 | 1323889600 | Yes | EAST ORLEANS | FAIR | 89 | 2020-02-12 | 11303 | LFUS | 27886 | 4082247647 | 622 | ENOI | 6 | 127 | UNKN | Inspected Unknown | N | Refused C phase at sw# 27886--Inspect unknown | -90.0441 | 29.9707 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 4 | 2020 | 1323938290 | Yes | EAST ORLEANS | FAIR | 89 | 2020-02-13 | 356 | TFUS | 32883 | 41762479118 | 612 | ENOI | 6 | 4 | VINE | Vine Growing into Line | N | dead vines..clear | -90.0144 | 29.9778 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 427 | 2020 | 1323653581 | Yes | EAST ORLEANS | WIND | 91 | 2020-02-07 | 38857 | SBKR | 2347 | 4215247804 | 2347 | ENOI | 6 | 427 | EARM | Equipment Failure - Crossarm | N | Recloser was locked out; See recloser case | -90.0021 | 29.9747 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 82 | 2020 | 1323525729 | Yes | ORLEANS | FAIR | 93 | 2020-02-05 | 7954 | DIS | 24330 | 3852446954 | 2016 | ENOI | 1 | 82 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1168 | 29.9525 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 10 | 2020 | 1324327115 | Yes | ORLEANS | FAIR | 94 | 2020-02-21 | 940 | TFUS | 51666 | 39674493122 | 509 | ENOI | 1 | 10 | EFLK | Equipment Failure - Fuse Link | N | refused ok | -90.0799 | 30.017 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 93 | 2020 | 1323549802 | Yes | EAST ORLEANS | THDR | 95 | 2020-02-05 | 8835 | SBKR | 621 | 4081848423 | 621 | ENOI | 6 | 93 | ECNS | Equipment Failure - Connector Sleeve | N | crew tripped due to down wire due to failed kearney coonection | -90.044 | 29.9922 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Substation Breaker | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 32 | 2020 | 1323593781 | Yes | EAST ORLEANS | FAIR | 100 | 2020-02-05 | 3200 | LFUS | 27190 | 4450051090 | 2213 | ENOI | 6 | 32 | EPRI | Equipment Failure - Primary Conductor | N |  | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 94 | 2020 | 1324247481 | Yes | ALGIERS ELEC ONLY | THDR | 103 | 2020-02-20 | 9682 | RCLR | 1136 | 4182146253 | W0722 | ENOI | 81 | 94 | LGHT | Lightning | N | lighting took out center phase recloser | -90.0129 | 29.9323 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Recloser | Lightning | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 14 | 2020 | 1324202736 | Yes | EAST ORLEANS | RAIN | 103 | 2020-02-20 | 1442 | LFUS | 21695 | 4038148637 | 1708 | ENOI | 6 | 14 | EFLK | Equipment Failure - Fuse Link | N | blown fuse on transformer and lateral taken out by bad weather | -90.0579 | 29.9982 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 50 | 2020 | 1324308301 | Yes | ORLEANS | WIND | 104 | 2020-02-20 | 5200 | LFUS | 44646 | 3853148813 | 410 | ENOI | 1 | 50 | EFLK | Equipment Failure - Fuse Link | N | Refused latteral | -90.116 | 30.0036 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 78 | 2020 | 1324642076 | Yes | EAST ORLEANS | FAIR | 104 | 2020-02-28 | 8112 | LFUS | 27321-F | 4235149906 | 2211 | ENOI | 6 | 78 | UNKN | Inspected Unknown | N | c phase blown; refused and held | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 114 | 2020 | 1323981833 | Yes | ORLEANS | FAIR | 105 | 2020-02-14 | 11970 | LFUS | 21458 | 3906145893 | 1923 | ENOI | 1 | 114 | UNKN | Inspected Unknown | N | refused okk | -90.1004 | 29.9231 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 140 | 2020 | 1323713292 | Yes | ORLEANS | FAIR | 106 | 2020-02-08 | 14840 | LFUS | 37734 | 4029548586 | 1708 | ENOI | 1 | 140 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | b phase only | -90.0603 | 29.9969 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1 | 2020 | 1323546098 | Yes | EAST ORLEANS | RAIN | 107 | 2020-02-05 | 107 | LFUS | 83983 | 4101048935 | 617 | ENOI | 6 | 1 | VINE | Vine Growing into Line | N | John Domangue cleared vines on pole and refused lateral per OC | -90.0377 | 30.0062 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 134 | 2020 | 1323441474 | Yes | EAST ORLEANS | FAIR | 108 | 2020-02-03 | 14472 | LFUS | 21152 | 4051147776 | 623 | ENOI | 6 | 134 | SCHD | Scheduled Interruption | N | crew onsite making repairs | -90.0538 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 75 | 2020 | 1323552613 | Yes | ORLEANS | WIND | 112 | 2020-02-05 | 8400 | DIS | 25426 | 3895046772 | 1553 | ENOI | 1 | 75 | EMER | Emergency Switching | N | Taken out for safety to replace burnt cross-arm & repair damaged phase | -90.1036 | 29.9474 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | B | Council District B | Jay Banks | 70125 | 2
2020 | 97 | 2020 | 1323767376 | Yes | EAST ORLEANS | FAIR | 112 | 2020-02-10 | 10864 | LFUS | 26127 | 4386451333 | 2223 | ENOI | 6 | 97 | SCHD | Scheduled Interruption | N | Contractor had outage for reliability work | -89.9466 | 30.0712 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 11 | 2020 | 1323610473 | Yes | ORLEANS | WIND | 114 | 2020-02-06 | 1254 | TFUS | 74399 | 40386478720 | 1709 | ENOI | 1 | 11 | LGHT | Lightning | N | refused transformer taken out by weather | -90.0577 | 29.9772 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70116 | 2
2020 | 48 | 2020 | 1323655644 | Yes | EAST ORLEANS | WIND | 114 | 2020-02-07 | 5472 | LFUS | 52377 | 4268250430 | 2215 | ENOI | 6 | 48 | ESEC | Secondary/Service Conductor | N |  | -89.9844 | 30.0466 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 26 | 2020 | 1323662339 | Yes | EAST ORLEANS | THDR | 115 | 2020-02-07 | 2990 | LFUS | 37094 | 4106547707 | 611 | ENOI | 6 | 26 | EARR | Equipment Failure - Arrestor | N | failed lightning arrestor on lateral/cleared/refused lateral | -90.0364 | 29.9723 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 124 | 2020 | 1323665502 | Yes | EAST ORLEANS | FAIR | 116 | 2020-02-07 | 14384 | LFUS | 28077 | 4115047686 | 611 | ENOI | 6 | 124 | EFLK | Equipment Failure - Fuse Link | N | crew restored lateral | -90.0337 | 29.9718 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 7 | 2020 | 1323939896 | Yes | ORLEANS | FAIR | 117 | 2020-02-13 | 819 | XFMR | 1349264 | 38517477512 | 2026 | ENOI | 1 | 7 | ETRD | Equipment Failure - Transformer | N | crew to change transformer | -90.1169 | 29.9743 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 107 | 2020 | 1323849876 | Yes | EAST ORLEANS | FAIR | 120 | 2020-02-12 | 12840 | LFUS | 21798 | 4382851374 | 2223 | ENOI | 6 | 107 | SCHD | Scheduled Interruption | N |  | -89.9477 | 30.0724 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 122 | 2020 | 1323630435 | Yes | EAST ORLEANS | THDR | 121 | 2020-02-06 | 14762 | LFUS | 21152 | 4051147776 | 623 | ENOI | 6 | 122 | SCHD | Scheduled Interruption | N |  | -90.0538 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 16 | 2020 | 1323614486 | Yes | EAST ORLEANS | RAIN | 123 | 2020-02-06 | 1968 | TFUS | 1155554 | 40524474979 | 2347 | ENOI | 6 | 16 | VOHL | Overhanging Limb | N | removed palm limbs off of transformer reuse ok customer back in lights | -90.0536 | 29.9667 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 57 | 2020 | 1323673353 | Yes | EAST ORLEANS | FAIR | 124 | 2020-02-07 | 7068 | LFUS | 37150 | 40855477822 | 622 | ENOI | 6 | 57 | ECNS | Equipment Failure - Connector Sleeve | N | made new kearney connection repair at trans. | -90.0431 | 29.9745 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 3 | 2020 | 1323734811 | Yes | ORLEANS | FAIR | 124 | 2020-02-09 | 372 | TFUS | 32116 | 39340459980 | 2147 | ENOI | 1 | 3 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons. refused ok RELATED TO TKT# 1323734811 (AKS) | -90.0915 | 29.9259 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 84 | 2020 | 1324375554 | Yes | ORLEANS | FAIR | 126 | 2020-02-22 | 10584 | LFUS | 21671 | 3979148836 | 1704 | ENOI | 1 | 84 | ETRD | Equipment Failure - Transformer | N | crew replaced xfmr | -90.0762 | 30.0038 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 1 | 2020 | 1323479576 | Yes | EAST ORLEANS | FAIR | 131 | 2020-02-03 | 131 | TFUS | 1177611 | 4066949720 | 508 | ENOI | 6 | 1 | UNKN | Inspected Unknown | N | fuse blown on a phase | -90.0482 | 30.0279 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70148 | 2
2020 | 8 | 2020 | 1324142737 | Yes | ORLEANS | FAIR | 133 | 2020-02-19 | 1064 | TFUS | 21729 | 38502489222 | 410 | ENOI | 1 | 8 | EMER | Emergency Switching | N | Out for safety of crew to replace pole | -90.117 | 30.0065 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Transformer Fuse | Emergency Switching | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 116 | 2020 | 1324305126 | Yes | ALGIERS ELEC ONLY | WIND | 133 | 2020-02-20 | 15428 | LFUS | 34312 | 4265245351 | W1712 | ENOI | 81 | 116 | EOTH | Equipment Failure - Other (Describe in Remarks Fie | N | hot line clamp burnt off stirrup, replaced and repaired, cust lights restored | -89.9868 | 29.9072 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70131 | 2
2020 | 745 | 2020 | 1323559097 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 | 73010 | DIS | 25215 | 4103247998 | 621 | ENOI | 6 | 745 | ECNS | Equipment Failure - Connector Sleeve | N | crew picking up wire due to a failed kearney connection | -90.0374 | 29.9803 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 198 | 2020 | 1323558838 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 | 26928 | DIS | 25301 | 4100148012 | 621 | ENOI | 6 | 198 | ECNS | Equipment Failure - Connector Sleeve | N | crew onsite making repairs: Wire burned down due to a failed kearney connection | -90.0384 | 29.9808 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 1 | 2020 | 1323548792 | Yes | EAST ORLEANS | THDR | 134 | 2020-02-05 | 134 | TFUS | 1483809 | 40334487975 | 1702 | ENOI | 6 | 1 | LGHT | Lightning | N | refused transformer taken out by molding falling across switch | -90.0592 | 30.0025 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 28 | 2020 | 1323400798 | Yes | EAST ORLEANS | FOGG | 137 | 2020-02-01 | 3836 | LFUS | 27891 | 4156747196 | 2346 | ENOI | 6 | 28 | FOBJ | Foreign Objects (Describe in Remarks Field) | N | balloons on line; refused a phase | -90.0208 | 29.9582 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 50 | 2020 | 1323588929 | Yes | EAST ORLEANS | THDR | 140 | 2020-02-05 | 7000 | DIS | 23818 | 4352749766 | 1608 | ENOI | 6 | 50 | EMER | Emergency Switching | N | crew to replace pole | -89.9557 | 30.0225 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 144 | 2020 | 1324656883 | Yes | ORLEANS | FAIR | 140 | 2020-02-28 | 20160 | LFUS | 86144 | 3898146691 | 1925 | ENOI | 1 | 144 | EARM | Equipment Failure - Crossarm | N | broken cross arm replaced | -90.1027 | 29.9451 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70125 | 2
2020 | 1 | 2020 | 1323520258 | Yes | EAST ORLEANS | FAIR | 142 | 2020-02-04 | 142 | SERV | SERVICE | 43572495525 | 1601 | ENOI | 6 | 1 | VHCL | Vehicle | N | truck hit service line..hold meter#AM11175406 removed service ..meter pan pulled off wall. RELATED TO TKT# 1323511838, 1323512749 (AKS) | -89.9566 | 30.0223 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Service Conductor | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1 | 2020 | 1323640712 | Yes | EAST ORLEANS | WIND | 148 | 2020-02-06 | 148 | SERV | SERVICE | 41140473283 | 2347 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | Had to replace bad hot leg on the pole. Back in lights. Will need a crew to cut limbs off of a palm tree. The branches are brushing against the primary. 2068575 | -90.0342 | 29.9619 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 11 | 2020 | 1324618796 | Yes | EAST ORLEANS | FAIR | 152 | 2020-02-27 | 1672 | TFUS | 60528 | 41062476942 | 611 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0363 | 29.972 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 974 | 2020 | 1323655936 | Yes | EAST ORLEANS | WIND | 154 | 2020-02-07 | 149996 | RCLR | 38677 | 4119947436 | 2347 | ENOI | 6 | 974 | EARM | Equipment Failure - Crossarm | N | insulator off arm at location | -90.034 | 29.9673 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Recloser | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 16 | 2020 | 1324017985 | Yes | ORLEANS | FAIR | 154 | 2020-02-15 | 2464 | XFMR | 1375593 | 3988249289 | 510 | ENOI | 1 | 16 | HECO | Human Error - Company (Describe in Remarks Field) | N | trans. 1375593 was out taken out by bell contractor ont on scene rclr was in | -90.0733 | 30.0162 | 19-YTD20 | 210557 | Jan1 to Yesterday | Human Error | Transformer | Human Error | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 306 | 2020 | 1323587389 | Yes | EAST ORLEANS | THDR | 156 | 2020-02-05 | 47736 | DIS | D01643 | 4356849760 | 1601 | ENOI | 6 | 306 | EMER | Emergency Switching | N | taken out for safety to replace burnt pole | -89.9557 | 30.0225 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Disconnect Switch | Emergency Switching | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 9 | 2020 | 1323561274 | Yes | EAST ORLEANS | THDR | 162 | 2020-02-05 | 1458 | TFUS | 73957 | 41821479083 | 612 | ENOI | 6 | 9 | LGHT | Lightning | N | weather | -90.0125 | 29.9777 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 12 | 2020 | 1323710068 | Yes | ORLEANS | FAIR | 163 | 2020-02-08 | 1956 | TFUS | 59131 | 39328458518 | 1923 | ENOI | 1 | 12 | ECON | Equipment Failure - Connector / Sleeve | N | there is a lead on the transformer heating up will return after hours to replace lead. per 310 | -90.092 | 29.9219 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 55 | 2020 | 1324520081 | Yes | EAST ORLEANS | FAIR | 165 | 2020-02-26 | 9075 | LFUS | 21423 | 4262649350 | 1604 | ENOI | 6 | 55 | EFSW | Equipment Failure - Fuse Switch | N | repared riser and switch, customer back in | -89.9863 | 30.0172 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 198 | 2020 | 1323563948 | Yes | EAST ORLEANS | THDR | 166 | 2020-02-05 | 32868 | DIS | 25215 | 4103247998 | 611 | ENOI | 6 | 198 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up wire | -90.0374 | 29.9803 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 2 | 2020 | 1323550570 | Yes | ORLEANS | THDR | 168 | 2020-02-05 | 336 | TFUS | 29325 | 39377470287 | 1553 | ENOI | 1 | 2 | LGHT | Lightning | N | weather | -90.0899 | 29.9543 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Transformer Fuse | Lightning | DLIN | B | Council District B | Jay Banks | 70113 | 2
2020 | 96 | 2020 | 1324527282 | Yes | ORLEANS | FAIR | 184 | 2020-02-26 | 17664 | OPEN | 3908445887 | 3908445887 | 1917 | ENOI | 1 | 96 | SCHD | Scheduled Interruption | N | Contract crew replacing rotten pole | -90.0996 | 29.9229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Open | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 6 | 2020 | 1324616559 | Yes | EAST ORLEANS | FAIR | 184 | 2020-02-27 | 1104 | TFUS | 1417774 | 41010475194 | 611 | ENOI | 6 | 6 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.0382 | 29.9672 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | C | Council District C | Kristin Palmer | 70117 | 2
2020 | 1 | 2020 | 1323988573 | Yes | ORLEANS | FAIR | 193 | 2020-02-15 | 193 | SECO | METER | 39437478935 | 912 | ENOI | 1 | 1 | MTEX | Meter Exchange | N | cust AMI mtr was opened AMOC doesnt work weekends and DOC doesnt have control to close mtr so changed mtr to mtr#8180313 sn-34644421 r-00000 KC | -90.0878 | 29.978 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Secondary Conductor | Other | DLIN | A | Council District A | Joseph Giarrusso | 70119 | 2
2020 | 58 | 2020 | 1324464499 | Yes | EAST ORLEANS | FAIR | 195 | 2020-02-25 | 11310 | LFUS | 24738 | 4346351051 | 2223 | ENOI | 6 | 58 | VHCL | Vehicle | N | car hit pole RELATED TO AMFM 1324463382 | -89.9595 | 30.0636 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Line Fuse | Public Damage | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 142 | 2020 | 1324538266 | Yes | ORLEANS | FAIR | 197 | 2020-02-26 | 27974 | LFUS | 27985 | 3909645896 | 1917 | ENOI | 1 | 142 | SCHD | Scheduled Interruption | N | Contract crew replacing pole at the intersection of Chestnut and Milan | -90.0993 | 29.9232 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 70 | 2020 | 1324538399 | Yes | ORLEANS | FAIR | 197 | 2020-02-26 | 13790 | LFUS | 27759 | 3909745885 | 1917 | ENOI | 1 | 70 | SCHD | Scheduled Interruption | N | Contract crew replacing pole at the intersection of Chestnut and Milan | -90.0993 | 29.9229 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70115 | 2
2020 | 9 | 2020 | 1324416282 | Yes | ORLEANS | FAIR | 199 | 2020-02-24 | 1791 | TFUS | 1000615 | 39768462508 | 2135 | ENOI | 1 | 9 | SCHD | Scheduled Interruption | N | repairs to secondary | -90.078 | 29.9328 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 18 | 2020 | 1323561267 | Yes | EAST ORLEANS | THDR | 200 | 2020-02-05 | 3600 | LFUS | 62285 | 4180447921 | 612 | ENOI | 6 | 18 | LGHT | Lightning | N |  | -90.0131 | 29.9781 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 14 | 2020 | 1323899529 | Yes | ORLEANS | FAIR | 203 | 2020-02-12 | 2842 | TFUS | 72350 | 38822482342 | 903 | ENOI | 1 | 14 | ECNS | Equipment Failure - Connector Sleeve | N | picked up span of primary that fell due to the hot tap connection | -90.107 | 29.9875 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70124 | 2
2020 | 1 | 2020 | 1323653145 | Yes | EAST ORLEANS | WIND | 210 | 2020-02-06 | 210 | LFUS | 61838 | 4107349839 | 1001 | ENOI | 6 | 1 | EFSW | Equipment Failure - Fuse Switch | N | refused lateral 61838 b/c phases only customer back on | -90.0354 | 30.031 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 75 | 2020 | 1323576846 | Yes | ORLEANS | THDR | 212 | 2020-02-05 | 15900 | LFUS | 27869 | 3847346112 | 1917 | ENOI | 1 | 75 | LGHT | Lightning | N | weather | -90.1188 | 29.9292 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 11 | 2020 | 1323716666 | Yes | EAST ORLEANS | FAIR | 214 | 2020-02-08 | 2354 | TFUS | 1417733 | 40381486047 | 1708 | ENOI | 6 | 11 | EARR | Equipment Failure - Arrestor | N | refuse b phase ..cleared arrester | -90.0577 | 29.9973 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 269 | 2020 | 1323986713 | Yes | EAST ORLEANS | FAIR | 215 | 2020-02-15 | 57835 | LFUS | 27320-F | 4235049908 | 2211 | ENOI | 6 | 269 | EELB | Equipment Failure - Elbow | N | crew replaced bad elbow, customers back on now | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 50 | 2020 | 1323623756 | Yes | EAST ORLEANS | FAIR | 219 | 2020-02-06 | 10950 | LFUS | 21126 | 4120947834 | 621 | ENOI | 6 | 50 | ECNS | Equipment Failure - Connector Sleeve | N | riser on switch broke, repaired, customers back on | -90.0319 | 29.9758 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 30 | 2020 | 1323555868 | Yes | EAST ORLEANS | THDR | 231 | 2020-02-05 | 6930 | LFUS | 82569 | 4192847736 | 2347 | ENOI | 6 | 30 | EPRI | Equipment Failure - Primary Conductor | N | crew picked up wire | -90.0091 | 29.9728 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 55 | 2020 | 1323610634 | Yes | EAST ORLEANS | THDR | 232 | 2020-02-06 | 12760 | LFUS | 23476 | 4333250949 | 2223 | ENOI | 6 | 55 | LGHT | Lightning | N | weasther | -89.9637 | 30.0609 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 5 | 2020 | 1323823115 | Yes | EAST ORLEANS | FAIR | 242 | 2020-02-11 | 1694 | XFMR | 1049527 | 4184247070 | 2346 | ENOI | 6 | 5 | ETRD | Equipment Failure - Transformer | N | replaced bad transformer | -90.0122 | 29.9546 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 7 | 2020 | 1324387775 | Yes | EAST ORLEANS | FAIR | 242 | 2020-02-23 | 1694 | TFUS | 527839 | 42532504275 | 2215 | ENOI | 6 | 7 | ASQL | Animal - Squirrel | N | refused pot; lights back on | -89.989 | 30.0469 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 10 | 2020 | 1323571541 | Yes | EAST ORLEANS | THDR | 243 | 2020-02-05 | 2430 | TFUS | 1358844 | 44417501345 | 1205 | ENOI | 6 | 10 | AOTH | Animal - Other (Describe in Remarks Field) | N | rat took out b phase lateral in cubicle 82- refused ok-cust back on | -89.9296 | 30.0381 | 19-YTD20 | 210557 | Jan1 to Yesterday | Animal | Transformer Fuse | Animal | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 20 | 2020 | 1323636140 | Yes | EAST ORLEANS | WIND | 253 | 2020-02-06 | 5060 | LFUS | 75618 | 4081847779 | 622 | ENOI | 6 | 20 | VINE | Vine Growing into Line | N | vine pole..clear..refused lateral.. | -90.0441 | 29.9744 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Line Fuse | Vegetation | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 4 | 2020 | 1324041039 | Yes | ORLEANS | FAIR | 264 | 2020-02-16 | 1056 | XFMR | 549347 | 38505459883 | 1914 | ENOI | 1 | 4 | ETRD | Equipment Failure - Transformer | N | bad xfmr, changed xfmr | -90.1178 | 29.9259 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | A | Council District A | Joseph Giarrusso | 70115 | 2
2020 | 25 | 2020 | 1323557034 | Yes | EAST ORLEANS | THDR | 266 | 2020-02-05 | 6650 | LFUS | 34975 | 4151047208 | 2346 | ENOI | 6 | 25 | LGHT | Lightning | N | refuse b phase | -90.0226 | 29.9585 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 98 | 2020 | 1324448213 | Yes | ORLEANS | FAIR | 274 | 2020-02-24 | 26852 | LFUS | F05614 | 39978464632 | 2137 | ENOI | 1 | 98 | EARM | Equipment Failure - Crossarm | N | crossarms replaced | -90.0713 | 29.9386 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70130 | 2
2020 | 1 | 2020 | 1324635782 | Yes | ORLEANS | FAIR | 274 | 2020-02-27 | 274 | XFMR | 1087045 | 3914247399 | 912 | ENOI | 1 | 1 | ETRD | Equipment Failure - Transformer | N | crew changed out xfmr | -90.0972 | 29.9645 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | B | Council District B | Jay Banks | 70119 | 2
2020 | 26 | 2020 | 1323911490 | Yes | ALGIERS ELEC ONLY | FAIR | 277 | 2020-02-13 | 7202 | TFUS | BY78432 | 4057647060 | W0715 | ENOI | 81 | 26 | VINE | Vine Growing into Line | N | serviceman removed vines from transformer (pwd) | -90.0521 | 29.9548 | 19-YTD20 | 210557 | Jan1 to Yesterday | Vegetation | Transformer Fuse | Vegetation | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 68 | 2020 | 1323384442 | Yes | ORLEANS | FAIR | 280 | 2020-02-01 | 19040 | LFUS | 17674 | 4020349326 | 503 | ENOI | 1 | 68 | EARM | Equipment Failure - Crossarm | N | Broken crossarm caused lateral outage also caused 1 span of lateral to burn down at sleeve. | -90.0632 | 30.0171 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 26 | 2020 | 1323427511 | Yes | ORLEANS | FAIR | 283 | 2020-02-02 | 7358 | LFUS | 21189 | 3800546584 | B0527 | ENOI | 1 | 26 | SCHD | Scheduled Interruption | N | Scheduled Interruption | -90.1335 | 29.9423 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Line Fuse | Scheduled Interruption | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 1 | 2020 | 1324683772 | Yes | EAST ORLEANS | FAIR | 289 | 2020-02-29 | 289 | SECO | SERVICE | 40861490898 | 501 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N |  | -90.0422 | 30.0105 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Secondary Conductor | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70126 | 2
2020 | 66 | 2020 | 1323551306 | Yes | EAST ORLEANS | THDR | 297 | 2020-02-05 | 19602 | LFUS | 27885 | 4349649589 | 1612 | ENOI | 6 | 66 | LGHT | Lightning | N |  | -89.959 | 30.0234 | 19-YTD20 | 210557 | Jan1 to Yesterday | Lightning | Line Fuse | Lightning | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 1 | 2020 | 1323436744 | Yes | EAST ORLEANS | FAIR | 307 | 2020-02-03 | 307 | TFUS | 28497 | 41836500134 | 2212 | ENOI | 6 | 1 | ECNS | Equipment Failure - Connector Sleeve | N | replaced jumper connection | -90.0113 | 30.0356 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 9 | 2020 | 1324187155 | Yes | ALGIERS ELEC ONLY | FAIR | 311 | 2020-02-20 | 2799 | XFMR | BY98542 | 4159646652 | W0723 | ENOI | 81 | 9 | ETRD | Equipment Failure - Transformer | N | bad transformer at location. | -90.02 | 29.9432 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70114 | 2
2020 | 41 | 2020 | 1323557039 | Yes | EAST ORLEANS | THDR | 315 | 2020-02-05 | 12915 | LFUS | 31818 | 4164547152 | 2346 | ENOI | 6 | 41 | EPOL | Equipment Failure - Pole | N | refuse latteral | -90.0182 | 29.957 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70117 | 2
2020 | 238 | 2020 | 1324044207 | Yes | ORLEANS | FAIR | 320 | 2020-02-16 | 76160 | DIS | 23320 | 38432474479 | 2022 | ENOI | 1 | 238 | VHCL | Vehicle | N | Crew on site replacing broken pole PID IN PROGRESS RELATED TO TKT# 1324040006 (AKS) | -90.1197 | 29.966 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 268 | 2020 | 1324358592 | Yes | EAST ORLEANS | FAIR | 329 | 2020-02-21 | 88172 | DIS | 24625 | 4063748581 | 1710 | ENOI | 6 | 268 | EARM | Equipment Failure - Crossarm | N | broken cross arm crew is enroute to replace arm | -90.0497 | 29.9965 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70122 | 2
2020 | 3 | 2020 | 1324059083 | Yes | EAST ORLEANS | FAIR | 336 | 2020-02-17 | 1008 | TFUS | 62400 | 42950505451 | 2215 | ENOI | 6 | 3 | SCHD | Scheduled Interruption | N | Crew opened in order to safely do required work............. | -89.9759 | 30.0498 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Transformer Fuse | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 581 | 2020 | 1324644436 | Yes | EAST ORLEANS | FAIR | 345 | 2020-02-28 | 200445 | SWIT | 25680 | 4211049707 | 1610 | ENOI | 6 | 581 | EPRI | Equipment Failure - Primary Conductor | N | Bad cable bet sw. # 25680 & # 86561. Picked up cust. from sw. # 25185 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2
2020 | 1 | 2020 | 1324132625 | Yes | EAST ORLEANS | FAIR | 352 | 2020-02-18 | 352 | SERV | SERVICE | 42512499834 | 2216 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | repaired | -89.99 | 30.0345 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 5 | 2020 | 1323574976 | Yes | EAST ORLEANS | THDR | 389 | 2020-02-05 | 1945 | TFUS | 1543254 | 43598495566 | 1601 | ENOI | 6 | 5 | EPOL | Equipment Failure - Pole | N | crew replacing pole | -89.9557 | 30.0224 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 16 | 2020 | 1323384421 | Yes | EAST ORLEANS | FAIR | 390 | 2020-02-01 | 6240 | TFUS | 617753 | 43842513577 | 2217 | ENOI | 6 | 16 | ESEC | Secondary/Service Conductor | N | manhole burnt up repaired | -89.9472 | 30.0719 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 1 | 2020 | 1323384382 | Yes | EAST ORLEANS | FAIR | 393 | 2020-02-01 | 393 | SERV | SERVICE | 4386451333 | 2217 | ENOI | 6 | 1 | ESEC | Secondary/Service Conductor | N | manhole burnt | -89.9466 | 30.0712 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Service Conductor | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 11 | 2020 | 1324158085 | Yes | EAST ORLEANS | FAIR | 402 | 2020-02-19 | 4422 | DIS | 36981 | 4542049869 | 1202 | ENOI | 6 | 11 | SCHD | Scheduled Interruption | N | Taken out for safety of Transmission crews to repair damaged shield wire from the night before. All customers were notified | -89.8981 | 30.0303 | 19-YTD20 | 210557 | Jan1 to Yesterday | Scheduled Interruption | Disconnect Switch | Scheduled Interruption | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 8 | 2020 | 1323642003 | Yes | EAST ORLEANS | WIND | 433 | 2020-02-06 | 3464 | TFUS | 3010148 | 43306495734 | 1611 | ENOI | 6 | 8 | EFLK | Equipment Failure - Fuse Link | N | changed fuse barrel on trans.. | -89.9649 | 30.023 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 48 | 2020 | 1323636868 | Yes | EAST ORLEANS | WIND | 451 | 2020-02-06 | 21648 | LFUS | 23476 | 4333250949 | 2223 | ENOI | 6 | 48 | EFSW | Equipment Failure - Fuse Switch | N | fuse switch repaired | -89.9637 | 30.0609 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 23 | 2020 | 1323990854 | Yes | EAST ORLEANS | FAIR | 492 | 2020-02-15 | 11316 | LFUS | 21120 | 4107947975 | 621 | ENOI | 6 | 23 | CORR | Corrosion | N | repaired broke jumper | -90.0358 | 29.9798 | 19-YTD20 | 210557 | Jan1 to Yesterday | Other | Line Fuse | Other | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 31 | 2020 | 1323930361 | Yes | EAST ORLEANS | FAIR | 550 | 2020-02-13 | 17050 | LFUS | 25289 | 4290350439 | 2216 | ENOI | 6 | 31 | ETRD | Equipment Failure - Transformer | N | crew to replace underground pot | -89.9774 | 30.0469 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70127 | 2
2020 | 45 | 2020 | 1323657975 | Yes | EAST ORLEANS | WIND | 558 | 2020-02-07 | 25110 | DIS | D01653 | 4116547515 | 2347 | ENOI | 6 | 45 | EARM | Equipment Failure - Crossarm | N | crew to replace insulator and crossarm | -90.0333 | 29.9672 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Disconnect Switch | Equipment Failure | DLIN | D | Council District D | Jared Brossett | 70117 | 2
2020 | 66 | 2020 | 1323642921 | Yes | EAST ORLEANS | WIND | 578 | 2020-02-06 | 38148 | LFUS | 36787 | 4369551079 | 2217 | ENOI | 6 | 66 | ETRD | Equipment Failure - Transformer | N | Crew on site replacing transformer | -89.9522 | 30.0643 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 42 | 2020 | 1323384290 | Yes | EAST ORLEANS | FAIR | 579 | 2020-02-01 | 24318 | LFUS | 23610 | 4356750910 | 2217 | ENOI | 6 | 42 | ETRD | Equipment Failure - Transformer | N | crew replaced | -89.9562 | 30.0596 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Line Fuse | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70128 | 2
2020 | 12 | 2020 | 1324391305 | Yes | EAST ORLEANS | FAIR | 639 | 2020-02-23 | 7668 | XFMR | 1373043 | 44468499346 | 1601 | ENOI | 6 | 12 | ETRD | Equipment Failure - Transformer | N |  | -89.9282 | 30.0326 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70129 | 2
2020 | 1 | 2020 | 1323526696 | Yes | ORLEANS | FAIR | 1055 | 2020-02-05 | 1055 | DIS | 23962 | 3843647209 | 2024 | ENOI | 1 | 1 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1197 | 29.9594 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 11 | 2020 | 1323525368 | Yes | ORLEANS | FAIR | 1140 | 2020-02-05 | 12540 | DIS | 23886 | 3851346971 | 2016 | ENOI | 1 | 11 | VHCL | Vehicle | N | car broke pole; shield wire down - Related to #1323525567 (DGault) | -90.1172 | 29.9529 | 19-YTD20 | 210557 | Jan1 to Yesterday | Public Damage | Disconnect Switch | Public Damage | DLIN | A | Council District A | Joseph Giarrusso | 70118 | 2
2020 | 17 | 2020 | 1324472835 | Yes | ORLEANS | FAIR | 1511 | 2020-02-25 | 25687 | XFMR | 75060 | 40339473868 | 614 | ENOI | 1 | 17 | ETRD | Equipment Failure - Transformer | N | crew to replace transformer | -90.0595 | 29.9638 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Transformer | Equipment Failure | DLIN | C | Council District C | Kristin Palmer | 70116 | 2
2020 | 11 | 2020 | 1324654003 | Yes | EAST ORLEANS | FAIR | 1757 | 2020-02-28 | 19327 | SWIT | 27120 | 4230549755 | 1610 | ENOI | 6 | 11 | EPRI | Equipment Failure - Primary Conductor | N | Isolated bad cable bet sw, # 25680 & 86561 | -97.0758 | 27.9066 | 19-YTD20 | 210557 | Jan1 to Yesterday | Equipment Failure | Switch | Equipment Failure | DLIN | E | Council District E | Cyndi Nguyen | 70126 | 2